## Summary
| Conditions | Logs | f [Hz] | SG [°C] | DG [°C] | SSH [°C] | Duty [kW] | Flow rate [m3/h] | IE [%] | VE [%] | COP [-]
0 | 5.8 / 42.0 @ 70 Hz | 1343-1344-1345 | 70 | 5.7675 | 42.033 | 9.6185 | 540.0435 | 731.769 | 70.1173 | 95.5912 | 4.6471
1 | 5.8 / 41.9 @ 75 Hz | 1340-1341-1342 | 75 | 5.8012 | 41.9346 | 11.7019 | 578.9672 | 781.3772 | 69.4085 | 95.2645 | 4.6261
2 | 7.4 / 33.4 @ 45 Hz | 1337-1338-1339 | 45 | 7.3715 | 33.3538 | 12.8114 | 393.9711 | 465.4878 | 69.7394 | 94.5827 | 6.8599

## Test_log
| Log Number | Unnamed: 1 | 1345 | 1344 | 1343 | 1342 | 1341 | 1340 | 1339 | 1338 | 1337 | 1336 | 1335 | 1334 | 1333 | 1332 | 1331 | 1330 | 1329 | 1328 | 1327 | 1326 | 1325 | 1324 | 1323 | 1322 | 1321 | 1320 | 1319 | 1318 | 1317 | 1316 | 1315 | 1314 | 1313 | 1312 | 1311 | 1310 | 1309 | 1308 | 1307 | 1306 | 1305 | 1304 | 1303 | 1302 | 1301 | 1300 | 1299 | 1298 | 1297 | 1296 | 1295 | 1294 | 1293 | 1292 | 1291 | 1290 | 1289 | 1288 | 1287 | 1286 | 1285 | 1284 | 1283 | 1282 | 1281 | 1280 | 1279 | 1278 | 1277 | 1276 | 1275 | 1274 | 1273 | 1272 | 1271 | 1270 | 1269 | 1268 | 1267 | 1266 | 1265 | 1264 | 1263 | 1262 | 1261 | 1260 | 1259 | 1258 | 1257 | 1256 | 1255 | 1254 | 1253 | 1252 | 1251 | 1250 | 1249 | 1248 | 1247 | 1246 | 1245 | 1244 | 1243 | 1242 | 1241 | 1240 | 1239 | 1238 | 1237 | 1236 | 1235 | 1234 | 1233 | 1232 | 1231 | 1230 | 1229 | 1228 | 1227 | 1226 | 1225 | 1224 | 1223 | 1222 | 1221 | 1220 | 1219 | 1218 | 1217 | 1216 | 1215 | 1214 | 1213 | 1212 | 1211 | 1210 | 1209 | 1208 | 1207 | 1206 | 1205 | 1204 | 1203 | 1202 | 1201 | 1200 | 1199 | 1198 | 1197 | 1196 | 1195 | 1194 | 1193 | 1192 | 1191 | 1190 | 1189 | 1188 | 1187 | 1186 | 1185 | 1184 | 1183 | 1182 | 1181 | 1180 | 1179 | 1178 | 1177 | 1176 | 1175 | 1174 | 1173 | 1172 | 1171 | 1170 | 1169 | 1168 | 1167 | 1166 | 1165 | 1164 | 1163 | 1162 | 1161 | 1160 | 1159 | 1158 | 1157 | 1156 | 1155 | 1154 | 1153 | 1152 | 1151 | 1150 | 1149 | 1148 | 1147 | 1146 | 1145 | 1144 | 1143 | 1142 | 1141 | 1140 | 1139 | 1138 | 1137 | 1136 | 1135 | 1134 | 1133 | 1132 | 1131 | 1130 | 1129 | 1128 | 1127 | 1126 | 1125 | 1124 | 1123 | 1122 | 1121 | 1120
0 | Parameters | Units | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs
1 | Date |  | 2020-05-07 14:39 | 2020-05-07 14:31 | 2020-05-07 14:27 | 2020-05-07 14:07 | 2020-05-07 14:03 | 2020-05-07 14:01 | 2020-05-07 13:17 | 2020-05-07 13:15 | 2020-05-07 13:11 | 2020-05-07 13:01 | 2020-05-07 12:58 | 2020-05-07 12:54 | 2020-05-07 12:49 | 2020-05-07 12:45 | 2020-05-07 12:42 | 2020-05-07 11:49 | 2020-05-07 11:46 | 2020-05-07 11:42 | 2020-05-07 10:53 | 2020-05-07 10:43 | 2020-05-07 10:33 | 2020-05-06 16:33 | 2020-05-06 16:30 | 2020-05-06 16:27 | 2020-05-06 16:04 | 2020-05-06 15:58 | 2020-05-06 15:55 | 2020-05-06 15:38 | 2020-05-06 15:35 | 2020-05-06 15:32 | 2020-05-06 14:32 | 2020-05-06 14:29 | 2020-05-06 14:26 | 2020-05-06 13:50 | 2020-05-06 13:47 | 2020-05-06 13:44 | 2020-05-06 12:51 | 2020-05-06 12:31 | 2020-05-06 12:30 | 2020-05-06 12:28 | 2020-05-06 12:19 | 2020-05-06 12:18 | 2020-05-06 12:15 | 2020-05-06 12:11 | 2020-05-06 12:02 | 2020-05-06 10:57 | 2020-05-06 10:54 | 2020-05-06 10:50 | 2020-05-06 10:27 | 2020-05-06 10:24 | 2020-05-06 10:21 | 2020-05-06 10:14 | 2020-05-06 10:10 | 2020-05-06 10:07 | 2020-05-01 15:06 | 2020-05-01 15:02 | 2020-05-01 14:59 | 2020-05-01 14:03 | 2020-05-01 14:01 | 2020-05-01 13:57 | 2020-05-01 13:34 | 2020-05-01 13:31 | 2020-05-01 13:29 | 2020-05-01 12:22 | 2020-05-01 12:19 | 2020-05-01 12:16 | 2020-05-01 10:58 | 2020-05-01 10:55 | 2020-05-01 10:52 | 2020-05-01 10:39 | 2020-05-01 10:34 | 2020-04-30 16:33 | 2020-04-30 16:30 | 2020-04-30 16:26 | 2020-04-30 15:21 | 2020-04-30 15:19 | 2020-04-30 15:17 | 2020-04-30 14:22 | 2020-04-30 14:01 | 2020-04-30 13:58 | 2020-04-30 13:54 | 2020-04-30 12:33 | 2020-04-30 12:29 | 2020-04-30 12:26 | 2020-04-30 11:18 | 2020-04-30 11:06 | 2020-04-30 11:03 | 2020-04-30 11:01 | 2020-04-29 16:20 | 2020-04-29 16:15 | 2020-04-29 16:12 | 2020-04-29 16:10 | 2020-04-29 15:22 | 2020-04-29 15:15 | 2020-04-29 15:11 | 2020-04-29 14:39 | 2020-04-29 14:34 | 2020-04-29 14:19 | 2020-04-28 16:38 | 2020-04-28 16:36 | 2020-04-28 16:30 | 2020-04-28 16:27 | 2020-04-28 16:18 | 2020-04-28 16:12 | 2020-04-28 16:07 | 2020-04-28 16:00 | 2020-04-22 13:14 | 2020-04-22 13:10 | 2020-04-22 13:07 | 2020-04-22 12:45 | 2020-04-22 12:42 | 2020-04-22 12:39 | 2020-04-22 12:34 | 2020-04-22 12:31 | 2020-04-22 12:28 | 2020-04-22 12:15 | 2020-04-22 12:09 | 2020-04-22 12:06 | 2020-04-22 11:03 | 2020-04-22 10:59 | 2020-04-22 10:56 | 2020-04-20 16:27 | 2020-04-20 16:21 | 2020-04-20 16:16 | 2020-04-20 15:54 | 2020-04-20 15:50 | 2020-04-20 15:47 | 2020-04-20 12:48 | 2020-04-20 12:44 | 2020-04-20 12:41 | 2020-04-20 12:32 | 2020-04-20 12:28 | 2020-04-20 12:24 | 2020-04-20 10:49 | 2020-04-20 10:46 | 2020-04-20 10:41 | 2020-04-17 10:56 | 2020-04-17 10:51 | 2020-04-17 10:44 | 2020-04-17 10:12 | 2020-04-17 10:07 | 2020-04-17 10:03 | 2020-04-16 16:15 | 2020-04-16 16:10 | 2020-04-16 16:06 | 2020-04-16 16:00 | 2020-04-16 15:50 | 2020-04-16 15:47 | 2020-04-16 12:26 | 2020-04-16 12:22 | 2020-04-16 12:18 | 2020-04-16 11:49 | 2020-04-16 11:46 | 2020-04-16 11:43 | 2020-04-15 11:35 | 2020-04-15 11:26 | 2020-04-15 11:21 | 2020-04-15 11:08 | 2020-04-15 11:05 | 2020-04-15 11:01 | 2020-04-15 10:52 | 2020-04-15 10:48 | 2020-04-15 10:43 | 2020-04-14 16:34 | 2020-04-14 16:32 | 2020-04-14 16:29 | 2020-04-14 15:19 | 2020-04-14 15:14 | 2020-04-14 15:11 | 2020-04-09 11:53 | 2020-04-09 11:48 | 2020-04-09 11:44 | 2020-04-09 11:32 | 2020-04-09 11:28 | 2020-04-09 11:24 | 2020-04-08 16:19 | 2020-04-08 16:15 | 2020-04-08 16:12 | 2020-04-07 16:41 | 2020-04-07 16:37 | 2020-04-07 16:35 | 2020-04-07 16:31 | 2020-04-07 16:28 | 2020-04-07 16:25 | 2020-04-07 16:18 | 2020-04-07 16:13 | 2020-04-07 16:10 | 2020-04-07 15:16 | 2020-04-07 15:14 | 2020-04-07 15:10 | 2020-04-07 12:55 | 2020-04-07 12:52 | 2020-04-07 12:49 | 2020-04-07 11:03 | 2020-04-07 11:00 | 2020-04-07 10:55 | 2020-04-07 10:33 | 2020-04-07 10:29 | 2020-04-07 10:26 | 2020-04-06 16:18 | 2020-04-06 16:15 | 2020-04-06 16:12 | 2020-04-06 16:04 | 2020-04-06 16:01 | 2020-04-06 15:54 | 2020-04-06 12:43 | 2020-04-06 12:40 | 2020-04-06 12:36 | 2020-04-06 12:32 | 2020-04-06 12:29 | 2020-04-06 12:26 | 2020-04-06 12:17 | 2020-04-06 12:14 | 2020-04-06 12:11 | 2020-04-06 12:05 | 2020-04-06 12:03 | 2020-04-06 11:59 | 2020-04-06 11:49 | 2020-04-06 11:46 | 2020-04-06 11:43 | 2020-04-06 10:40 | 2020-04-06 10:37 | 2020-04-06 10:35 | 2020-04-06 10:28 | 2020-04-06 10:24 | 2020-04-06 10:20
2 | Time |  | 2020-05-07 | 2020-05-07 | 2020-05-07 | 2020-05-07 | 2020-05-07 | 2020-05-07 | 2020-05-07 | 2020-05-07 | 2020-05-07 | 2020-05-07 | 2020-05-07 | 2020-05-07 | 2020-05-07 | 2020-05-07 | 2020-05-07 | 2020-05-07 | 2020-05-07 | 2020-05-07 | 2020-05-07 | 2020-05-07 | 2020-05-07 | 2020-05-06 | 2020-05-06 | 2020-05-06 | 2020-05-06 | 2020-05-06 | 2020-05-06 | 2020-05-06 | 2020-05-06 | 2020-05-06 | 2020-05-06 | 2020-05-06 | 2020-05-06 | 2020-05-06 | 2020-05-06 | 2020-05-06 | 2020-05-06 | 2020-05-06 | 2020-05-06 | 2020-05-06 | 2020-05-06 | 2020-05-06 | 2020-05-06 | 2020-05-06 | 2020-05-06 | 2020-05-06 | 2020-05-06 | 2020-05-06 | 2020-05-06 | 2020-05-06 | 2020-05-06 | 2020-05-06 | 2020-05-06 | 2020-05-06 | 2020-05-01 | 2020-05-01 | 2020-05-01 | 2020-05-01 | 2020-05-01 | 2020-05-01 | 2020-05-01 | 2020-05-01 | 2020-05-01 | 2020-05-01 | 2020-05-01 | 2020-05-01 | 2020-05-01 | 2020-05-01 | 2020-05-01 | 2020-05-01 | 2020-05-01 | 2020-04-30 | 2020-04-30 | 2020-04-30 | 2020-04-30 | 2020-04-30 | 2020-04-30 | 2020-04-30 | 2020-04-30 | 2020-04-30 | 2020-04-30 | 2020-04-30 | 2020-04-30 | 2020-04-30 | 2020-04-30 | 2020-04-30 | 2020-04-30 | 2020-04-30 | 2020-04-29 | 2020-04-29 | 2020-04-29 | 2020-04-29 | 2020-04-29 | 2020-04-29 | 2020-04-29 | 2020-04-29 | 2020-04-29 | 2020-04-29 | 2020-04-28 | 2020-04-28 | 2020-04-28 | 2020-04-28 | 2020-04-28 | 2020-04-28 | 2020-04-28 | 2020-04-28 | 2020-04-22 | 2020-04-22 | 2020-04-22 | 2020-04-22 | 2020-04-22 | 2020-04-22 | 2020-04-22 | 2020-04-22 | 2020-04-22 | 2020-04-22 | 2020-04-22 | 2020-04-22 | 2020-04-22 | 2020-04-22 | 2020-04-22 | 2020-04-20 | 2020-04-20 | 2020-04-20 | 2020-04-20 | 2020-04-20 | 2020-04-20 | 2020-04-20 | 2020-04-20 | 2020-04-20 | 2020-04-20 | 2020-04-20 | 2020-04-20 | 2020-04-20 | 2020-04-20 | 2020-04-20 | 2020-04-17 | 2020-04-17 | 2020-04-17 | 2020-04-17 | 2020-04-17 | 2020-04-17 | 2020-04-16 | 2020-04-16 | 2020-04-16 | 2020-04-16 | 2020-04-16 | 2020-04-16 | 2020-04-16 | 2020-04-16 | 2020-04-16 | 2020-04-16 | 2020-04-16 | 2020-04-16 | 2020-04-15 | 2020-04-15 | 2020-04-15 | 2020-04-15 | 2020-04-15 | 2020-04-15 | 2020-04-15 | 2020-04-15 | 2020-04-15 | 2020-04-14 | 2020-04-14 | 2020-04-14 | 2020-04-14 | 2020-04-14 | 2020-04-14 | 2020-04-09 | 2020-04-09 | 2020-04-09 | 2020-04-09 | 2020-04-09 | 2020-04-09 | 2020-04-08 | 2020-04-08 | 2020-04-08 | 2020-04-07 | 2020-04-07 | 2020-04-07 | 2020-04-07 | 2020-04-07 | 2020-04-07 | 2020-04-07 | 2020-04-07 | 2020-04-07 | 2020-04-07 | 2020-04-07 | 2020-04-07 | 2020-04-07 | 2020-04-07 | 2020-04-07 | 2020-04-07 | 2020-04-07 | 2020-04-07 | 2020-04-07 | 2020-04-07 | 2020-04-07 | 2020-04-06 | 2020-04-06 | 2020-04-06 | 2020-04-06 | 2020-04-06 | 2020-04-06 | 2020-04-06 | 2020-04-06 | 2020-04-06 | 2020-04-06 | 2020-04-06 | 2020-04-06 | 2020-04-06 | 2020-04-06 | 2020-04-06 | 2020-04-06 | 2020-04-06 | 2020-04-06 | 2020-04-06 | 2020-04-06 | 2020-04-06 | 2020-04-06 | 2020-04-06 | 2020-04-06 | 2020-04-06 | 2020-04-06 | 2020-04-06
3 | Conditions |  | 5.8 / 42.1 ºC SH 9.4 ºC | 5.7 / 42 ºC SH 9.7 ºC | 5.7 / 42.1 ºC SH 9.7 ºC | 5.9 / 41.9 ºC SH 11.7 ºC | 5.8 / 42 ºC SH 11.7 ºC | 5.8 / 41.9 ºC SH 11.7 ºC | 7.3 / 33.3 ºC SH 13 ºC | 7.4 / 33.4 ºC SH 12.8 ºC | 7.4 / 33.3 ºC SH 12.7 ºC | 7.3 / 33.2 ºC SH 11.8 ºC | 7.5 / 33.3 ºC SH 11.5 ºC | 7.5 / 33.4 ºC SH 11.3 ºC | 7.5 / 33.4 ºC SH 11.1 ºC | 7.4 / 33.3 ºC SH 11.1 ºC | 7.4 / 33.2 ºC SH 11.1 ºC | 7.9 / 28.1 ºC SH 9.3 ºC | 7.8 / 28.1 ºC SH 9.2 ºC | 7.7 / 27.9 ºC SH 9 ºC | 7.8 / 27.9 ºC SH 11.2 ºC | 7.9 / 28.1 ºC SH 10.7 ºC | 7.8 / 28 ºC SH 10.6 ºC | 7.4 / 33.3 ºC SH 10 ºC | 7.5 / 33.4 ºC SH 9.5 ºC | 7.4 / 33.3 ºC SH 9.4 ºC | 7.3 / 33.2 ºC SH 8.9 ºC | 7.4 / 33.2 ºC SH 8.8 ºC | 7.4 / 33.2 ºC SH 8.8 ºC | 7.4 / 33.3 ºC SH 8.9 ºC | 7.4 / 33.3 ºC SH 8.8 ºC | 7.5 / 33.3 ºC SH 8.7 ºC | 5.9 / 42.1 ºC SH 11.3 ºC | 5.8 / 42.1 ºC SH 11.2 ºC | 5.7 / 42 ºC SH 11.1 ºC | 5.8 / 42 ºC SH 10.8 ºC | 5.8 / 42 ºC SH 10.6 ºC | 5.7 / 42 ºC SH 10.4 ºC | 5.8 / 42 ºC SH 11.1 ºC | 4 / 50.6 ºC SH 10.3 ºC | 4 / 50.6 ºC SH 10.3 ºC | 4 / 50.6 ºC SH 10.3 ºC | 4 / 50.6 ºC SH 10.4 ºC | 4 / 50.6 ºC SH 10.4 ºC | 4.1 / 50.6 ºC SH 10.4 ºC | 4.1 / 50.6 ºC SH 10.5 ºC | 4.1 / 50.6 ºC SH 10.9 ºC | 1.8 / 51.7 ºC SH 10.3 ºC | 1.7 / 51.6 ºC SH 10.8 ºC | 1.7 / 51.6 ºC SH 10 ºC | 4 / 50.7 ºC SH 10.5 ºC | 4 / 50.6 ºC SH 10.4 ºC | 4 / 50.6 ºC SH 10.4 ºC | 4 / 50.1 ºC SH 11.2 ºC | 4 / 50 ºC SH 11 ºC | 4 / 49.9 ºC SH 10.7 ºC | 1.7 / 51.6 ºC SH 9.4 ºC | 1.7 / 51.7 ºC SH 9.5 ºC | 1.7 / 51.6 ºC SH 9.6 ºC | 5.8 / 42 ºC SH 11.1 ºC | 5.8 / 42 ºC SH 11 ºC | 5.7 / 42.1 ºC SH 11.1 ºC | 5.8 / 42 ºC SH 11.4 ºC | 5.8 / 42 ºC SH 11.5 ºC | 5.8 / 41.9 ºC SH 11.5 ºC | 7.4 / 33.2 ºC SH 10.9 ºC | 7.4 / 33.3 ºC SH 11.3 ºC | 7.4 / 33.3 ºC SH 11.7 ºC | 7.7 / 27.9 ºC SH 10.6 ºC | 7.7 / 28 ºC SH 10.7 ºC | 7.9 / 28.1 ºC SH 10.6 ºC | 7.9 / 28.3 ºC SH 10 ºC | 7.8 / 28 ºC SH 10 ºC | 5.8 / 41.9 ºC SH 9.5 ºC | 5.8 / 41.9 ºC SH 9.3 ºC | 5.8 / 42 ºC SH 8.8 ºC | 7.4 / 33.2 ºC SH 9.6 ºC | 7.4 / 33.2 ºC SH 9.4 ºC | 7.4 / 33.2 ºC SH 9.3 ºC | 7.5 / 33.4 ºC SH 8.9 ºC | 7.4 / 33.3 ºC SH 9.4 ºC | 7.4 / 33.2 ºC SH 9.4 ºC | 7.4 / 33.2 ºC SH 9.5 ºC | 5.8 / 33.2 ºC SH 11 ºC | 5.8 / 33.2 ºC SH 11.1 ºC | 5.9 / 33.2 ºC SH 11 ºC | 7.6 / 28.3 ºC SH 10 ºC | 7.9 / 28.3 ºC SH 10.7 ºC | 7.8 / 28.2 ºC SH 10.8 ºC | 7.8 / 28.1 ºC SH 10.5 ºC | 3.8 / 50.4 ºC SH 9.8 ºC | 3.9 / 50.6 ºC SH 10.1 ºC | 4 / 50.6 ºC SH 10.4 ºC | 3.9 / 50.6 ºC SH 10.5 ºC | 3.9 / 50.6 ºC SH 9.6 ºC | 4.1 / 50.6 ºC SH 10.6 ºC | 4.1 / 50.6 ºC SH 10.9 ºC | 4 / 50 ºC SH 14.9 ºC | 4 / 50.1 ºC SH 15.4 ºC | 4.1 / 50.1 ºC SH 14.8 ºC | 4.1 / 50.6 ºC SH 17.6 ºC | 4.1 / 50.6 ºC SH 17.6 ºC | 4 / 50.5 ºC SH 17.6 ºC | 4 / 50.5 ºC SH 17.6 ºC | 4.1 / 50.2 ºC SH 17.4 ºC | 4.1 / 50.3 ºC SH 17.3 ºC | 4.1 / 50.2 ºC SH 17.4 ºC | 4.1 / 50 ºC SH 17.3 ºC | 1.7 / 51.6 ºC SH 10.4 ºC | 1.8 / 51.6 ºC SH 10.7 ºC | 1.7 / 51.7 ºC SH 10.7 ºC | 4.1 / 50.6 ºC SH 9.6 ºC | 4 / 50.5 ºC SH 9.8 ºC | 4 / 50.5 ºC SH 10.6 ºC | 4 / 50 ºC SH 11.5 ºC | 3.9 / 49.9 ºC SH 11.8 ºC | 4 / 50 ºC SH 12 ºC | 4.1 / 50.7 ºC SH 9.1 ºC | 4 / 50.5 ºC SH 9.9 ºC | 4 / 50.6 ºC SH 9.3 ºC | 7.4 / 33.4 ºC SH 10.2 ºC | 7.5 / 33.4 ºC SH 10 ºC | 7.3 / 33.2 ºC SH 10.3 ºC | 1.7 / 51.7 ºC SH 9.7 ºC | 1.7 / 51.8 ºC SH 9.5 ºC | 1.8 / 51.7 ºC SH 9.3 ºC | 4.1 / 50.1 ºC SH 9.5 ºC | 4 / 50 ºC SH 9.3 ºC | 4 / 50 ºC SH 8.9 ºC | 3.9 / 50.6 ºC SH 10.8 ºC | 4 / 50.6 ºC SH 10.4 ºC | 4 / 50.6 ºC SH 10.5 ºC | 4 / 50.5 ºC SH 9.3 ºC | 4 / 50.5 ºC SH 9.5 ºC | 3.9 / 50.4 ºC SH 9.6 ºC | 7.3 / 33.4 ºC SH 9.4 ºC | 7.4 / 33.5 ºC SH 9.3 ºC | 7.3 / 33.2 ºC SH 9.1 ºC | 7.4 / 33.4 ºC SH 10.9 ºC | 7.4 / 33.3 ºC SH 11.1 ºC | 7.4 / 33.4 ºC SH 11.9 ºC | 7.4 / 33.3 ºC SH 11.7 ºC | 7.4 / 33.1 ºC SH 11.3 ºC | 7.4 / 33.2 ºC SH 10.9 ºC | 7.8 / 28 ºC SH 10.1 ºC | 7.8 / 28 ºC SH 10.2 ºC | 7.9 / 28 ºC SH 10.3 ºC | 7.8 / 28.1 ºC SH 10.3 ºC | 7.8 / 28.1 ºC SH 10 ºC | 7.8 / 28 ºC SH 10 ºC | 5.7 / 42 ºC SH 9.8 ºC | 5.8 / 41.9 ºC SH 9.7 ºC | 5.8 / 41.9 ºC SH 9.7 ºC | 5.8 / 41.9 ºC SH 10.5 ºC | 5.8 / 42 ºC SH 10.3 ºC | 5.8 / 41.9 ºC SH 9.9 ºC | 1.7 / 51.8 ºC SH 10.9 ºC | 1.7 / 51.7 ºC SH 9.8 ºC | 1.6 / 51.8 ºC SH 8.4 ºC | 4 / 50.7 ºC SH 9.2 ºC | 4 / 50.7 ºC SH 9 ºC | 3.9 / 50.6 ºC SH 9.1 ºC | 4 / 50.2 ºC SH 9.2 ºC | 4 / 50 ºC SH 8.9 ºC | 3.9 / 50 ºC SH 9 ºC | 4.1 / 50.8 ºC SH 10.8 ºC | 4 / 50.7 ºC SH 12.1 ºC | 4 / 50.5 ºC SH 11.3 ºC | 7.4 / 33.2 ºC SH 11.4 ºC | 7.4 / 33.4 ºC SH 11.2 ºC | 7.4 / 33.2 ºC SH 11 ºC | 4 / 50.1 ºC SH 11.3 ºC | 4 / 50.1 ºC SH 11.3 ºC | 3.9 / 50.1 ºC SH 11.5 ºC | 4 / 50.7 ºC SH 11.6 ºC | 4 / 50.8 ºC SH 11.5 ºC | 4 / 50.9 ºC SH 10.7 ºC | 7.4 / 33.3 ºC SH 9.9 ºC | 7.3 / 33.2 ºC SH 10 ºC | 7.4 / 33.3 ºC SH 9.9 ºC | 7.7 / 28.2 ºC SH 10.3 ºC | 7.7 / 28.2 ºC SH 10.1 ºC | 7.7 / 28.1 ºC SH 10 ºC | 7.9 / 28 ºC SH 9.8 ºC | 7.4 / 28.1 ºC SH 10.4 ºC | 7.3 / 28.1 ºC SH 10.6 ºC | 7.5 / 28.1 ºC SH 10.5 ºC | 7.4 / 27.9 ºC SH 10.6 ºC | 7.4 / 27.8 ºC SH 10.9 ºC | 7.5 / 33.3 ºC SH 10.1 ºC | 7.4 / 33.3 ºC SH 10.1 ºC | 7.3 / 33.1 ºC SH 10.4 ºC | 7.4 / 33.3 ºC SH 9.5 ºC | 7.3 / 33.2 ºC SH 9.7 ºC | 7.3 / 33.2 ºC SH 9.8 ºC | 5.8 / 42.1 ºC SH 10.3 ºC | 5.8 / 42.1 ºC SH 10.3 ºC | 5.8 / 41.8 ºC SH 10.5 ºC | 5.8 / 42 ºC SH 10.9 ºC | 5.8 / 41.9 ºC SH 10.7 ºC | 5.7 / 41.9 ºC SH 10.6 ºC | 1.6 / 51.7 ºC SH 10.2 ºC | 1.7 / 51.5 ºC SH 10.1 ºC | 1.7 / 51.6 ºC SH 10 ºC | 1.8 / 51.6 ºC SH 9.9 ºC | 1.7 / 51.6 ºC SH 9.6 ºC | 1.7 / 51.5 ºC SH 9.3 ºC | 4.1 / 50 ºC SH 9.9 ºC | 4 / 49.9 ºC SH 9.8 ºC | 4.1 / 50 ºC SH 10.1 ºC | 4 / 49.9 ºC SH 9.8 ºC | 4 / 49.8 ºC SH 9.9 ºC | 4 / 49.9 ºC SH 10 ºC | 4 / 50.5 ºC SH 10 ºC | 3.9 / 50.4 ºC SH 10 ºC | 4 / 50.5 ºC SH 9.7 ºC | 3.9 / 50.7 ºC SH 9.9 ºC | 4 / 50.7 ºC SH 9.9 ºC | 4 / 50.7 ºC SH 9.9 ºC | 4 / 50.6 ºC SH 10.3 ºC | 3.9 / 50.7 ºC SH 10.2 ºC | 4 / 50.5 ºC SH 10 ºC | 7.4 / 33.2 ºC SH 10.3 ºC | 7.3 / 33.1 ºC SH 10.5 ºC | 7.3 / 33.2 ºC SH 10.4 ºC | 7.4 / 33.3 ºC SH 10.3 ºC | 7.4 / 33.3 ºC SH 10.4 ºC | 7.4 / 33.2 ºC SH 10.6 ºC
4 | Test Purpose |  | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD - target duty 524 kW | 310-240FS, 2.6VR MOD - target duty 524 kW | 310-240FS, 2.6VR MOD - target duty 524 kW | 310-240FS, 2.6VR MOD - target duty 524 kW | 310-240FS, 2.6VR MOD - target duty 524 kW | 310-240FS, 2.6VR MOD - target duty 332 kW | 310-240FS, 2.6VR MOD - target duty 332 kW | 310-240FS, 2.6VR MOD - target duty 332 kW | 310-240FS, 2.6VR MOD - target duty 332 kW | 310-240FS, 2.6VR MOD - target duty 148 kW | 310-240FS, 2.6VR MOD - target duty 148 kW | 310-240FS, 2.6VR MOD - target duty 148 kW | 310-240FS, 2.6VR MOD - target duty 148 kW | 310-240FS, 2.6VR MOD - target duty 148 kW | 310-240FS, 2.6VR MOD - target duty 569kW | 310-240FS, 2.6VR MOD - target duty 569kW | 310-240FS, 2.6VR MOD - target duty 569kW | 310-240FS, 2.6VR MOD - target duty 361kW | 310-240FS, 2.6VR MOD - target duty 361kW | 310-240FS, 2.6VR MOD - target duty 361kW | 310-240FS, 2.6VR MOD - target duty 361kW | 310-240FS, 2.6VR MOD - target duty 361kW | 310-240FS, 2.6VR MOD - target duty 361kW | 310-240FS, 2.6VR MOD - target duty 361kW | 310-240FS, 2.6VR MOD - target duty 361kW | 310-240FS, 2.6VR MOD - target duty 361kW | 310-240FS, 2.6VR MOD - target duty 361kW | 310-240FS, 2.6VR MOD - target duty 161kW | 310-240FS, 2.6VR MOD - target duty 161kW | 310-240FS, 2.6VR MOD - target duty 161kW | 310-240FS, 2.6VR MOD - target duty 161kW | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE - Target duty 347.6 | 310240FS - DAE - Target duty 347.6 | 310240FS - DAE - Target duty 347.6 | 310240FS - DAE - Target duty 347.6 | 310240FS - DAE - Target duty 347.6 | 310240FS - DAE - Target duty 347.6 | 310240FS - DAE - Target duty 155.3. | 310240FS - DAE - Target duty 155.3. | 310240FS - DAE - Target duty 155.3. | 310240FS - DAE - Target duty 166.2 | 310240FS - DAE - Target duty 166.2 | 310240FS - DAE - Target duty 166.2 | 310240FS - DAE - Target duty 547.2 | 310240FS - DAE - Target duty 547.2 | 310240FS - DAE - Target duty 547.2 | 310240FS - DAE - Target duty 585.8 | 310240FS - DAE - Target duty 585.8 | 310240FS - DAE - Target duty 585.8 | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE - Target duty 153 kW | 310240FS - DAE - Target duty 153 kW | 310240FS - DAE - Target duty 153 kW | 310240FS - DAE - Target duty 153 kW | 310240FS - DAE - Target duty 153 kW | 310240FS - DAE - Target duty 153 kW | 310240FS - DAE - Target duty 166 kW | 310240FS - DAE - Target duty 166 kW | 310240FS - DAE - Target duty 166 kW | 310240FS - DAE - Target duty 372 kW | 310240FS - DAE - Target duty 372 kW | 310240FS - DAE - Target duty 372 kW | 310240FS - DAE - Target duty 343 kW | 310240FS - DAE - Target duty 343 kW | 310240FS - DAE - Target duty 343 kW | 310240FS - DAE - Target duty 541 kW | 310240FS - DAE - Target duty 541 kW | 310240FS - DAE - Target duty 541 kW | 310240FS - DAE - Target duty 585 kW | 310240FS - DAE - Target duty 585 kW | 310240FS - DAE - Target duty 585 kW | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE
5 | Econ on/off |  | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | econ (should be non econ) | econ (should be non econ) | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | econ | econ | econ | econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | econ | econ | econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | econ | econ | econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | econ | econ | econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | econ | econ | econ | non econ | non econ | non econ | non econ | non econ | non econ
6 | LI on/off |  | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI
7 | Compressor ID |  | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL
8 | Compressor Size |  | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL
9 | Notes |  | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR Test @20Hz (higher duty) | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR Test @20Hz (higher duty) | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR Test @20Hz (higher duty) | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR Test @20Hz (higher duty) | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR Test @20Hz (higher duty) | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR ? on suction temp reading - prob not fitted at suction compressor flange correctly. | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR ? on suction temp reading - prob not fitted at suction compressor flange correctly. | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR ? on suction temp reading - prob not fitted at suction compressor flange correctly. | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR ? on suction temp reading - prob not fitted at suction compressor flange correctly. | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR ? on suction temp reading - prob not fitted at suction compressor flange correctly. | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR ? on suction temp reading - prob not fitted at suction compressor flange correctly. | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR ? on suction temp reading - prob not fitted at suction compressor flange correctly. | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR ? on suction temp reading - prob not fitted at suction compressor flange correctly. | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer Withour econ plug OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer Withour econ plug OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer Withour econ plug OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer Withour econ plug OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer Withour econ plug OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer Withour econ plug OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer Withour econ plug OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer Withour econ plug OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer Withour econ plug OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer Withour econ plug OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer Withour econ plug OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer Withour econ plug OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer Withour econ plug OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer Withour econ plug OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer Withour econ plug OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice + plug Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice + plug Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice + plug Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice + plug Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice + plug Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice + plug Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice + plug Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice + plug Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice + plug Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice + plug Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice + plug Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice + plug Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice + plug Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice + plug Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice + plug Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Center Bearing orifice 3rd Bearing oil feed orifice Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Center Bearing orifice 3rd Bearing oil feed orifice Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Center Bearing orifice 3rd Bearing oil feed orifice Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Center Bearing orifice 3rd Bearing oil feed orifice Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Center Bearing orifice 3rd Bearing oil feed orifice Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Center Bearing orifice 3rd Bearing oil feed orifice Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Center Bearing orifice 3rd Bearing oil feed orifice Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Center Bearing orifice 3rd Bearing oil feed orifice Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Center Bearing orifice 3rd Bearing oil feed orifice Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR 21% of load @ 110Hz | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR 21% of load @ 110Hz | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR 21% of load @ 110Hz | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR 21% of load @ 110Hz | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR 21% of load @ 110Hz | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR 21% of load @ 110Hz | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR 21% of full load @ 120Hz | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR 21% of full load @ 120Hz | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR 47% of full load @ 120Hz | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR 47% of full load @ 120Hz | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR 47% of full load @ 120Hz | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR 47% of full load @ 120Hz | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR 47% of load @ 110Hz | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR 47% of load @ 110Hz | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR 47% of load @ 110Hz | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR 74% of load @ 110Hz | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR 74% of load @ 110Hz | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR 74% of load @ 110Hz | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR 74% of full load 120Hz | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR 74% of full load 120Hz | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR 74% of full load 120Hz | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR Slide / VVR Oil vent shut | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR Slide / VVR Oil vent shut | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR Slide / VVR Oil vent shut | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR Slide VVR/Oil vent shut | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR Slide VVR/Oil vent shut | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR Slide VVR/Oil vent shut | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR Slide VVR/Oil vent shut | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR Slide VVR/Oil vent shut | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR Slide VVR/Oil vent shut | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR Slide VVR/Oil vent shut | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR Slide VVR/Oil vent shut | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR Slide VVR/Oil vent shut | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR
10 | Refrigerant |  | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a
11 | Comp PR |  | 2.9858 | 2.9869 | 2.9931 | 2.9706 | 2.9823 | 2.9793 | 2.2333 | 2.2343 | 2.2308 | 2.2263 | 2.2241 | 2.2252 | 2.2244 | 2.228 | 2.2215 | 1.8915 | 1.8932 | 1.8885 | 1.8847 | 1.8889 | 1.8859 | 2.224 | 2.2252 | 2.2227 | 2.2258 | 2.2238 | 2.2207 | 2.2233 | 2.2259 | 2.2235 | 2.9857 | 2.9888 | 2.989 | 2.9849 | 2.9852 | 2.987 | 2.9829 | 3.9614 | 3.9594 | 3.9661 | 3.9616 | 3.9581 | 3.9564 | 3.9502 | 3.9476 | 4.4051 | 4.4063 | 4.4123 | 3.9712 | 3.9563 | 3.9564 | 3.9107 | 3.9006 | 3.8899 | 4.405 | 4.4122 | 4.4076 | 2.98 | 2.9836 | 2.9955 | 2.9796 | 2.9802 | 2.9803 | 2.2179 | 2.2231 | 2.2217 | 1.8894 | 1.8914 | 1.8906 | 1.8977 | 1.8902 | 2.981 | 2.9781 | 2.979 | 2.2224 | 2.2207 | 2.2233 | 2.2247 | 2.2248 | 2.2204 | 2.2201 | 2.3405 | 2.3463 | 2.3404 | 1.9151 | 1.9033 | 1.8978 | 1.8924 | 3.9666 | 3.9728 | 3.9688 | 3.9737 | 3.9768 | 3.9547 | 3.9441 | 3.9104 | 3.9119 | 3.8939 | 3.9491 | 3.9471 | 3.9514 | 3.9526 | 3.9088 | 3.9152 | 3.9136 | 3.8873 | 4.4074 | 4.4003 | 4.414 | 3.958 | 3.9523 | 3.9526 | 3.9083 | 3.9026 | 3.9017 | 3.9667 | 3.9576 | 3.9603 | 2.2319 | 2.2315 | 2.2254 | 4.4201 | 4.4196 | 4.4103 | 3.9051 | 3.9061 | 3.9083 | 3.9655 | 3.9565 | 3.9543 | 3.9546 | 3.9532 | 3.9548 | 2.2367 | 2.2346 | 2.226 | 2.2327 | 2.2237 | 2.2329 | 2.2206 | 2.2171 | 2.2216 | 1.8879 | 1.8879 | 1.8799 | 1.8948 | 1.8924 | 1.8911 | 2.9917 | 2.9738 | 2.976 | 2.9733 | 2.9767 | 2.9685 | 4.4226 | 4.4207 | 4.4346 | 3.9684 | 3.9736 | 3.9716 | 3.9187 | 3.901 | 3.9152 | 3.9701 | 3.9665 | 3.9521 | 2.2232 | 2.2377 | 2.2212 | 3.9104 | 3.9173 | 3.9207 | 3.9731 | 3.9791 | 3.9886 | 2.2246 | 2.2249 | 2.2273 | 1.9041 | 1.9033 | 1.8986 | 1.8817 | 1.9214 | 1.9224 | 1.9119 | 1.9064 | 1.905 | 2.2262 | 2.2236 | 2.2216 | 2.23 | 2.2287 | 2.2297 | 2.987 | 2.984 | 2.9671 | 2.9787 | 2.9796 | 2.9802 | 4.4272 | 4.3983 | 4.3957 | 4.3981 | 4.4042 | 4.4019 | 3.894 | 3.8854 | 3.8947 | 3.8943 | 3.8897 | 3.8866 | 3.9509 | 3.953 | 3.9546 | 3.9773 | 3.9771 | 3.9789 | 3.9543 | 3.9827 | 3.9591 | 2.2241 | 2.2257 | 2.2251 | 2.2245 | 2.2265 | 2.2204
12 | Comp PD |  | 7.1426 | 7.1277 | 7.1521 | 7.0976 | 7.1247 | 7.1038 | 4.6729 | 4.6898 | 4.6696 | 4.643 | 4.6604 | 4.6644 | 4.6663 | 4.6658 | 4.6401 | 3.4389 | 3.4429 | 3.413 | 3.4068 | 3.4282 | 3.4101 | 4.65 | 4.6654 | 4.6499 | 4.6454 | 4.64 | 4.6399 | 4.6482 | 4.6539 | 4.6569 | 7.1518 | 7.1469 | 7.1342 | 7.1252 | 7.1355 | 7.1274 | 7.1266 | 10.0062 | 10.0071 | 10.0166 | 10.0075 | 10.0038 | 10.0029 | 9.9916 | 9.9888 | 10.6247 | 10.6061 | 10.6064 | 10.039 | 9.9977 | 9.991 | 9.8381 | 9.7982 | 9.7707 | 10.6043 | 10.6306 | 10.6071 | 7.1227 | 7.1257 | 7.1604 | 7.1212 | 7.1159 | 7.1106 | 4.6314 | 4.6529 | 4.6467 | 3.4158 | 3.4246 | 3.4357 | 3.4663 | 3.4242 | 7.1153 | 7.1052 | 7.1191 | 4.6406 | 4.6401 | 4.6475 | 4.6635 | 4.6534 | 4.641 | 4.6386 | 4.826 | 4.8345 | 4.8304 | 3.5019 | 3.4841 | 3.4602 | 3.4404 | 9.9597 | 10.0097 | 10.0188 | 10.0064 | 10.0234 | 9.9958 | 9.9765 | 9.8174 | 9.8236 | 9.8151 | 9.9817 | 9.9969 | 9.9719 | 9.9742 | 9.8485 | 9.882 | 9.8562 | 9.7799 | 10.6135 | 10.6049 | 10.6251 | 10.0097 | 9.9586 | 9.9743 | 9.8113 | 9.7791 | 9.7913 | 10.0376 | 9.9698 | 9.9987 | 4.6848 | 4.685 | 4.6419 | 10.6526 | 10.6554 | 10.6371 | 9.8395 | 9.8161 | 9.8103 | 9.9936 | 9.9923 | 9.993 | 9.9799 | 9.961 | 9.9549 | 4.6872 | 4.6934 | 4.646 | 4.6861 | 4.6506 | 4.6807 | 4.6435 | 4.6232 | 4.6393 | 3.4204 | 3.4206 | 3.402 | 3.4432 | 3.4334 | 3.4253 | 7.1431 | 7.0936 | 7.0933 | 7.1046 | 7.1146 | 7.0838 | 10.6654 | 10.6339 | 10.6672 | 10.0387 | 10.0435 | 10.0101 | 9.855 | 9.7899 | 9.8247 | 10.0653 | 10.0199 | 9.981 | 4.6385 | 4.6942 | 4.6399 | 9.8312 | 9.84 | 9.835 | 10.031 | 10.0718 | 10.0894 | 4.6551 | 4.6426 | 4.6558 | 3.4712 | 3.4664 | 3.4511 | 3.4058 | 3.4959 | 3.497 | 3.4748 | 3.4482 | 3.4343 | 4.665 | 4.6534 | 4.6313 | 4.6709 | 4.6543 | 4.6565 | 7.1534 | 7.1401 | 7.0739 | 7.1211 | 7.1089 | 7.1 | 10.6479 | 10.5811 | 10.5878 | 10.6034 | 10.6056 | 10.575 | 9.795 | 9.7549 | 9.7986 | 9.7784 | 9.7482 | 9.7606 | 9.9638 | 9.9517 | 9.9631 | 10.0328 | 10.0404 | 10.0414 | 9.9857 | 10.0337 | 9.9871 | 4.6458 | 4.6378 | 4.6427 | 4.6559 | 4.6542 | 4.6356
13 | LVDT |  | -37.4319 | -37.4329 | -37.4326 | -37.432 | -37.4327 | -37.4326 | -37.4326 | -37.4331 | -37.4344 | -37.4323 | -37.4321 | -37.4333 | -37.4331 | -37.4328 | -37.4329 | -37.4325 | -37.4323 | -37.4326 | -37.4335 | -37.4338 | -37.4323 | -37.4334 | -37.4323 | -37.4335 | -37.4319 | -37.4339 | -37.4335 | -37.4317 | -37.4326 | -37.434 | -37.4321 | -37.4342 | -37.4334 | -37.4328 | -37.4333 | -37.4332 | -37.4332 | -37.4327 | -37.4334 | -37.4327 | -37.432 | -37.4335 | -37.4337 | -37.4326 | -37.4337 | -37.4323 | -37.432 | -37.4329 | -37.4331 | -37.4327 | -37.4326 | -37.4329 | -37.4324 | -37.4323 | -37.4335 | -37.433 | -37.4332 | -37.4326 | -37.4329 | -37.4327 | -37.4329 | -37.4324 | -37.4329 | -37.4328 | -37.4327 | -37.4319 | -37.4333 | -37.4329 | -37.4322 | -37.4319 | -37.4326 | -37.4328 | -37.433 | -37.4329 | -37.4324 | -37.4338 | -37.4325 | -37.4332 | -37.4326 | -37.4327 | -37.4328 | -37.4335 | -37.4328 | -37.4336 | -37.433 | -37.4331 | -37.4342 | -37.4333 | -37.4336 | -37.433 | -37.4328 | -37.4331 | -37.4325 | -37.4327 | -37.4323 | -37.4323 | -37.4329 | -37.4329 | -37.4324 | -37.4327 | -37.4318 | -37.4322 | -37.4332 | -37.4334 | -37.4334 | -37.4329 | -37.4326 | -37.4325 | -37.4321 | -37.4328 | -37.4331 | -37.4325 | -37.4327 | -37.4328 | -37.4323 | -37.4333 | -37.433 | -37.4327 | -37.433 | -37.4326 | -37.4323 | -37.4328 | -37.4328 | -37.4326 | -37.4324 | -37.4329 | -37.4321 | -37.4327 | -37.4334 | -37.4337 | -37.4329 | -37.4319 | -37.4328 | -37.4328 | -37.4324 | -37.4315 | -37.4328 | -37.4324 | -37.4327 | -37.4333 | -37.4332 | -37.4328 | -37.4329 | -37.4333 | -37.4338 | -37.433 | -37.4331 | -37.4328 | -37.4332 | -37.4321 | -37.4327 | -37.432 | -37.4325 | -37.4328 | -37.4323 | -37.4329 | -37.4326 | -37.4333 | -37.4323 | -37.4325 | -37.4332 | -37.4334 | -37.4327 | -37.433 | -37.4314 | -37.4332 | -37.434 | -37.4328 | -37.4335 | -37.4327 | -37.4323 | -37.4331 | -37.4333 | -37.4325 | -37.4323 | -37.4322 | -37.4323 | -37.4316 | -37.4326 | -37.4323 | -37.4325 | -37.4327 | -37.433 | -37.4323 | -37.4328 | -37.4325 | -37.433 | -37.4336 | -37.4323 | -37.4331 | -37.4328 | -37.4334 | -37.4335 | -37.4338 | -37.433 | -37.4334 | -37.4318 | -37.4321 | -37.4325 | -37.4337 | -37.4327 | -37.4334 | -37.4325 | -37.4331 | -37.4332 | -37.4329 | -37.4333 | -37.4325 | -37.4324 | -37.4324 | -37.4327 | -37.4331 | -37.4323 | -37.4327 | -37.4327 | -37.4329 | -37.4321 | -37.4342 | -37.433 | -37.4325 | -37.4327 | -37.4326 | -37.433 | -37.4331 | -37.4335 | -37.434
14 | Comp Running |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
15 | Comp data
16 | Tester |  | AS | AS | MJ | AS | AS | AS | AS | AS | AS | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | AS | AS | AS | AS | AS | AS | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | AS | AS | AS | AS | AS | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | AS + MJ | AS + MJ | AS + MJ | AS | AS | AS | AS | AS + MJ | AS + MJ | AS + MJ | AS + MJ | AS + MJ | AS + MJ | AS | AS | AS | AS | AS | AS | AS | AS | AS | AS | AS | AS | AS | AS | AS | AS | AS | AS | AS | AS | AS | AS | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ
17 | Comp match?
18 | Motor Size |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | VR |  | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 1.6 | 1.6 | 1.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 2.6 | 2.6 | 2.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 1 2 2.6 | 1 2 2.6 | 1 2 2.6 | 1 2 2.6 | 1 2 2.6 | 1 2 2.6 | 1 2 2.6 | 1 2 2.6 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 1.6 | 1.6 | 1.6 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 1.6 | 1.6 | 1.6 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6
20 | Motor ID |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | Comp Type |  | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL
22 | Comp swept vol | m3/hr | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82
23 | Corrected comp swept vol for Hz | m3/hr | 765.4714 | 765.4824 | 765.6027 | 820.1972 | 820.1863 | 820.2737 | 492.1708 | 492.1927 | 492.0833 | 437.5216 | 437.4232 | 437.4779 | 437.4669 | 437.5216 | 437.4451 | 207.7588 | 207.7588 | 207.8463 | 218.6405 | 218.6514 | 218.8264 | 437.4997 | 437.4341 | 437.4451 | 470.1886 | 470.298 | 470.3089 | 470.3418 | 470.2324 | 470.2433 | 776.4625 | 776.4078 | 776.4625 | 820.2191 | 820.2191 | 820.2081 | 809.2936 | 1203.004 | 1203.004 | 1203.004 | 1203.004 | 1202.8946 | 1203.004 | 1203.004 | 1203.1134 | 1312.368 | 1312.368 | 1312.4774 | 1312.4774 | 1312.368 | 1312.5867 | 1312.368 | 1312.368 | 1312.2586 | 1312.4774 | 1312.368 | 1312.368 | 754.6335 | 754.4366 | 754.5132 | 765.5371 | 765.4277 | 765.548 | 437.4997 | 437.4779 | 437.4669 | 207.7588 | 207.7916 | 207.7369 | 218.8374 | 218.728 | 820.23 | 820.2519 | 820.1206 | 470.3089 | 470.2761 | 470.298 | 470.1777 | 492.1599 | 492.1271 | 492.1927 | 492.138 | 492.0286 | 492.0833 | 218.8155 | 218.7936 | 218.6952 | 218.6843 | 1203.004 | 1203.004 | 1203.2227 | 1203.2227 | 1312.368 | 1312.368 | 1312.368 | 1312.2586 | 1312.368 | 1312.368 | 1312.2586 | 1312.4774 | 1312.1493 | 1312.2586 | 1312.2586 | 1312.368 | 1312.368 | 1312.368 | 1312.368 | 1312.2586 | 1312.4774 | 1312.4774 | 1312.368 | 1312.368 | 1312.4774 | 1312.2586 | 1312.2586 | 1202.7853 | 1203.004 | 1203.004 | 492.1927 | 492.1489 | 492.0724 | 1312.2586 | 1312.4774 | 1312.4774 | 1312.4774 | 1312.368 | 1312.368 | 1312.368 | 1312.368 | 1312.368 | 1203.1134 | 1203.004 | 1203.004 | 492.1161 | 492.2036 | 492.1599 | 470.2761 | 470.2652 | 470.2761 | 437.456 | 437.4888 | 437.3794 | 207.7479 | 207.7807 | 207.8353 | 218.6843 | 218.7061 | 218.8374 | 776.4844 | 776.4735 | 776.4844 | 831.243 | 831.1227 | 831.2101 | 1312.2586 | 1312.4774 | 1312.368 | 1312.4774 | 1312.368 | 1312.4774 | 1312.368 | 1312.368 | 1312.2586 | 1203.1134 | 1203.1134 | 1203.004 | 492.1271 | 492.1599 | 492.1161 | 1312.2586 | 1312.368 | 1312.1493 | 1312.2586 | 1312.368 | 1312.2586 | 492.1708 | 492.0943 | 492.1708 | 218.7389 | 218.7717 | 218.8046 | 207.8244 | 207.901 | 207.7588 | 218.7389 | 218.7499 | 218.7608 | 470.2652 | 470.2433 | 470.2761 | 437.4669 | 437.4123 | 437.5326 | 765.5808 | 765.5699 | 754.6882 | 831.1773 | 831.1445 | 831.1992 | 1312.6961 | 1312.2586 | 1312.368 | 1312.4774 | 1312.2586 | 1312.368 | 1312.368 | 1312.4774 | 1312.368 | 1312.4774 | 1312.4774 | 1312.2586 | 1312.2586 | 1312.2586 | 1312.368 | 1312.6961 | 1312.368 | 1312.368 | 1202.8946 | 1203.004 | 1202.8946 | 492.0724 | 492.0943 | 492.1052 | 492.138 | 492.1708 | 492.1161
24
25
26 | Atmopsheric Pressure (manual input) | bar | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135
27 | Suction Temp | ºC | 15.2453 | 15.4783 | 15.4345 | 17.5607 | 17.521 | 17.4276 | 20.2842 | 20.2017 | 20.063 | 19.0741 | 18.9792 | 18.8013 | 18.5706 | 18.4883 | 18.493 | 17.1189 | 17.0125 | 16.7228 | 18.9759 | 18.5056 | 18.4042 | 17.3922 | 16.9391 | 16.7895 | 16.1943 | 16.1802 | 16.1937 | 16.3087 | 16.2008 | 16.1704 | 17.1666 | 17.0217 | 16.8172 | 16.5701 | 16.3831 | 16.1233 | 16.9093 | 14.3163 | 14.3056 | 14.2855 | 14.3732 | 14.3977 | 14.4554 | 14.6297 | 14.9905 | 12.1148 | 12.491 | 11.6225 | 14.4707 | 14.4767 | 14.447 | 15.2061 | 14.9845 | 14.7759 | 11.0711 | 11.1825 | 11.2949 | 16.9689 | 16.7949 | 16.82 | 17.2337 | 17.2418 | 17.2429 | 18.3113 | 18.719 | 19.14 | 18.3754 | 18.4238 | 18.4575 | 17.928 | 17.8053 | 15.2657 | 15.1213 | 14.6392 | 16.9474 | 16.8708 | 16.7454 | 16.3672 | 16.8494 | 16.8831 | 16.9756 | 16.818 | 16.8359 | 16.894 | 17.6224 | 18.5485 | 18.5994 | 18.336 | 13.6671 | 14.0142 | 14.3711 | 14.4289 | 13.5508 | 14.6941 | 15.0175 | 18.91 | 19.3815 | 18.9184 | 21.6936 | 21.6804 | 21.6293 | 21.5924 | 21.5042 | 21.445 | 21.4117 | 21.3538 | 12.1552 | 12.4514 | 12.4251 | 13.616 | 13.7924 | 14.5835 | 15.4833 | 15.6995 | 15.957 | 13.1966 | 13.8774 | 13.2902 | 17.6319 | 17.477 | 17.6169 | 11.4366 | 11.2606 | 11.0319 | 13.6057 | 13.3032 | 12.8859 | 14.7596 | 14.4407 | 14.5919 | 13.3308 | 13.5145 | 13.5078 | 16.7238 | 16.7508 | 16.4436 | 18.3129 | 18.5421 | 19.3375 | 19.1512 | 18.6899 | 18.3133 | 17.8738 | 18.0498 | 18.1805 | 18.1335 | 17.8199 | 17.7217 | 15.4962 | 15.4738 | 15.4137 | 16.3355 | 16.1358 | 15.6846 | 12.61 | 11.434 | 10.0759 | 13.2532 | 13.0466 | 13.0493 | 13.1758 | 12.8939 | 12.9535 | 14.8885 | 16.1038 | 15.307 | 18.7739 | 18.5876 | 18.4132 | 15.277 | 15.2205 | 15.4129 | 15.5764 | 15.5655 | 14.7076 | 17.317 | 17.3614 | 17.2785 | 17.975 | 17.7715 | 17.7131 | 17.6607 | 17.7695 | 17.9254 | 17.9538 | 18.0434 | 18.2548 | 17.5106 | 17.506 | 17.7587 | 16.8961 | 17.0643 | 17.0753 | 16.19 | 16.1314 | 16.3208 | 16.6937 | 16.4427 | 16.3142 | 11.8317 | 11.827 | 11.7316 | 11.6198 | 11.323 | 10.9422 | 13.9971 | 13.8499 | 14.136 | 13.8051 | 13.8426 | 14.0177 | 14.0055 | 13.9145 | 13.6531 | 13.8262 | 13.8955 | 13.8649 | 14.34 | 14.1076 | 14.024 | 17.6488 | 17.7462 | 17.7469 | 17.7016 | 17.8186 | 18.0213
28 | Suction Pressure | BarA | 3.5968 | 3.5873 | 3.5884 | 3.6017 | 3.5943 | 3.5891 | 3.7889 | 3.7995 | 3.794 | 3.7862 | 3.8072 | 3.807 | 3.811 | 3.7996 | 3.7987 | 3.8575 | 3.8547 | 3.8411 | 3.8506 | 3.8567 | 3.8494 | 3.799 | 3.8079 | 3.8029 | 3.7896 | 3.7916 | 3.8008 | 3.7998 | 3.7963 | 3.8064 | 3.6017 | 3.5936 | 3.5869 | 3.5897 | 3.5944 | 3.587 | 3.594 | 3.3789 | 3.3815 | 3.3771 | 3.3791 | 3.3818 | 3.3835 | 3.3868 | 3.3888 | 3.1203 | 3.1137 | 3.1083 | 3.3788 | 3.3818 | 3.3794 | 3.38 | 3.378 | 3.3809 | 3.1144 | 3.1155 | 3.1128 | 3.5974 | 3.5923 | 3.5883 | 3.5973 | 3.5935 | 3.5906 | 3.8027 | 3.8042 | 3.8035 | 3.8404 | 3.8418 | 3.8577 | 3.8611 | 3.8468 | 3.5918 | 3.5918 | 3.5974 | 3.7965 | 3.8012 | 3.7992 | 3.8079 | 3.7993 | 3.8028 | 3.8017 | 3.6002 | 3.591 | 3.6037 | 3.8266 | 3.857 | 3.8543 | 3.8554 | 3.3572 | 3.3671 | 3.3747 | 3.365 | 3.3672 | 3.383 | 3.3887 | 3.3732 | 3.3736 | 3.3916 | 3.3847 | 3.3921 | 3.3787 | 3.3781 | 3.3858 | 3.3898 | 3.3829 | 3.3872 | 3.1149 | 3.1188 | 3.1122 | 3.384 | 3.3732 | 3.3782 | 3.3736 | 3.369 | 3.3743 | 3.3834 | 3.3709 | 3.3776 | 3.803 | 3.8043 | 3.788 | 3.1147 | 3.116 | 3.1191 | 3.3869 | 3.3778 | 3.3733 | 3.37 | 3.3797 | 3.3825 | 3.3777 | 3.373 | 3.3691 | 3.79 | 3.8016 | 3.7897 | 3.8016 | 3.8004 | 3.7965 | 3.8041 | 3.7984 | 3.7979 | 3.852 | 3.8523 | 3.8661 | 3.8482 | 3.8472 | 3.844 | 3.5865 | 3.5939 | 3.5897 | 3.6003 | 3.5993 | 3.5985 | 3.1162 | 3.1087 | 3.1058 | 3.3819 | 3.3775 | 3.3687 | 3.3765 | 3.3746 | 3.3702 | 3.3889 | 3.3777 | 3.381 | 3.792 | 3.7928 | 3.7994 | 3.378 | 3.3731 | 3.3674 | 3.374 | 3.3809 | 3.3759 | 3.8014 | 3.7902 | 3.7934 | 3.8394 | 3.8376 | 3.8404 | 3.8626 | 3.794 | 3.7913 | 3.8104 | 3.8042 | 3.7946 | 3.8043 | 3.8029 | 3.7912 | 3.7974 | 3.788 | 3.7866 | 3.6 | 3.5988 | 3.5962 | 3.599 | 3.5911 | 3.5855 | 3.1069 | 3.1137 | 3.118 | 3.1204 | 3.1154 | 3.1086 | 3.3846 | 3.3807 | 3.385 | 3.3785 | 3.3734 | 3.3813 | 3.3765 | 3.37 | 3.3721 | 3.3698 | 3.3726 | 3.3709 | 3.3801 | 3.3639 | 3.375 | 3.7952 | 3.7838 | 3.7898 | 3.8022 | 3.7946 | 3.7985
29 | Suction SH | ºC | 9.4295 | 9.7396 | 9.6865 | 11.7056 | 11.726 | 11.674 | 12.9533 | 12.7888 | 12.6923 | 11.7635 | 11.5063 | 11.3301 | 11.0687 | 11.0747 | 11.0859 | 9.2609 | 9.1758 | 8.9897 | 11.1705 | 10.6531 | 10.6074 | 9.9831 | 9.4613 | 9.3503 | 8.8574 | 8.8284 | 8.7703 | 8.893 | 8.8127 | 8.7044 | 11.3115 | 11.2317 | 11.0813 | 10.8116 | 10.5869 | 10.387 | 11.1162 | 10.2972 | 10.2646 | 10.2818 | 10.352 | 10.3537 | 10.3973 | 10.5441 | 10.8877 | 10.3469 | 10.7823 | 9.9621 | 10.4527 | 10.4328 | 10.4233 | 11.178 | 10.9729 | 10.7394 | 9.3561 | 9.4578 | 9.5938 | 11.149 | 11.0158 | 11.073 | 11.4144 | 11.4532 | 11.477 | 10.8738 | 11.2698 | 11.6959 | 10.6476 | 10.6856 | 10.5975 | 10.0422 | 10.029 | 9.4905 | 9.3458 | 8.8189 | 9.5578 | 9.4444 | 9.3344 | 8.8894 | 9.4378 | 9.4443 | 9.5455 | 10.9755 | 11.067 | 11.0231 | 10.001 | 10.694 | 10.7658 | 10.494 | 9.8315 | 10.0948 | 10.3873 | 10.5276 | 9.6302 | 10.6404 | 10.9159 | 14.939 | 15.4072 | 14.7917 | 17.6256 | 17.5501 | 17.6117 | 17.58 | 17.4269 | 17.3341 | 17.3591 | 17.2641 | 10.4357 | 10.6962 | 10.7296 | 9.5537 | 9.8212 | 10.5705 | 11.509 | 11.7638 | 11.9763 | 9.1395 | 9.9261 | 9.2822 | 10.1917 | 10.0266 | 10.2927 | 9.7184 | 9.5313 | 9.2746 | 9.5186 | 9.2937 | 8.9144 | 10.8157 | 10.4146 | 10.5421 | 9.3214 | 9.5454 | 9.5714 | 9.3838 | 9.3217 | 9.1065 | 10.8836 | 11.1218 | 11.9472 | 11.7024 | 11.2851 | 10.9128 | 10.0575 | 10.2315 | 10.2563 | 10.3459 | 10.0403 | 9.9667 | 9.7641 | 9.6814 | 9.6553 | 10.4915 | 10.3002 | 9.8552 | 10.8786 | 9.7704 | 8.4378 | 9.2086 | 9.0391 | 9.1167 | 9.1771 | 8.9107 | 9.0079 | 10.7852 | 12.0946 | 11.2698 | 11.4184 | 11.2262 | 11.0012 | 11.2656 | 11.2507 | 11.491 | 11.5988 | 11.5299 | 10.7134 | 9.8895 | 10.0204 | 9.9124 | 10.2554 | 10.0656 | 9.9853 | 9.7632 | 10.3985 | 10.5757 | 10.4565 | 10.5944 | 10.8792 | 10.0605 | 10.0664 | 10.4098 | 9.4996 | 9.7399 | 9.7618 | 10.3485 | 10.2999 | 10.5105 | 10.8608 | 10.6732 | 10.5899 | 10.184 | 10.1183 | 9.9836 | 9.8506 | 9.5988 | 9.2792 | 9.9301 | 9.8152 | 10.0654 | 9.7893 | 9.8697 | 9.9779 | 10.0065 | 9.9707 | 9.6914 | 9.8839 | 9.9297 | 9.9134 | 10.3108 | 10.215 | 10.0378 | 10.2687 | 10.4544 | 10.4088 | 10.2674 | 10.4436 | 10.6161
30 | Suction Gauge | ºC | 5.8159 | 5.7387 | 5.7481 | 5.855 | 5.795 | 5.7536 | 7.3309 | 7.4129 | 7.3707 | 7.3106 | 7.4729 | 7.4713 | 7.5019 | 7.4136 | 7.4071 | 7.8581 | 7.8367 | 7.733 | 7.8054 | 7.8525 | 7.7967 | 7.4091 | 7.4779 | 7.4393 | 7.337 | 7.3518 | 7.4234 | 7.4157 | 7.3881 | 7.4661 | 5.8551 | 5.79 | 5.7359 | 5.7585 | 5.7962 | 5.7363 | 5.7931 | 4.0191 | 4.041 | 4.0037 | 4.0212 | 4.044 | 4.0581 | 4.0857 | 4.1028 | 1.7679 | 1.7087 | 1.6604 | 4.018 | 4.0439 | 4.0237 | 4.0281 | 4.0116 | 4.0364 | 1.7149 | 1.7248 | 1.7011 | 5.8199 | 5.7791 | 5.747 | 5.8193 | 5.7885 | 5.7659 | 7.4376 | 7.4492 | 7.4441 | 7.7278 | 7.7381 | 7.86 | 7.8858 | 7.7763 | 5.7751 | 5.7756 | 5.8203 | 7.3896 | 7.4265 | 7.411 | 7.4778 | 7.4116 | 7.4388 | 7.4301 | 5.8425 | 5.7689 | 5.8709 | 7.6214 | 7.8545 | 7.8336 | 7.8419 | 3.8356 | 3.9195 | 3.9838 | 3.9014 | 3.9206 | 4.0538 | 4.1016 | 3.971 | 3.9743 | 4.1267 | 4.068 | 4.1303 | 4.0176 | 4.0123 | 4.0773 | 4.1109 | 4.0527 | 4.0896 | 1.7195 | 1.7552 | 1.6955 | 4.0623 | 3.9712 | 4.013 | 3.9743 | 3.9357 | 3.9807 | 4.0571 | 3.9514 | 4.0081 | 7.4402 | 7.4504 | 7.3242 | 1.7182 | 1.7293 | 1.7573 | 4.0871 | 4.0095 | 3.9715 | 3.9439 | 4.0261 | 4.0498 | 4.0094 | 3.9691 | 3.9364 | 7.34 | 7.4291 | 7.3371 | 7.4293 | 7.4202 | 7.3903 | 7.4488 | 7.4048 | 7.4005 | 7.8163 | 7.8183 | 7.9242 | 7.7876 | 7.7795 | 7.755 | 5.7321 | 5.7925 | 5.7584 | 5.844 | 5.8357 | 5.8295 | 1.7314 | 1.6637 | 1.6382 | 4.0446 | 4.0075 | 3.9326 | 3.9987 | 3.9832 | 3.9456 | 4.1033 | 4.0092 | 4.0372 | 7.3554 | 7.3613 | 7.412 | 4.0114 | 3.9698 | 3.9219 | 3.9776 | 4.0357 | 3.9942 | 7.4275 | 7.341 | 7.3661 | 7.7196 | 7.7059 | 7.7278 | 7.8975 | 7.3709 | 7.3497 | 7.4973 | 7.449 | 7.3756 | 7.4501 | 7.4396 | 7.349 | 7.3966 | 7.3244 | 7.3135 | 5.8415 | 5.8315 | 5.8103 | 5.8329 | 5.7695 | 5.7243 | 1.6477 | 1.7087 | 1.748 | 1.7692 | 1.7242 | 1.663 | 4.067 | 4.0347 | 4.0707 | 4.0158 | 3.9729 | 4.0398 | 3.999 | 3.9438 | 3.9618 | 3.9423 | 3.9658 | 3.9515 | 4.0292 | 3.8926 | 3.9862 | 7.38 | 7.2918 | 7.3381 | 7.4342 | 7.375 | 7.4052
31 | Discharge Temp | ºC | 64.9206 | 65.4558 | 65.7251 | 67.6261 | 67.6046 | 67.6164 | 56.3924 | 56.3225 | 56.2193 | 56.017 | 55.9235 | 55.7537 | 55.4961 | 55.3446 | 55.1113 | 45.7004 | 45.4766 | 45.3926 | 46.4671 | 46.0189 | 45.609 | 53.5322 | 53.2481 | 53.3954 | 52.6919 | 52.6848 | 52.5961 | 53.6881 | 53.541 | 53.3669 | 66.9299 | 66.7963 | 66.7029 | 66.5891 | 66.413 | 66.1839 | 67.2566 | 79.4 | 79.3899 | 79.3811 | 79.4592 | 79.4766 | 79.5019 | 79.6386 | 79.8189 | 83.6596 | 83.69 | 83.1033 | 80.6129 | 80.5601 | 80.7132 | 80.4026 | 80.0417 | 79.8318 | 82.6253 | 82.7389 | 82.8015 | 66.8161 | 66.7456 | 66.7452 | 67.1784 | 67.198 | 67.1985 | 55.9889 | 56.3751 | 56.574 | 46.7646 | 46.6674 | 46.5323 | 45.7305 | 45.2656 | 65.4899 | 65.4777 | 65.9108 | 53.5212 | 53.4746 | 53.3858 | 53.0156 | 53.6689 | 53.7036 | 53.7298 | 56.208 | 56.2506 | 56.3103 | 47.6678 | 48.0269 | 47.9808 | 47.9414 | 79.0585 | 79.3621 | 79.6115 | 79.6811 | 80.2055 | 80.973 | 81.2442 | 84.6134 | 84.8795 | 84.1783 | 81.3351 | 81.2728 | 80.9674 | 80.7776 | 80.4931 | 80.4914 | 80.2766 | 79.5949 | 81.6492 | 81.8133 | 81.7659 | 78.36 | 78.5664 | 79.1082 | 79.3911 | 79.5723 | 79.7772 | 77.2175 | 77.1545 | 76.8154 | 54.0542 | 53.963 | 53.9896 | 81.1123 | 80.8792 | 80.8373 | 77.4235 | 77.1664 | 76.8264 | 79.0837 | 78.7779 | 79.2053 | 76.5866 | 76.7418 | 76.5902 | 52.7574 | 52.5277 | 52.4436 | 54.6356 | 55.0605 | 55.1597 | 54.7452 | 54.0465 | 53.7595 | 46.5342 | 46.5135 | 46.384 | 46.505 | 45.5963 | 45.1859 | 64.4279 | 64.2532 | 64.3681 | 65.2223 | 64.9016 | 64.4856 | 82.3417 | 81.291 | 80.4547 | 78.0616 | 77.9128 | 77.841 | 77.0956 | 77.092 | 77.3296 | 78.4717 | 79.1191 | 78.5143 | 54.4239 | 54.1733 | 53.8665 | 79.6024 | 79.6789 | 79.8482 | 80.4132 | 80.318 | 79.6525 | 53.2308 | 53.4036 | 53.8557 | 46.8378 | 46.7412 | 46.8191 | 46.4041 | 47.0398 | 46.9755 | 46.7694 | 46.714 | 46.6495 | 53.6349 | 53.649 | 53.7512 | 53.5421 | 53.736 | 54.1174 | 65.0396 | 64.7326 | 64.928 | 65.7567 | 65.5189 | 65.2597 | 81.891 | 81.6127 | 81.551 | 81.3886 | 81.121 | 80.9454 | 78.01 | 77.8995 | 78.0808 | 77.851 | 77.8788 | 77.9965 | 78.6803 | 78.5979 | 78.6633 | 78.8859 | 78.9505 | 78.9132 | 77.7743 | 77.6319 | 77.0981 | 53.3605 | 53.4136 | 53.4166 | 53.4228 | 53.4506 | 53.2936
32 | Discharge Pressure | BarA | 10.7394 | 10.715 | 10.7405 | 10.6993 | 10.719 | 10.6929 | 8.4618 | 8.4893 | 8.4636 | 8.4292 | 8.4677 | 8.4714 | 8.4773 | 8.4653 | 8.4388 | 7.2964 | 7.2976 | 7.2541 | 7.2574 | 7.285 | 7.2595 | 8.4489 | 8.4733 | 8.4528 | 8.435 | 8.4315 | 8.4407 | 8.4481 | 8.4501 | 8.4633 | 10.7535 | 10.7405 | 10.7212 | 10.7149 | 10.7299 | 10.7144 | 10.7206 | 13.3851 | 13.3886 | 13.3936 | 13.3867 | 13.3856 | 13.3864 | 13.3784 | 13.3776 | 13.745 | 13.7197 | 13.7147 | 13.4178 | 13.3795 | 13.3704 | 13.2181 | 13.1762 | 13.1516 | 13.7187 | 13.746 | 13.7199 | 10.7201 | 10.7179 | 10.7487 | 10.7184 | 10.7094 | 10.7013 | 8.4341 | 8.457 | 8.4502 | 7.2563 | 7.2664 | 7.2934 | 7.3274 | 7.271 | 10.7071 | 10.697 | 10.7165 | 8.4371 | 8.4414 | 8.4467 | 8.4713 | 8.4527 | 8.4438 | 8.4403 | 8.4262 | 8.4255 | 8.434 | 7.3284 | 7.3412 | 7.3145 | 7.2958 | 13.3169 | 13.3768 | 13.3935 | 13.3714 | 13.3907 | 13.3788 | 13.3652 | 13.1906 | 13.1972 | 13.2068 | 13.3664 | 13.389 | 13.3506 | 13.3523 | 13.2343 | 13.2717 | 13.2391 | 13.1672 | 13.7284 | 13.7237 | 13.7373 | 13.3937 | 13.3318 | 13.3524 | 13.1849 | 13.1481 | 13.1656 | 13.421 | 13.3407 | 13.3763 | 8.4878 | 8.4893 | 8.4299 | 13.7673 | 13.7713 | 13.7562 | 13.2264 | 13.1938 | 13.1836 | 13.3636 | 13.372 | 13.3756 | 13.3576 | 13.334 | 13.3241 | 8.4772 | 8.4949 | 8.4357 | 8.4877 | 8.451 | 8.4772 | 8.4476 | 8.4216 | 8.4372 | 7.2724 | 7.2728 | 7.2681 | 7.2915 | 7.2806 | 7.2693 | 10.7296 | 10.6876 | 10.683 | 10.7049 | 10.7139 | 10.6824 | 13.7816 | 13.7425 | 13.773 | 13.4206 | 13.421 | 13.3788 | 13.2315 | 13.1645 | 13.1949 | 13.4541 | 13.3976 | 13.362 | 8.4305 | 8.487 | 8.4393 | 13.2092 | 13.2131 | 13.2024 | 13.405 | 13.4526 | 13.4653 | 8.4564 | 8.4328 | 8.4492 | 7.3105 | 7.304 | 7.2915 | 7.2684 | 7.2899 | 7.2883 | 7.2852 | 7.2523 | 7.2289 | 8.4692 | 8.4563 | 8.4225 | 8.4682 | 8.4424 | 8.4431 | 10.7534 | 10.7388 | 10.6701 | 10.7201 | 10.7 | 10.6855 | 13.7548 | 13.6947 | 13.7058 | 13.7238 | 13.721 | 13.6836 | 13.1796 | 13.1356 | 13.1836 | 13.1569 | 13.1216 | 13.142 | 13.3403 | 13.3216 | 13.3353 | 13.4026 | 13.413 | 13.4123 | 13.3658 | 13.3976 | 13.3621 | 8.441 | 8.4216 | 8.4325 | 8.4581 | 8.4487 | 8.434
33 | Discharge SH | ºC | 22.8601 | 23.4816 | 23.6609 | 25.7072 | 25.6162 | 25.72 | 23.0797 | 22.8942 | 22.8991 | 22.8417 | 22.5862 | 22.4006 | 22.1182 | 22.0169 | 21.8955 | 17.5703 | 17.3411 | 17.4621 | 18.5212 | 17.9426 | 17.6529 | 20.2737 | 19.887 | 20.1205 | 19.492 | 19.4996 | 19.3723 | 20.4333 | 20.2775 | 20.0479 | 24.8198 | 24.7321 | 24.7068 | 24.6152 | 24.3861 | 24.2117 | 25.2625 | 28.7816 | 28.7612 | 28.7373 | 28.836 | 28.8567 | 28.8797 | 29.0404 | 29.2228 | 31.978 | 32.0823 | 31.5104 | 29.897 | 29.9585 | 30.1387 | 30.2849 | 30.0503 | 29.9147 | 31.0208 | 31.0542 | 31.1932 | 24.8238 | 24.761 | 24.6522 | 25.192 | 25.2434 | 25.2726 | 22.7931 | 23.0824 | 23.31 | 18.8238 | 18.6786 | 18.4163 | 17.455 | 17.2553 | 23.5433 | 23.5668 | 23.9311 | 20.3127 | 20.2481 | 20.1366 | 19.6627 | 20.3947 | 20.4667 | 20.5079 | 23.0456 | 23.0911 | 23.1146 | 19.3874 | 19.6867 | 19.7657 | 19.8144 | 28.644 | 28.7683 | 28.9679 | 29.1037 | 29.5704 | 30.3734 | 30.6853 | 34.5785 | 34.8248 | 34.0946 | 30.7725 | 30.6428 | 30.4519 | 30.2572 | 30.3266 | 30.2124 | 30.0958 | 29.6308 | 30.0162 | 30.194 | 30.1069 | 27.7159 | 28.1072 | 28.5874 | 29.3735 | 29.6658 | 29.8178 | 26.4922 | 26.6689 | 26.2233 | 20.6321 | 20.5345 | 20.8115 | 29.3654 | 29.1206 | 29.123 | 27.2808 | 27.1218 | 26.8128 | 28.5295 | 28.1986 | 28.6154 | 26.0503 | 26.2762 | 26.1543 | 19.3798 | 19.0757 | 19.2409 | 21.2141 | 21.7933 | 21.7821 | 21.4923 | 20.9033 | 20.5507 | 18.5174 | 18.4945 | 18.3873 | 18.398 | 17.5406 | 17.1837 | 22.4022 | 22.3757 | 22.5068 | 23.2834 | 22.931 | 22.6264 | 30.553 | 29.6166 | 28.6912 | 27.3374 | 27.1873 | 27.2415 | 26.9376 | 27.136 | 27.282 | 27.6477 | 28.4635 | 27.9648 | 21.2429 | 20.7547 | 20.6487 | 29.5114 | 29.5762 | 29.7777 | 29.7355 | 29.4985 | 28.7954 | 19.9406 | 20.2131 | 20.5962 | 18.6414 | 18.5754 | 18.712 | 18.4059 | 18.9403 | 18.8837 | 18.6919 | 18.7919 | 18.838 | 20.2908 | 20.3594 | 20.6041 | 20.2023 | 20.5052 | 20.8835 | 22.93 | 22.6742 | 23.1124 | 23.7644 | 23.5974 | 23.3896 | 30.1806 | 30.0783 | 29.9841 | 29.769 | 29.5098 | 29.4436 | 28.0083 | 28.0309 | 28.067 | 27.918 | 28.0525 | 28.1087 | 28.1958 | 28.1692 | 28.1938 | 28.2152 | 28.2489 | 28.2137 | 27.2136 | 26.9761 | 26.5484 | 20.1355 | 20.2704 | 20.2274 | 20.1256 | 20.1929 | 20.098
34 | Discharge Gauge | ºC | 42.0605 | 41.9742 | 42.0643 | 41.9189 | 41.9884 | 41.8964 | 33.3127 | 33.4284 | 33.3203 | 33.1753 | 33.3374 | 33.3531 | 33.3778 | 33.3276 | 33.2157 | 28.1301 | 28.1355 | 27.9304 | 27.9459 | 28.0763 | 27.9561 | 33.2585 | 33.3611 | 33.2748 | 33.1999 | 33.1852 | 33.2237 | 33.2548 | 33.2635 | 33.3189 | 42.11 | 42.0642 | 41.9961 | 41.9739 | 42.0269 | 41.9722 | 41.9941 | 50.6184 | 50.6287 | 50.6438 | 50.6231 | 50.6199 | 50.6222 | 50.5983 | 50.596 | 51.6816 | 51.6077 | 51.5929 | 50.7159 | 50.6016 | 50.5745 | 50.1176 | 49.9914 | 49.9171 | 51.6045 | 51.6847 | 51.6083 | 41.9923 | 41.9847 | 42.093 | 41.9864 | 41.9546 | 41.9259 | 33.1958 | 33.2926 | 33.264 | 27.9408 | 27.9887 | 28.116 | 28.2755 | 28.0103 | 41.9466 | 41.9109 | 41.9798 | 33.2086 | 33.2265 | 33.2491 | 33.3529 | 33.2742 | 33.2369 | 33.2219 | 33.1624 | 33.1595 | 33.1957 | 28.2804 | 28.3402 | 28.2151 | 28.127 | 50.4144 | 50.5938 | 50.6435 | 50.5774 | 50.635 | 50.5996 | 50.5589 | 50.0349 | 50.0548 | 50.0837 | 50.5626 | 50.6299 | 50.5155 | 50.5203 | 50.1665 | 50.279 | 50.1808 | 49.9641 | 51.633 | 51.6193 | 51.659 | 50.6441 | 50.4592 | 50.5208 | 50.0177 | 49.9065 | 49.9594 | 50.7253 | 50.4856 | 50.5921 | 33.4221 | 33.4285 | 33.1781 | 51.7468 | 51.7586 | 51.7144 | 50.1428 | 50.0446 | 50.0136 | 50.5542 | 50.5793 | 50.5899 | 50.5363 | 50.4656 | 50.4359 | 33.3776 | 33.4519 | 33.2027 | 33.4215 | 33.2672 | 33.3777 | 33.253 | 33.1432 | 33.2089 | 28.0168 | 28.019 | 27.9967 | 28.1069 | 28.0557 | 28.0022 | 42.0257 | 41.8775 | 41.8613 | 41.9388 | 41.9706 | 41.8592 | 51.7887 | 51.6744 | 51.7636 | 50.7242 | 50.7255 | 50.5996 | 50.158 | 49.956 | 50.0477 | 50.824 | 50.6556 | 50.5495 | 33.1809 | 33.4186 | 33.2179 | 50.091 | 50.1027 | 50.0705 | 50.6778 | 50.8195 | 50.8571 | 33.2901 | 33.1905 | 33.2595 | 28.1964 | 28.1658 | 28.1071 | 27.9981 | 28.0995 | 28.0917 | 28.0774 | 27.9221 | 27.8115 | 33.344 | 33.2896 | 33.147 | 33.3398 | 33.2308 | 33.2338 | 42.1095 | 42.0584 | 41.8156 | 41.9923 | 41.9215 | 41.8701 | 51.7103 | 51.5343 | 51.5669 | 51.6196 | 51.6112 | 51.5018 | 50.0017 | 49.8686 | 50.0138 | 49.933 | 49.8263 | 49.8879 | 50.4845 | 50.4287 | 50.4695 | 50.6707 | 50.7016 | 50.6995 | 50.5607 | 50.6558 | 50.5497 | 33.225 | 33.1433 | 33.1891 | 33.2972 | 33.2577 | 33.1957
35
36 | All data
37
38 | Condenser outlet Temp | ºC | 37.2105 | 37.3423 | 37.2127 | 36.9054 | 36.8049 | 36.7335 | 24.0654 | 24.1051 | 24.0312 | 24.2811 | 24.4752 | 24.4257 | 24.376 | 24.2513 | 24.0958 | 21.9118 | 22.0541 | 22.3482 | 19.0591 | 18.4114 | 18.1483 | 27.4108 | 27.3923 | 27.2633 | 26.5907 | 26.6012 | 26.5479 | 26.7285 | 26.9909 | 27.5861 | 37.9778 | 37.8682 | 37.8861 | 37.8739 | 37.927 | 37.8274 | 38.0712 | 47.042 | 47.0223 | 47.0176 | 47.0333 | 47.0596 | 46.996 | 46.9506 | 46.9263 | 48.2574 | 48.2035 | 48.141 | 47.19 | 47.0855 | 47.0239 | 46.3966 | 46.255 | 46.1172 | 47.9247 | 47.9743 | 47.9002 | 37.6329 | 37.8385 | 37.8883 | 37.7473 | 37.7458 | 37.6416 | 24.1266 | 24.0718 | 24.0483 | 19.5164 | 19.3356 | 19.1964 | 18.6829 | 18.4405 | 36.5646 | 36.4489 | 36.7001 | 24.0822 | 24.0712 | 24.0346 | 24.2881 | 24.0144 | 23.9092 | 23.8813 | 23.7302 | 23.7073 | 23.6865 | 18.6384 | 18.5637 | 18.592 | 18.5524 | 47.0129 | 47.3693 | 47.1603 | 47.3929 | 46.9336 | 46.8659 | 47.1338 | 46.1954 | 46.3654 | 46.3368 | 66.6618 | 66.7422 | 66.7591 | 67.0782 | 66.1608 | 65.3907 | 65.4746 | 65.2492 | 62.4113 | 60.9815 | 57.1621 | 48.6308 | 48.5012 | 48.1724 | 46.2014 | 46.1408 | 46.2205 | 50.8492 | 54.2135 | 57.7275 | 28.564 | 28.5002 | 28.3152 | 59.874 | 60.8127 | 60.2066 | 58.2772 | 57.745 | 57.3838 | 48.0522 | 57.8868 | 57.3028 | 55.1901 | 55.1102 | 55.8277 | 28.7745 | 28.7561 | 28.5535 | 23.5561 | 23.3952 | 23.6325 | 23.9307 | 23.7626 | 23.2708 | 19.7988 | 19.7113 | 19.6105 | 19.4813 | 19.0958 | 18.9903 | 37.2631 | 37.0439 | 37.0999 | 37.1578 | 37.0797 | 36.9324 | 48.2986 | 48.117 | 48.1633 | 46.9718 | 46.9266 | 46.8632 | 46.1423 | 46.2223 | 46.2472 | 46.7232 | 46.5312 | 46.4658 | 23.7818 | 24.0447 | 23.7941 | 46.0836 | 46.1058 | 46.1002 | 46.693 | 46.9333 | 46.8215 | 29.5725 | 29.5392 | 29.6174 | 22.0308 | 22.0015 | 21.9461 | 21.9335 | 21.8251 | 21.7626 | 21.3889 | 21.304 | 21.3409 | 24.9123 | 24.8401 | 24.6648 | 25.3003 | 25.065 | 25.079 | 37.4221 | 37.2682 | 36.9689 | 37.4341 | 37.3032 | 37.2519 | 48.03 | 47.8463 | 47.8624 | 47.7371 | 47.8023 | 47.843 | 46.0524 | 45.8107 | 46.1717 | 45.9373 | 45.919 | 45.9901 | 46.5723 | 46.5655 | 46.6306 | 46.7298 | 46.9151 | 46.7764 | 47.0533 | 47.0258 | 46.7697 | 24.6901 | 24.6908 | 24.7448 | 24.7364 | 24.66 | 24.5282
39 | Condenser outlet Pressure | BarA | 10.471 | 10.4609 | 10.4743 | 10.4232 | 10.4393 | 10.4292 | 8.2944 | 8.3183 | 8.2991 | 8.2647 | 8.3095 | 8.3117 | 8.3052 | 8.3037 | 8.2809 | 7.1817 | 7.1755 | 7.1434 | 7.1381 | 7.163 | 7.1439 | 8.2899 | 8.3264 | 8.2914 | 8.2593 | 8.2456 | 8.2656 | 8.2774 | 8.2816 | 8.2883 | 10.4781 | 10.4703 | 10.4593 | 10.4346 | 10.4557 | 10.4419 | 10.4605 | 12.9986 | 12.9892 | 13.0031 | 12.9944 | 12.9954 | 12.9767 | 12.9869 | 12.9922 | 13.3806 | 13.363 | 13.3493 | 13.0068 | 12.971 | 12.9539 | 12.8081 | 12.7534 | 12.7318 | 13.3953 | 13.4149 | 13.4024 | 10.49 | 10.4827 | 10.5129 | 10.472 | 10.4938 | 10.4711 | 8.2971 | 8.327 | 8.3119 | 7.16 | 7.1854 | 7.2051 | 7.228 | 7.1724 | 10.4688 | 10.4474 | 10.473 | 8.297 | 8.3109 | 8.3029 | 8.3288 | 8.3157 | 8.3046 | 8.3095 | 8.2741 | 8.2838 | 8.2881 | 7.2382 | 7.2551 | 7.2254 | 7.211 | 12.9908 | 13.0426 | 13.0557 | 13.0323 | 13.0132 | 12.9853 | 12.9845 | 12.8171 | 12.8274 | 12.8091 | 12.957 | 12.9697 | 12.932 | 12.9599 | 12.827 | 12.8467 | 12.817 | 12.7393 | 13.2783 | 13.3158 | 13.3138 | 12.9429 | 12.8841 | 12.9105 | 12.7096 | 12.6638 | 12.6777 | 13.0073 | 12.938 | 12.9628 | 8.3136 | 8.32 | 8.2621 | 13.3887 | 13.3833 | 13.3579 | 12.7786 | 12.7391 | 12.733 | 12.9149 | 12.9196 | 12.9148 | 12.9539 | 12.9369 | 12.923 | 8.3149 | 8.3156 | 8.272 | 8.3288 | 8.2851 | 8.3095 | 8.293 | 8.2718 | 8.2751 | 7.1686 | 7.1471 | 7.1572 | 7.1894 | 7.1705 | 7.1536 | 10.4836 | 10.4276 | 10.4293 | 10.4381 | 10.4373 | 10.4068 | 13.4028 | 13.3585 | 13.3826 | 12.9728 | 12.9793 | 12.9281 | 12.7836 | 12.723 | 12.7363 | 13.0521 | 12.9917 | 12.9708 | 8.2546 | 8.3155 | 8.2593 | 12.7556 | 12.7604 | 12.7499 | 12.9534 | 13.0018 | 13.014 | 8.2825 | 8.2573 | 8.26 | 7.1867 | 7.1758 | 7.1642 | 7.1377 | 7.1739 | 7.1781 | 7.1686 | 7.136 | 7.0996 | 8.2892 | 8.28 | 8.2502 | 8.3102 | 8.2667 | 8.2647 | 10.4944 | 10.4811 | 10.4174 | 10.4312 | 10.4123 | 10.4016 | 13.3797 | 13.3189 | 13.3331 | 13.346 | 13.3387 | 13.3051 | 12.745 | 12.6936 | 12.7551 | 12.7237 | 12.6872 | 12.7048 | 12.9062 | 12.8878 | 12.8957 | 12.9672 | 12.9839 | 12.9825 | 12.988 | 13.0263 | 12.9747 | 8.2458 | 8.2318 | 8.2436 | 8.2712 | 8.2621 | 8.2419
40 | Condenser outlet gauge | ºC | 41.1067 | 41.0703 | 41.1183 | 40.9349 | 40.9926 | 40.9563 | 32.6028 | 32.7046 | 32.6226 | 32.4757 | 32.6671 | 32.6766 | 32.6489 | 32.6425 | 32.5448 | 27.5871 | 27.5575 | 27.4041 | 27.3791 | 27.4976 | 27.4068 | 32.5833 | 32.7392 | 32.5899 | 32.4523 | 32.3937 | 32.4793 | 32.5301 | 32.5478 | 32.5768 | 41.1321 | 41.1042 | 41.0644 | 40.9759 | 41.0518 | 41.0019 | 41.0689 | 49.4525 | 49.4236 | 49.4662 | 49.4395 | 49.4426 | 49.3855 | 49.4166 | 49.4328 | 50.605 | 50.5524 | 50.5116 | 49.4775 | 49.3681 | 49.3158 | 48.8681 | 48.6991 | 48.6323 | 50.6487 | 50.7072 | 50.67 | 41.1746 | 41.1486 | 41.2568 | 41.1101 | 41.1884 | 41.1068 | 32.614 | 32.7417 | 32.6776 | 27.4837 | 27.6047 | 27.6983 | 27.8071 | 27.5428 | 41.0988 | 41.0219 | 41.1136 | 32.6136 | 32.673 | 32.6391 | 32.7494 | 32.6935 | 32.6463 | 32.6672 | 32.5159 | 32.5574 | 32.5758 | 27.8551 | 27.9351 | 27.7946 | 27.7264 | 49.4285 | 49.5865 | 49.6264 | 49.5552 | 49.4969 | 49.4118 | 49.4093 | 48.8959 | 48.9276 | 48.8712 | 49.3253 | 49.3643 | 49.2487 | 49.3342 | 48.9264 | 48.9871 | 48.8955 | 48.6555 | 50.2988 | 50.4112 | 50.4052 | 49.2823 | 49.1022 | 49.183 | 48.5634 | 48.4213 | 48.4645 | 49.4789 | 49.2672 | 49.3431 | 32.6848 | 32.712 | 32.4643 | 50.6291 | 50.6129 | 50.5372 | 48.777 | 48.655 | 48.636 | 49.1964 | 49.211 | 49.1962 | 49.3158 | 49.2639 | 49.2214 | 32.6902 | 32.6931 | 32.5071 | 32.7496 | 32.5629 | 32.6673 | 32.5967 | 32.5059 | 32.52 | 27.5244 | 27.422 | 27.4701 | 27.6236 | 27.5339 | 27.4531 | 41.1516 | 40.9505 | 40.9567 | 40.9883 | 40.9856 | 40.8757 | 50.6712 | 50.5389 | 50.6109 | 49.3737 | 49.3934 | 49.237 | 48.7924 | 48.6051 | 48.6461 | 49.6154 | 49.4314 | 49.3675 | 32.4323 | 32.6926 | 32.4524 | 48.706 | 48.7207 | 48.6883 | 49.3144 | 49.4623 | 49.4993 | 32.5517 | 32.444 | 32.4553 | 27.6106 | 27.559 | 27.5036 | 27.3768 | 27.5498 | 27.5699 | 27.5244 | 27.3688 | 27.1944 | 32.5805 | 32.541 | 32.4133 | 32.67 | 32.484 | 32.4757 | 41.1905 | 41.1426 | 40.914 | 40.9637 | 40.8956 | 40.8569 | 50.6023 | 50.4206 | 50.4631 | 50.5016 | 50.4799 | 50.379 | 48.6733 | 48.5138 | 48.7043 | 48.6072 | 48.4938 | 48.5486 | 49.17 | 49.1132 | 49.1376 | 49.3565 | 49.4075 | 49.4033 | 49.4199 | 49.5368 | 49.3793 | 32.3944 | 32.3344 | 32.385 | 32.5032 | 32.4646 | 32.3776
41 | Condenser outlet enthalpy | KJ/kg | 252.2495 | 252.4449 | 252.2528 | 251.7986 | 251.6499 | 251.5445 | 233.2231 | 233.2796 | 233.1747 | 233.5292 | 233.805 | 233.7347 | 233.6641 | 233.487 | 233.2662 | 230.1701 | 230.3709 | 230.786 | 226.1608 | 225.2551 | 224.8874 | 237.9936 | 237.967 | 237.7822 | 236.8195 | 236.8345 | 236.7583 | 237.0165 | 237.392 | 238.2449 | 253.3872 | 253.2247 | 253.2514 | 253.2337 | 253.3122 | 253.1646 | 253.5263 | 267.0342 | 267.0041 | 266.9964 | 267.0209 | 267.0615 | 266.9641 | 266.8937 | 266.8561 | 268.8998 | 268.8168 | 268.7205 | 267.2622 | 267.1022 | 267.0078 | 266.047 | 265.8311 | 265.6201 | 268.3838 | 268.4599 | 268.3455 | 252.8752 | 253.1804 | 253.2538 | 253.0453 | 253.0427 | 252.8884 | 233.31 | 233.2324 | 233.1989 | 226.8014 | 226.5484 | 226.3535 | 225.6353 | 225.2958 | 251.2944 | 251.1238 | 251.4945 | 233.2471 | 233.2314 | 233.1795 | 233.5394 | 233.151 | 233.0016 | 232.9621 | 232.7478 | 232.7154 | 232.6859 | 225.5731 | 225.4689 | 225.5081 | 225.4527 | 266.9896 | 267.5376 | 267.2147 | 267.5745 | 266.8665 | 266.7632 | 267.1763 | 265.7374 | 265.9983 | 265.9549 | 443.399 | 443.4655 | 443.5539 | 443.8593 | 443.0788 | 442.1807 | 442.3303 | 442.2234 | 437.965 | 436.2408 | 431.781 | 269.4961 | 269.2969 | 268.7855 | 265.7501 | 265.6585 | 265.7805 | 424.9335 | 429.1528 | 433.2195 | 239.6496 | 239.5577 | 239.2919 | 434.8007 | 435.9044 | 435.2536 | 434.2505 | 433.7222 | 433.319 | 268.599 | 433.4979 | 432.8308 | 430.2709 | 430.2156 | 431.0907 | 239.9526 | 239.926 | 239.6345 | 232.5013 | 232.2733 | 232.6095 | 233.0321 | 232.7936 | 232.0971 | 227.1975 | 227.0746 | 226.9334 | 226.7525 | 226.2124 | 226.0646 | 252.3272 | 252.0035 | 252.0863 | 252.1719 | 252.0564 | 251.8388 | 268.9627 | 268.683 | 268.7537 | 266.9268 | 266.8569 | 266.761 | 265.657 | 265.7819 | 265.8196 | 266.5412 | 266.2479 | 266.148 | 232.8208 | 233.1939 | 232.8383 | 265.5678 | 265.6018 | 265.5934 | 266.4981 | 266.8665 | 266.6939 | 241.103 | 241.055 | 241.1679 | 230.3381 | 230.2967 | 230.2184 | 230.2004 | 230.0477 | 229.9596 | 229.4328 | 229.3129 | 229.3646 | 234.4262 | 234.3235 | 234.0741 | 234.9785 | 234.6434 | 234.6633 | 252.5626 | 252.3349 | 251.8927 | 252.5814 | 252.3877 | 252.3118 | 268.5474 | 268.2651 | 268.2896 | 268.0953 | 268.1964 | 268.2606 | 265.5202 | 265.1511 | 265.703 | 265.3443 | 265.3173 | 265.4259 | 266.3138 | 266.304 | 266.404 | 266.5543 | 266.839 | 266.6254 | 267.052 | 267.0083 | 266.6154 | 234.1101 | 234.111 | 234.1878 | 234.1759 | 234.0674 | 233.8799
42 | Condenser outlet specific volume | m3/kg | 0.00086263 | 0.00086306 | 0.00086263 | 0.00086167 | 0.00086134 | 0.00086112 | 0.00082554 | 0.00082564 | 0.00082545 | 0.00082612 | 0.00082662 | 0.00082649 | 0.00082636 | 0.00082603 | 0.00082563 | 0.0008204 | 0.00082076 | 0.00082153 | 0.00081325 | 0.00081165 | 0.00081102 | 0.00083456 | 0.00083449 | 0.00083415 | 0.00083232 | 0.00083235 | 0.0008322 | 0.00083269 | 0.0008334 | 0.00083504 | 0.00086511 | 0.00086476 | 0.00086482 | 0.0008648 | 0.00086496 | 0.00086464 | 0.00086542 | 0.00089552 | 0.00089545 | 0.00089542 | 0.00089549 | 0.00089559 | 0.00089536 | 0.00089517 | 0.00089507 | 0.00089996 | 0.00089976 | 0.00089952 | 0.00089608 | 0.00089571 | 0.00089548 | 0.00089319 | 0.00089269 | 0.00089218 | 0.00089863 | 0.00089881 | 0.00089853 | 0.00086398 | 0.00086465 | 0.0008648 | 0.00086436 | 0.00086434 | 0.00086402 | 0.0008257 | 0.00082555 | 0.00082549 | 0.00081437 | 0.00081392 | 0.00081357 | 0.0008123 | 0.00081172 | 0.00086056 | 0.00086021 | 0.00086099 | 0.00082559 | 0.00082555 | 0.00082546 | 0.00082612 | 0.0008254 | 0.00082513 | 0.00082505 | 0.00082467 | 0.00082461 | 0.00082455 | 0.00081218 | 0.00081199 | 0.00081207 | 0.00081198 | 0.00089541 | 0.00089675 | 0.00089593 | 0.00089685 | 0.00089509 | 0.00089485 | 0.00089588 | 0.00089241 | 0.00089305 | 0.00089296 | 0.017382 | 0.017368 | 0.017435 | 0.01742 | 0.017553 | 0.017437 | 0.017498 | 0.01761 | 0.01639 | 0.016172 | 0.015743 | 0.00090182 | 0.00090135 | 0.00090002 | 0.00089252 | 0.00089233 | 0.00089262 | 0.015485 | 0.016018 | 0.016389 | 0.00083776 | 0.00083758 | 0.00083708 | 0.015931 | 0.016045 | 0.016018 | 0.016769 | 0.016777 | 0.016746 | 0.00089954 | 0.016481 | 0.016422 | 0.016108 | 0.016127 | 0.016236 | 0.00083835 | 0.0008383 | 0.00083775 | 0.0008242 | 0.00082379 | 0.0008244 | 0.00082519 | 0.00082476 | 0.00082347 | 0.00081507 | 0.00081486 | 0.00081461 | 0.00081428 | 0.00081333 | 0.00081308 | 0.00086279 | 0.00086212 | 0.00086229 | 0.00086248 | 0.00086223 | 0.00086177 | 0.0009001 | 0.00089942 | 0.00089958 | 0.00089526 | 0.00089509 | 0.00089488 | 0.00089224 | 0.00089259 | 0.00089267 | 0.00089425 | 0.00089356 | 0.00089332 | 0.00082482 | 0.00082548 | 0.00082485 | 0.00089204 | 0.00089212 | 0.00089211 | 0.00089421 | 0.00089509 | 0.00089465 | 0.00084063 | 0.00084055 | 0.00084077 | 0.0008207 | 0.00082063 | 0.00082049 | 0.00082047 | 0.00082018 | 0.00082002 | 0.00081907 | 0.00081886 | 0.00081897 | 0.00082778 | 0.0008276 | 0.00082714 | 0.00082881 | 0.0008282 | 0.00082824 | 0.00086329 | 0.00086281 | 0.00086188 | 0.00086337 | 0.00086296 | 0.0008628 | 0.00089906 | 0.00089839 | 0.00089844 | 0.00089794 | 0.0008982 | 0.00089839 | 0.00089193 | 0.00089105 | 0.00089237 | 0.00089151 | 0.00089147 | 0.00089172 | 0.00089378 | 0.00089377 | 0.00089401 | 0.00089434 | 0.00089504 | 0.0008945 | 0.00089557 | 0.00089543 | 0.00089449 | 0.00082721 | 0.00082722 | 0.00082736 | 0.00082732 | 0.00082713 | 0.00082678
43 | Oil flow(from Coriolis meter) | m3/hr | 3.3203 | 3.1158 | 2.9665 | 3.3055 | 3.3343 | 3.4 | 1.2898 | -0.087323 | -0.087149 | -0.08721 | -0.087407 | -0.087445 | -0.087371 | -0.087287 | -0.087356 | -0.087435 | -0.08743 | -0.087407 | 1.1153 | 1.3586 | 0.95133 | 1.7877 | 1.7826 | 1.7745 | 1.8736 | 1.8327 | 1.798 | 1.7297 | 1.7758 | 1.8303 | 3.2635 | 2.9657 | 2.9667 | 3.4473 | 3.4487 | 3.4911 | 3.1709 | 3.5254 | 3.4988 | 3.4647 | 3.4244 | 3.5817 | 3.4874 | 3.396 | 3.5166 | 3.3631 | 3.4401 | 3.409 | 3.3709 | 3.4555 | 3.4289 | 3.3061 | 3.3695 | 3.2814 | 3.1415 | 3.227 | 3.4368 | 2.4513 | 2.8303 | 2.3925 | 2.7399 | 2.8007 | 2.6863 | 1.7121 | 1.6289 | 1.7105 | 0.95405 | 0.96186 | 0.9611 | 0.95635 | 0.94654 | 3.3347 | 3.225 | 2.9106 | 1.7246 | 1.6962 | 1.815 | 1.7036 | 1.7167 | 1.6121 | 1.6906 | 1.0886 | 0.97593 | 0.76148 | -0.087224 | 1.2108 | 1.632 | 1.2297 | 3.438 | 3.3868 | 3.4775 | 3.4096 | 3.4376 | 3.3661 | 3.1758 | 3.3718 | 3.434 | 3.3974 | 3.0165 | 3.2518 | 3.4668 | 3.1946 | 3.0268 | 3.0704 | 3.4377 | 2.8544 | 2.4486 | 2.4486 | 2.4395 | 2.2385 | 2.3954 | 2.4339 | 2.3551 | 2.33 | 2.3509 | 2.3829 | 2.6506 | 2.1368 | 1.0563 | 1.0465 | 1.0489 | 2.4192 | 2.4118 | 2.4414 | 2.8753 | 3.1463 | 2.9777 | 2.8234 | 2.9772 | 2.7899 | 2.4674 | 2.4217 | 2.4947 | 1.6339 | 1.7331 | 1.6461 | 1.087 | 1.0489 | 1.0594 | 1.0384 | 1.1851 | 0.99594 | -0.087317 | 0.63614 | -0.087444 | 0.64103 | -0.087417 | 1.1103 | 2.1786 | 2.1492 | 1.986 | 2.4165 | 2.3444 | 2.5862 | 2.5215 | 2.5056 | 2.6371 | 2.8738 | 3.0474 | 3.0115 | 2.8429 | 3.0321 | 3.1359 | 2.8283 | 3.2098 | 2.9735 | 1.668 | 1.7092 | 1.7219 | 3.1612 | 3.2919 | 3.3233 | 3.0149 | 3.2999 | 3.008 | 1.7411 | 1.7201 | 1.5864 | 1.4902 | 0.91062 | 0.83756 | 0.83674 | 0.85483 | 0.87748 | 0.83415 | 0.842 | 0.82669 | 1.7246 | 1.7393 | 1.6357 | 1.6306 | 1.4592 | 1.3668 | 2.3871 | 2.5857 | 2.1973 | 2.8468 | 2.9008 | 2.8286 | 3.3881 | 3.2277 | 2.8084 | 2.9125 | 3.2939 | 3.1877 | 3.342 | 3.4541 | 3.4921 | 3.445 | 3.6332 | 3.3433 | 3.49 | 3.3309 | 3.5313 | 3.6822 | 3.4381 | 3.2007 | 3.5994 | 3.4482 | 3.5546 | 1.6782 | 1.6647 | 1.668 | 1.6664 | 1.7121 | 1.795
44 | Liquid subcoooling | ºC | 3.8962 | 3.728 | 3.9056 | 4.0295 | 4.1878 | 4.2228 | 8.5374 | 8.5995 | 8.5914 | 8.1946 | 8.1919 | 8.2509 | 8.2729 | 8.3912 | 8.4491 | 5.6753 | 5.5034 | 5.0559 | 8.32 | 9.0863 | 9.2585 | 5.1725 | 5.3469 | 5.3265 | 5.8616 | 5.7925 | 5.9313 | 5.8017 | 5.5569 | 4.9907 | 3.1543 | 3.236 | 3.1783 | 3.1019 | 3.1248 | 3.1745 | 2.9977 | 2.4105 | 2.4014 | 2.4486 | 2.4062 | 2.3829 | 2.3895 | 2.4659 | 2.5065 | 2.3475 | 2.3489 | 2.3706 | 2.2875 | 2.2825 | 2.2919 | 2.4714 | 2.444 | 2.5151 | 2.724 | 2.7329 | 2.7698 | 3.5417 | 3.3101 | 3.3685 | 3.3628 | 3.4426 | 3.4652 | 8.4875 | 8.6699 | 8.6293 | 7.9673 | 8.2691 | 8.5019 | 9.1242 | 9.1024 | 4.5341 | 4.5731 | 4.4135 | 8.5314 | 8.6018 | 8.6046 | 8.4613 | 8.6791 | 8.7371 | 8.786 | 8.7857 | 8.8501 | 8.8893 | 9.2167 | 9.3713 | 9.2026 | 9.174 | 2.4156 | 2.2173 | 2.4661 | 2.1623 | 2.5633 | 2.5459 | 2.2755 | 2.7005 | 2.5622 | 2.5344 | no subcooling | no subcooling | no subcooling | no subcooling | no subcooling | no subcooling | no subcooling | no subcooling | no subcooling | no subcooling | no subcooling | 0.65151 | 0.601 | 1.0105 | 2.362 | 2.2805 | 2.244 | no subcooling | no subcooling | no subcooling | 4.1208 | 4.2119 | 4.1491 | no subcooling | no subcooling | no subcooling | no subcooling | no subcooling | no subcooling | 1.1442 | no subcooling | no subcooling | no subcooling | no subcooling | no subcooling | 3.9157 | 3.937 | 3.9536 | 9.1935 | 9.1677 | 9.0348 | 8.666 | 8.7433 | 9.2492 | 7.7255 | 7.7107 | 7.8595 | 8.1424 | 8.4381 | 8.4628 | 3.8886 | 3.9066 | 3.8568 | 3.8305 | 3.9059 | 3.9433 | 2.3726 | 2.4219 | 2.4476 | 2.4019 | 2.4668 | 2.3738 | 2.6501 | 2.3827 | 2.399 | 2.8922 | 2.9002 | 2.9017 | 8.6505 | 8.6479 | 8.6583 | 2.6224 | 2.6149 | 2.5881 | 2.6214 | 2.529 | 2.6778 | 2.9793 | 2.9048 | 2.8379 | 5.5798 | 5.5575 | 5.5575 | 5.4434 | 5.7247 | 5.8073 | 6.1355 | 6.0648 | 5.8535 | 7.6682 | 7.7008 | 7.7485 | 7.3697 | 7.419 | 7.3967 | 3.7685 | 3.8744 | 3.9451 | 3.5295 | 3.5924 | 3.6051 | 2.5722 | 2.5744 | 2.6006 | 2.7646 | 2.6776 | 2.536 | 2.6209 | 2.7031 | 2.5326 | 2.6699 | 2.5748 | 2.5585 | 2.5977 | 2.5478 | 2.5069 | 2.6267 | 2.4924 | 2.6269 | 2.3666 | 2.5109 | 2.6096 | 7.7042 | 7.6437 | 7.6402 | 7.7669 | 7.8046 | 7.8495
45 | Condenser Duty (refrigerant side) | kw | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
46 | Water inlet Temp | ºC | 19.1706 | 19.2579 | 19.2399 | 19.3284 | 19.195 | 19.2122 | 16.3518 | 16.3348 | 16.1146 | 15.946 | 15.8575 | 15.7966 | 15.5707 | 15.5261 | 15.421 | 15.5106 | 15.2922 | 14.4391 | 13.8599 | 16.2164 | 17.8913 | 13.3663 | 13.2669 | 13.1478 | 13.2412 | 13.371 | 13.4436 | 13.6418 | 13.7093 | 13.853 | 16.1733 | 16.0673 | 16.0418 | 16.064 | 16.1212 | 16.0748 | 17.7088 | 19.5885 | 19.5834 | 19.5744 | 19.5845 | 19.599 | 19.6388 | 19.6134 | 19.3662 | 19.8731 | 19.9867 | 20.0976 | 19.5893 | 19.5332 | 19.5603 | 19.4082 | 19.2273 | 19.0251 | 20.7719 | 20.7342 | 20.8174 | 15.4273 | 15.3216 | 15.2496 | 15.2471 | 15.1754 | 15.1093 | 13.9511 | 13.8172 | 13.6947 | 12.6948 | 13.0823 | 13.7749 | 18.1605 | 18.0699 | 17.7684 | 17.9092 | 17.8826 | 13.815 | 13.8442 | 13.8815 | 13.8543 | 13.8974 | 13.8801 | 13.8312 | 13.4268 | 13.3494 | 13.3756 | 15.9948 | 15.8921 | 15.852 | 15.8267 | 20.1856 | 20.0852 | 20.1214 | 20.136 | 20.5078 | 20.4149 | 20.3691 | 20.1037 | 19.9334 | 19.4516 | 28.874 | 28.8325 | 28.7274 | 28.699 | 28.4905 | 28.3242 | 28.2643 | 28.1149 | 21.4464 | 21.4876 | 21.5159 | 21.2924 | 21.2721 | 21.2758 | 21.2081 | 21.0269 | 20.8481 | 20.2567 | 19.6765 | 20.0889 | 13.6438 | 13.6113 | 13.5818 | 33.3389 | 36.6842 | 37.3747 | 37.4102 | 36.2679 | 35.6916 | 22.9187 | 37.6857 | 40.7735 | 40.0671 | 40.3214 | 40.6087 | 12.7142 | 12.6812 | 12.6039 | 13.639 | 13.5863 | 13.5706 | 12.6107 | 12.4486 | 12.2551 | 13.9622 | 13.9383 | 13.8689 | 13.8046 | 13.6867 | 13.6523 | 17.3045 | 17.5048 | 17.534 | 17.8022 | 17.7281 | 17.6796 | 19.6289 | 19.5284 | 19.3725 | 19.1337 | 19.015 | 18.9288 | 18.9337 | 18.8658 | 18.7066 | 18.1262 | 18.0776 | 18.0933 | 12.1947 | 11.0955 | 11.0197 | 22.8478 | 22.8397 | 22.8634 | 22.4285 | 22.2296 | 22.1522 | 16.7922 | 16.7968 | 16.7683 | 13.8599 | 13.8556 | 13.9048 | 13.8986 | 13.8774 | 13.8506 | 13.8596 | 13.8718 | 13.8706 | 15.5947 | 15.5573 | 15.5764 | 15.7517 | 15.783 | 15.836 | 17.4464 | 17.4045 | 17.5036 | 17.4811 | 17.3589 | 17.2905 | 21.9983 | 21.8195 | 21.6713 | 21.7713 | 21.8011 | 21.8634 | 22.7172 | 22.7104 | 22.8797 | 22.9844 | 23.043 | 23.0751 | 22.9855 | 22.9045 | 22.8251 | 22.6153 | 22.5436 | 22.1909 | 21.7036 | 21.6659 | 21.7369 | 15.2273 | 15.3691 | 15.4407 | 15.4798 | 15.4756 | 15.4363
47 | Water outlet temp | ºC | 44.9395 | 47.2846 | 45.8457 | 50.1188 | 47.1407 | 48.3521 | 36.4704 | 35.9823 | 36.2697 | 32.8356 | 34.3842 | 32.7164 | 31.7966 | 32.1115 | 32.9647 | 20.0584 | 15.5873 | 15.4895 | 16.5552 | 19.5249 | 15.1391 | 21.4277 | 19.7597 | 20.6889 | 24.9823 | 24.8287 | 29.4682 | 27.2473 | 25.5081 | 27.071 | 36.5213 | 42.202 | 37.9827 | 38.8177 | 36.3446 | 35.3697 | 37.5654 | 47.5238 | 45.5295 | 48.5766 | 50.1006 | 46.1432 | 46.632 | 49.6106 | 46.0687 | 53.156 | 53.7208 | 49.2415 | 52.4622 | 49.8108 | 48.4789 | 52.862 | 54.0405 | 50.7946 | 57.664 | 61.944 | 61.3853 | 38.7612 | 39.793 | 36.3515 | 40.8879 | 35.7884 | 37.9032 | 29.6009 | 30.4048 | 29.329 | 18.7343 | 18.253 | 19.3824 | 14.3899 | 15.2207 | 47.0884 | 47.5911 | 46.9919 | 30.6469 | 29.6385 | 29.7104 | 27.5687 | 28.6781 | 28.6398 | 29.7591 | 29.9805 | 30.0481 | 30.5321 | 12.702 | 13.6852 | 14.3204 | 13.0383 | 47.837 | 48.3072 | 34.9512 | 50.805 | 48.2934 | 49.9925 | 55.7676 | 59.7699 | 58.827 | 54.7037 | 34.7344 | 34.3884 | 34.4314 | 31.0737 | 38.1057 | 35.0242 | 33.4602 | 36.5148 | 39.1721 | 42.9336 | 39.0972 | 47.2853 | 42.5878 | 46.753 | 44.869 | 50.6929 | 51.1671 | 36.9144 | 48.3349 | 39.7977 | 25.8963 | 23.517 | 25.3456 | 49.6756 | 37.7648 | 40.5525 | 35.2966 | 37.0462 | 35.5421 | 42.004 | 47.9044 | 38.4117 | 40.1793 | 36.5618 | 39.2312 | 22.381 | 22.1141 | 22.1801 | 34.9776 | 35.7639 | 33.8167 | 33.5131 | 32.4609 | 33.0911 | 21.8727 | 21.3105 | 19.6911 | 20.9913 | 21.1958 | 20.5297 | 44.9197 | 47.9299 | 47.2804 | 48.4287 | 46.177 | 49.6908 | 53.6828 | 54.1247 | 53.4829 | 51.7569 | 51.2061 | 57.7445 | 56.3868 | 51.9502 | 54.8903 | 61.2735 | 56.6091 | 58.1285 | 33.711 | 33.8634 | 33.4014 | 61.5977 | 62.4826 | 61.2339 | 63.0719 | 63.2921 | 64.1162 | 34.1938 | 33.6383 | 34.7775 | 23.6567 | 23.2878 | 24.764 | 24.2498 | 23.4029 | 23.3206 | 24.3567 | 22.4373 | 23.724 | 32.1819 | 32.9339 | 31.4323 | 33.0071 | 33.3826 | 30.7415 | 50.3499 | 49.7721 | 50.0473 | 48.6153 | 46.4038 | 50.6604 | 71.9227 | 70.1114 | 70.8323 | 71.3189 | 70.3842 | 67.3117 | 68.8988 | 63.2164 | 66.8354 | 68.4861 | 68.145 | 68.8372 | 68.4802 | 67.1532 | 67.2391 | 67.378 | 68.9007 | 71.4628 | 63.0812 | 67.8563 | 63.5068 | 31.419 | 32.195 | 30.9939 | 31.3879 | 32.293 | 32.7841
48 | Water Flow rate (calculated) | m3/hr | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
49
50 | Liquid line strainers temp | ºC | 29.7919 | 29.6403 | 29.7927 | 29.731 | 29.5642 | 29.455 | 21.8173 | 21.8672 | 21.609 | 21.6596 | 21.7639 | 21.7194 | 21.698 | 21.508 | 21.4127 | 17.2275 | 17.1544 | 17.0246 | 17.2791 | 17.2687 | 17.1197 | 19.3802 | 19.5041 | 19.4294 | 19.8333 | 19.9069 | 19.9265 | 19.9314 | 19.9789 | 19.9628 | 28.2511 | 28.1549 | 28.1877 | 27.7717 | 27.9333 | 27.8063 | 27.5638 | 35.1703 | 35.1374 | 35.1211 | 35.1275 | 35.1411 | 34.968 | 35.0275 | 35.0547 | 35.5169 | 35.4045 | 35.5792 | 34.0782 | 33.9412 | 33.8676 | 33.6533 | 33.4583 | 33.1871 | 35.291 | 35.3984 | 35.336 | 26.7387 | 27.0113 | 26.8133 | 26.5493 | 26.5671 | 26.4097 | 19.5811 | 19.5401 | 19.3927 | 16.1917 | 16.2726 | 16.384 | 16.6414 | 16.3755 | 27.8706 | 27.5711 | 27.7412 | 19.1731 | 19.1998 | 19.1668 | 19.0656 | 18.9145 | 18.8172 | 18.7174 | 18.1569 | 18.1129 | 18.0443 | 14.4297 | 14.4271 | 14.4092 | 14.451 | 33.076 | 33.2669 | 33.0264 | 33.2927 | 32.2822 | 32.212 | 32.5648 | 31.3818 | 32.2057 | 31.5219 | 35.9596 | 36.12 | 35.8515 | 35.8122 | 35.3043 | 35.5121 | 35.4678 | 35.1191 | 36.357 | 36.6341 | 36.6941 | 35.5966 | 35.2948 | 35.3649 | 34.878 | 34.9249 | 35.1476 | 36.6823 | 36.6097 | 36.3613 | 20.2797 | 20.2475 | 20.0054 | 37.6986 | 37.483 | 37.5144 | 35.1415 | 35.0416 | 35.0195 | 35.8057 | 35.6554 | 35.5957 | 36.7519 | 36.5958 | 36.5478 | 20.3036 | 20.4673 | 20.3016 | 22.6112 | 22.4146 | 22.4245 | 22.4484 | 22.279 | 22.4022 | 19.0951 | 19.0934 | 19.0829 | 19.1539 | 19.2934 | 19.1855 | 30.9115 | 30.6281 | 30.6611 | 30.2285 | 30.1831 | 30.0949 | 38.4898 | 38.181 | 38.1918 | 36.7929 | 36.7892 | 36.5988 | 35.9225 | 35.7306 | 35.7006 | 38.4095 | 38.1857 | 38.3361 | 21.6485 | 21.7534 | 21.5388 | 37.0339 | 36.9675 | 36.9494 | 37.5945 | 38.0217 | 38.2088 | 25.9783 | 25.8637 | 25.8889 | 19.6174 | 19.5974 | 19.5686 | 19.5173 | 19.5821 | 19.5598 | 19.4635 | 19.2697 | 19.0973 | 23.0721 | 22.9994 | 22.8035 | 23.2213 | 23.1104 | 23.0651 | 32.4691 | 32.3974 | 32.154 | 31.5886 | 31.5313 | 31.4165 | 40.4617 | 40.2111 | 40.2838 | 40.3378 | 40.1942 | 40.2262 | 38.4128 | 38.121 | 38.5167 | 38.1468 | 38.0696 | 38.2043 | 39.0074 | 38.9281 | 38.9821 | 38.8468 | 39.4238 | 39.2126 | 39.5855 | 39.6867 | 39.4894 | 22.3963 | 22.2825 | 22.3756 | 22.5878 | 22.5137 | 22.4184
51 | Liquid line strainers pressure | BarA | 10.3828 | 10.3634 | 10.3768 | 10.3394 | 10.3383 | 10.3277 | 8.2585 | 8.303 | 8.2708 | 8.2441 | 8.2933 | 8.301 | 8.2912 | 8.2769 | 8.27 | 7.1722 | 7.1567 | 7.1381 | 7.134 | 7.1345 | 7.1247 | 8.2672 | 8.2911 | 8.2498 | 8.2157 | 8.2031 | 8.2106 | 8.2368 | 8.2198 | 8.2558 | 10.3897 | 10.3653 | 10.3477 | 10.3453 | 10.3319 | 10.3332 | 10.3597 | 12.8745 | 12.8619 | 12.8733 | 12.8773 | 12.8779 | 12.8588 | 12.8556 | 12.8539 | 13.2649 | 13.2267 | 13.2111 | 12.8946 | 12.8459 | 12.8259 | 12.6775 | 12.6341 | 12.5907 | 13.2516 | 13.281 | 13.2825 | 10.3842 | 10.4104 | 10.4288 | 10.4015 | 10.3998 | 10.3931 | 8.2688 | 8.2896 | 8.2865 | 7.1585 | 7.168 | 7.191 | 7.2348 | 7.1713 | 10.3564 | 10.36 | 10.3599 | 8.2802 | 8.2849 | 8.28 | 8.3125 | 8.2815 | 8.2834 | 8.2725 | 8.2486 | 8.2517 | 8.2699 | 7.2271 | 7.2361 | 7.2182 | 7.1957 | 12.854 | 12.9301 | 12.946 | 12.9293 | 12.8835 | 12.8626 | 12.8586 | 12.6828 | 12.6903 | 12.6839 | 12.7984 | 12.823 | 12.7871 | 12.7981 | 12.6595 | 12.6962 | 12.6586 | 12.591 | 13.1417 | 13.1712 | 13.1865 | 12.7768 | 12.7235 | 12.7404 | 12.5484 | 12.5193 | 12.5504 | 12.8694 | 12.8014 | 12.8415 | 8.3089 | 8.3144 | 8.2466 | 13.2443 | 13.2325 | 13.2168 | 12.6372 | 12.589 | 12.5783 | 12.763 | 12.7622 | 12.7777 | 12.815 | 12.8048 | 12.797 | 8.2864 | 8.3042 | 8.2654 | 8.2954 | 8.2568 | 8.2908 | 8.2713 | 8.2379 | 8.2517 | 7.1445 | 7.1607 | 7.1396 | 7.1718 | 7.1576 | 7.1414 | 10.3696 | 10.3265 | 10.3218 | 10.3236 | 10.3393 | 10.2928 | 13.2456 | 13.2288 | 13.229 | 12.8331 | 12.8263 | 12.7862 | 12.6396 | 12.5837 | 12.5961 | 12.9097 | 12.8599 | 12.8321 | 8.2176 | 8.2781 | 8.2282 | 12.6131 | 12.6181 | 12.61 | 12.794 | 12.8459 | 12.8796 | 8.2368 | 8.228 | 8.2376 | 7.1755 | 7.173 | 7.152 | 7.1424 | 7.1688 | 7.1674 | 7.1484 | 7.1181 | 7.0896 | 8.2612 | 8.2439 | 8.2142 | 8.2517 | 8.2294 | 8.2481 | 10.3834 | 10.3725 | 10.3017 | 10.3317 | 10.3154 | 10.2828 | 13.2333 | 13.1721 | 13.1842 | 13.203 | 13.179 | 13.1487 | 12.587 | 12.5476 | 12.5978 | 12.5728 | 12.5392 | 12.5643 | 12.7657 | 12.739 | 12.7523 | 12.8056 | 12.8215 | 12.8464 | 12.8558 | 12.9023 | 12.8466 | 8.2062 | 8.1952 | 8.2012 | 8.2287 | 8.2361 | 8.2121
52 | Liquid line strainers gauge | ºC | 40.789 | 40.719 | 40.7676 | 40.6321 | 40.6283 | 40.5897 | 32.4491 | 32.6395 | 32.5018 | 32.3872 | 32.5982 | 32.631 | 32.5891 | 32.5277 | 32.4984 | 27.5418 | 27.4677 | 27.3787 | 27.3592 | 27.3614 | 27.3145 | 32.4863 | 32.5887 | 32.4118 | 32.2653 | 32.2109 | 32.2433 | 32.3558 | 32.2826 | 32.4373 | 40.8141 | 40.726 | 40.6623 | 40.6535 | 40.6049 | 40.6099 | 40.7058 | 49.0726 | 49.0339 | 49.0689 | 49.0811 | 49.0828 | 49.0244 | 49.0143 | 49.0093 | 50.2585 | 50.1437 | 50.0967 | 49.1341 | 48.9847 | 48.9231 | 48.4637 | 48.3287 | 48.1933 | 50.2185 | 50.3067 | 50.3112 | 40.7942 | 40.8889 | 40.9548 | 40.8564 | 40.8505 | 40.8263 | 32.4932 | 32.5822 | 32.5691 | 27.4762 | 27.5218 | 27.6313 | 27.8394 | 27.5372 | 40.6936 | 40.7067 | 40.7064 | 32.5419 | 32.5619 | 32.5409 | 32.6798 | 32.5477 | 32.5555 | 32.5089 | 32.4065 | 32.4197 | 32.4977 | 27.8029 | 27.8451 | 27.7607 | 27.6536 | 49.0094 | 49.2431 | 49.2917 | 49.2405 | 49.1001 | 49.0359 | 49.0237 | 48.4801 | 48.5034 | 48.4836 | 48.8381 | 48.9139 | 48.8034 | 48.8371 | 48.4079 | 48.5218 | 48.405 | 48.1943 | 49.8871 | 49.9764 | 50.0223 | 48.7716 | 48.6066 | 48.6588 | 48.0609 | 47.9696 | 48.0673 | 49.0568 | 48.8476 | 48.9712 | 32.6647 | 32.6881 | 32.3979 | 50.1966 | 50.1611 | 50.1138 | 48.3383 | 48.1879 | 48.1546 | 48.7288 | 48.7262 | 48.7742 | 48.8896 | 48.858 | 48.8338 | 32.5685 | 32.6447 | 32.4788 | 32.6069 | 32.4419 | 32.5873 | 32.5039 | 32.3607 | 32.4201 | 27.4095 | 27.4869 | 27.386 | 27.5396 | 27.4719 | 27.3948 | 40.7415 | 40.5855 | 40.5685 | 40.5752 | 40.6319 | 40.4631 | 50.2006 | 50.1499 | 50.1504 | 48.9451 | 48.9243 | 48.8004 | 48.3458 | 48.1715 | 48.2102 | 49.1807 | 49.0275 | 48.9421 | 32.2732 | 32.533 | 32.3188 | 48.2633 | 48.2788 | 48.2535 | 48.8246 | 48.9845 | 49.0883 | 32.3557 | 32.3183 | 32.3593 | 27.5574 | 27.5454 | 27.4453 | 27.3993 | 27.5253 | 27.5189 | 27.4281 | 27.2828 | 27.1461 | 32.4604 | 32.3862 | 32.2587 | 32.42 | 32.3241 | 32.4043 | 40.7912 | 40.7519 | 40.4954 | 40.6045 | 40.5452 | 40.4268 | 50.1635 | 49.9791 | 50.0154 | 50.0723 | 50 | 49.9082 | 48.1817 | 48.0585 | 48.2154 | 48.1374 | 48.0322 | 48.1107 | 48.7371 | 48.6545 | 48.6959 | 48.8603 | 48.9094 | 48.9861 | 49.0151 | 49.1578 | 48.9868 | 32.2242 | 32.1769 | 32.2027 | 32.3209 | 32.3527 | 32.2498
53 | Liquid line strainers enthalpy | KJ/kg | 241.4149 | 241.1965 | 241.4161 | 241.3272 | 241.0869 | 240.9296 | 230.0441 | 230.1147 | 229.7506 | 229.8217 | 229.969 | 229.9065 | 229.8762 | 229.6085 | 229.4742 | 223.6035 | 223.5015 | 223.3206 | 223.6749 | 223.6605 | 223.4529 | 226.6209 | 226.7945 | 226.6895 | 227.2551 | 227.3581 | 227.3857 | 227.3927 | 227.4592 | 227.4369 | 239.1991 | 239.0611 | 239.1081 | 238.5118 | 238.7433 | 238.5615 | 238.2141 | 249.2177 | 249.1697 | 249.1457 | 249.155 | 249.1749 | 248.9216 | 249.0088 | 249.0486 | 249.7222 | 249.5578 | 249.814 | 247.6206 | 247.4211 | 247.314 | 247.0025 | 246.7186 | 246.324 | 249.3913 | 249.5483 | 249.4568 | 237.0345 | 237.4241 | 237.1411 | 236.7643 | 236.7897 | 236.5651 | 226.9022 | 226.8449 | 226.6385 | 222.1625 | 222.2751 | 222.4301 | 222.7885 | 222.4181 | 238.6535 | 238.2246 | 238.4682 | 226.331 | 226.3684 | 226.3223 | 226.1809 | 225.9693 | 225.8333 | 225.6938 | 224.9109 | 224.8495 | 224.754 | 219.7213 | 219.7178 | 219.6928 | 219.7503 | 246.1609 | 246.4382 | 246.0882 | 246.4757 | 245.008 | 244.9062 | 245.4181 | 243.7046 | 244.8978 | 243.9074 | 250.3767 | 250.6121 | 250.218 | 250.1601 | 249.4161 | 249.7206 | 249.6559 | 249.1453 | 250.9573 | 251.3648 | 251.4531 | 249.8437 | 249.4015 | 249.5042 | 248.7926 | 248.8615 | 249.1874 | 251.4393 | 251.3331 | 250.9669 | 227.882 | 227.8368 | 227.4966 | 252.9348 | 252.6162 | 252.6628 | 249.1777 | 249.0317 | 248.9994 | 250.1508 | 249.9302 | 249.8425 | 251.5425 | 251.3126 | 251.242 | 227.9153 | 228.1453 | 227.9123 | 231.1645 | 230.8867 | 230.9008 | 230.9345 | 230.6951 | 230.8691 | 226.2112 | 226.209 | 226.1941 | 226.2937 | 226.4891 | 226.3378 | 243.0323 | 242.6224 | 242.6701 | 242.045 | 241.9795 | 241.8522 | 254.1063 | 253.6488 | 253.6649 | 251.6027 | 251.5973 | 251.3173 | 250.3237 | 250.0424 | 249.9983 | 253.992 | 253.6609 | 253.8844 | 229.806 | 229.9541 | 229.6515 | 251.9609 | 251.8628 | 251.8362 | 252.7867 | 253.4182 | 253.6949 | 235.9447 | 235.7811 | 235.8171 | 226.9432 | 226.9151 | 226.8745 | 226.8026 | 226.8937 | 226.8624 | 226.7273 | 226.4554 | 226.2137 | 231.8158 | 231.7129 | 231.4358 | 232.0269 | 231.8699 | 231.8059 | 245.2922 | 245.1881 | 244.8345 | 244.0133 | 243.9303 | 243.764 | 257.0427 | 256.6693 | 256.7777 | 256.8581 | 256.6439 | 256.6923 | 254.0017 | 253.5695 | 254.1558 | 253.6074 | 253.4935 | 253.6927 | 254.8822 | 254.7647 | 254.8448 | 254.6428 | 255.501 | 255.1862 | 255.7413 | 255.8915 | 255.5984 | 230.8605 | 230.6998 | 230.8312 | 231.1311 | 231.0265 | 230.8917
54 | Liquid line strainers specific volume | m3/kg | 0.00084027 | 0.00083985 | 0.00084028 | 0.00084012 | 0.00083965 | 0.00083934 | 0.00081974 | 0.00081985 | 0.00081921 | 0.00081935 | 0.00081959 | 0.00081948 | 0.00081943 | 0.00081895 | 0.00081871 | 0.00080878 | 0.00080861 | 0.00080831 | 0.00080892 | 0.0008089 | 0.00080854 | 0.00081364 | 0.00081394 | 0.00081377 | 0.00081478 | 0.00081496 | 0.00081501 | 0.00081501 | 0.00081514 | 0.00081508 | 0.00083595 | 0.00083569 | 0.00083579 | 0.00083464 | 0.00083509 | 0.00083474 | 0.00083407 | 0.00085488 | 0.00085478 | 0.00085473 | 0.00085475 | 0.00085479 | 0.00085427 | 0.00085445 | 0.00085454 | 0.00085573 | 0.00085541 | 0.00085595 | 0.00085155 | 0.00085117 | 0.00085096 | 0.00085039 | 0.00084983 | 0.00084905 | 0.00085505 | 0.00085536 | 0.00085517 | 0.00083181 | 0.00083253 | 0.00083199 | 0.00083129 | 0.00083134 | 0.00083091 | 0.00081413 | 0.00081402 | 0.00081366 | 0.00080632 | 0.0008065 | 0.00080676 | 0.00080736 | 0.00080675 | 0.00083491 | 0.00083409 | 0.00083455 | 0.00081312 | 0.00081319 | 0.00081311 | 0.00081285 | 0.00081249 | 0.00081225 | 0.00081201 | 0.00081066 | 0.00081055 | 0.00081038 | 0.00080216 | 0.00080215 | 0.00080212 | 0.00080222 | 0.00084859 | 0.00084911 | 0.00084839 | 0.00084919 | 0.00084624 | 0.00084605 | 0.00084708 | 0.00084373 | 0.00084611 | 0.00084413 | 0.00085735 | 0.00085784 | 0.00085703 | 0.0008569 | 0.00085541 | 0.00085603 | 0.00085591 | 0.00085487 | 0.0008584 | 0.00085925 | 0.00085943 | 0.00085624 | 0.00085534 | 0.00085555 | 0.00085416 | 0.00085432 | 0.00085498 | 0.00085957 | 0.00085938 | 0.00085858 | 0.00081585 | 0.00081577 | 0.00081519 | 0.00086258 | 0.0008619 | 0.00086201 | 0.00085492 | 0.00085464 | 0.00085458 | 0.0008569 | 0.00085643 | 0.00085624 | 0.00085982 | 0.00085934 | 0.00085919 | 0.00081592 | 0.00081632 | 0.00081592 | 0.00082176 | 0.00082127 | 0.00082128 | 0.00082135 | 0.00082093 | 0.00082124 | 0.00081334 | 0.00081333 | 0.00081331 | 0.00081347 | 0.00081382 | 0.00081356 | 0.00084348 | 0.00084269 | 0.00084278 | 0.00084154 | 0.00084141 | 0.00084118 | 0.00086513 | 0.00086414 | 0.00086417 | 0.00085994 | 0.00085993 | 0.00085936 | 0.00085733 | 0.00085676 | 0.00085666 | 0.00086507 | 0.00086437 | 0.00086487 | 0.00081933 | 0.00081957 | 0.00081905 | 0.00086083 | 0.00086062 | 0.00086056 | 0.00086251 | 0.00086385 | 0.00086443 | 0.00083066 | 0.00083036 | 0.00083042 | 0.00081462 | 0.00081457 | 0.0008145 | 0.00081438 | 0.00081453 | 0.00081448 | 0.00081425 | 0.00081378 | 0.00081336 | 0.00082296 | 0.00082278 | 0.00082229 | 0.00082336 | 0.00082308 | 0.00082295 | 0.00084804 | 0.00084783 | 0.00084714 | 0.00084547 | 0.00084531 | 0.00084499 | 0.00087165 | 0.00087084 | 0.00087108 | 0.00087125 | 0.00087078 | 0.00087091 | 0.00086527 | 0.00086435 | 0.0008656 | 0.00086441 | 0.00086418 | 0.00086461 | 0.0008671 | 0.00086686 | 0.00086703 | 0.00086655 | 0.00086844 | 0.00086773 | 0.00086896 | 0.00086926 | 0.00086864 | 0.00082124 | 0.00082096 | 0.00082119 | 0.00082173 | 0.00082153 | 0.0008213
55 | Liquid line strainers sub cooling | ºC | 10.9972 | 11.0787 | 10.9748 | 10.9012 | 11.064 | 11.1347 | 10.6318 | 10.7723 | 10.8929 | 10.7276 | 10.8343 | 10.9116 | 10.891 | 11.0197 | 11.0857 | 10.3143 | 10.3133 | 10.3541 | 10.0801 | 10.0927 | 10.1948 | 13.106 | 13.0846 | 12.9825 | 12.432 | 12.304 | 12.3168 | 12.4245 | 12.3037 | 12.4745 | 12.5629 | 12.5711 | 12.4746 | 12.8818 | 12.6716 | 12.8035 | 13.142 | 13.9023 | 13.8964 | 13.9478 | 13.9537 | 13.9418 | 14.0564 | 13.9867 | 13.9546 | 14.7416 | 14.7392 | 14.5175 | 15.0559 | 15.0435 | 15.0555 | 14.8104 | 14.8704 | 15.0062 | 14.9275 | 14.9084 | 14.9753 | 14.0556 | 13.8775 | 14.1415 | 14.3071 | 14.2834 | 14.4166 | 12.912 | 13.0421 | 13.1763 | 11.2845 | 11.2491 | 11.2473 | 11.198 | 11.1618 | 12.823 | 13.1355 | 12.9651 | 13.3688 | 13.3621 | 13.3741 | 13.6143 | 13.6333 | 13.7384 | 13.7915 | 14.2495 | 14.3068 | 14.4534 | 13.3732 | 13.4181 | 13.3515 | 13.2027 | 15.9334 | 15.9762 | 16.2653 | 15.9478 | 16.8179 | 16.8239 | 16.4589 | 17.0984 | 16.2978 | 16.9616 | 12.8785 | 12.7939 | 12.9518 | 13.0249 | 13.1036 | 13.0097 | 12.9372 | 13.0752 | 13.5301 | 13.3424 | 13.3283 | 13.175 | 13.3118 | 13.2939 | 13.1828 | 13.0447 | 12.9197 | 12.3745 | 12.2379 | 12.6099 | 12.385 | 12.4406 | 12.3925 | 12.498 | 12.6781 | 12.5995 | 13.1968 | 13.1464 | 13.1351 | 12.9231 | 13.0708 | 13.1785 | 12.1376 | 12.2622 | 12.286 | 12.265 | 12.1774 | 12.1772 | 9.9957 | 10.0273 | 10.1628 | 10.0555 | 10.0818 | 10.0179 | 8.3144 | 8.3935 | 8.3031 | 8.3857 | 8.1784 | 8.2092 | 9.83 | 9.9574 | 9.9074 | 10.3467 | 10.4487 | 10.3682 | 11.7108 | 11.9689 | 11.9586 | 12.1522 | 12.1351 | 12.2016 | 12.4234 | 12.4409 | 12.5095 | 10.7712 | 10.8418 | 10.606 | 10.6247 | 10.7796 | 10.7799 | 11.2294 | 11.3113 | 11.3041 | 11.2301 | 10.9628 | 10.8795 | 6.3774 | 6.4546 | 6.4704 | 7.94 | 7.948 | 7.8768 | 7.8819 | 7.9432 | 7.9591 | 7.9645 | 8.0132 | 8.0488 | 9.3884 | 9.3869 | 9.4552 | 9.1987 | 9.2137 | 9.3393 | 8.3221 | 8.3545 | 8.3414 | 9.0159 | 9.0139 | 9.0103 | 9.7017 | 9.768 | 9.7316 | 9.7344 | 9.8058 | 9.682 | 9.7689 | 9.9375 | 9.6987 | 9.9906 | 9.9626 | 9.9065 | 9.7297 | 9.7264 | 9.7138 | 10.0135 | 9.4856 | 9.7735 | 9.4296 | 9.4711 | 9.4974 | 9.8279 | 9.8944 | 9.8271 | 9.7331 | 9.8389 | 9.8314
56 | Sub cooling loss cond - strainers | ºC
57 | Liquid line loss PD | BarA | 0.088283 | 0.097509 | 0.097454 | 0.083853 | 0.10097 | 0.10152 | 0.035904 | 0.015258 | 0.028243 | 0.020639 | 0.016135 | 0.01067 | 0.014 | 0.026853 | 0.010852 | 0.00951 | 0.018822 | 0.005326 | 0.004168 | 0.028504 | 0.019279 | 0.022679 | 0.035257 | 0.041571 | 0.043523 | 0.042508 | 0.054926 | 0.040647 | 0.061808 | 0.032564 | 0.088407 | 0.10502 | 0.11156 | 0.089335 | 0.12389 | 0.10864 | 0.10077 | 0.1241 | 0.12725 | 0.12979 | 0.11707 | 0.11752 | 0.11784 | 0.1313 | 0.13823 | 0.1157 | 0.13627 | 0.13824 | 0.11226 | 0.12502 | 0.12793 | 0.13061 | 0.11928 | 0.14111 | 0.14367 | 0.13394 | 0.11993 | 0.10575 | 0.072277 | 0.084188 | 0.070531 | 0.094002 | 0.077969 | 0.028252 | 0.037386 | 0.025403 | 0.00156 | 0.017408 | 0.014081 | -0.006809 | 0.001169 | 0.11247 | 0.08746 | 0.11308 | 0.016776 | 0.026005 | 0.022977 | 0.01632 | 0.034122 | 0.02124 | 0.037033 | 0.02552 | 0.032156 | 0.018244 | 0.01102 | 0.019007 | 0.007138 | 0.015319 | 0.13679 | 0.11251 | 0.10975 | 0.10307 | 0.12968 | 0.12271 | 0.12586 | 0.13434 | 0.13712 | 0.12523 | 0.15861 | 0.14679 | 0.14484 | 0.16185 | 0.16747 | 0.15054 | 0.15839 | 0.14829 | 0.13663 | 0.14457 | 0.12734 | 0.1661 | 0.16065 | 0.17013 | 0.16121 | 0.14459 | 0.12731 | 0.1379 | 0.13655 | 0.12126 | 0.004718 | 0.005609 | 0.015493 | 0.14437 | 0.15078 | 0.1411 | 0.1414 | 0.15017 | 0.15471 | 0.1519 | 0.15746 | 0.13713 | 0.13882 | 0.13206 | 0.12606 | 0.02848 | 0.011346 | 0.006601 | 0.033436 | 0.028258 | 0.018741 | 0.02168 | 0.033835 | 0.023329 | 0.024049 | -0.013576 | 0.017576 | 0.017645 | 0.01299 | 0.012205 | 0.11396 | 0.10106 | 0.10747 | 0.11442 | 0.098026 | 0.11402 | 0.15719 | 0.1297 | 0.15364 | 0.13975 | 0.15295 | 0.14197 | 0.14397 | 0.13931 | 0.14017 | 0.14238 | 0.13186 | 0.13866 | 0.037021 | 0.037358 | 0.031128 | 0.14249 | 0.14229 | 0.1399 | 0.15943 | 0.15596 | 0.13434 | 0.045724 | 0.029279 | 0.022371 | 0.01118 | 0.002861 | 0.012204 | -0.00469 | 0.005131 | 0.010698 | 0.020169 | 0.017939 | 0.010042 | 0.028049 | 0.036101 | 0.035971 | 0.058438 | 0.037266 | 0.016641 | 0.11107 | 0.10858 | 0.11574 | 0.09948 | 0.096926 | 0.11878 | 0.14641 | 0.14681 | 0.14895 | 0.143 | 0.15969 | 0.15638 | 0.15807 | 0.146 | 0.15728 | 0.15089 | 0.14795 | 0.14053 | 0.14058 | 0.14879 | 0.14334 | 0.16164 | 0.16239 | 0.13609 | 0.13213 | 0.12399 | 0.12803 | 0.03958 | 0.036588 | 0.04238 | 0.042494 | 0.026084 | 0.029732
58 | Liquid line solenoid valve open (circuit 1)
59 | Liquid line solenoid valve open (circuit 2)
60
61 | Note for temp / pressure between exp and flowmeter refer to ICAD / EKC
62
63 | Suction flow meter (High) Temp | ºC | 15.2297 | 15.3698 | 15.5567 | 17.6118 | 17.6091 | 17.5038 | 20.4014 | 20.3128 | 20.1394 | 19.1442 | 19.0634 | 18.8666 | 18.6152 | 18.4872 | 18.5596 | 17.037 | 16.9921 | 16.7394 | 19.1675 | 18.549 | 18.3818 | 17.5931 | 16.9054 | 16.7132 | 16.0549 | 16.0284 | 16.0511 | 16.2887 | 16.1463 | 16.0964 | 17.3012 | 17.1679 | 17.0034 | 16.7474 | 16.5928 | 16.3034 | 16.988 | 14.6452 | 14.6343 | 14.6348 | 14.6544 | 14.7171 | 14.7525 | 14.8143 | 15.3291 | 12.3966 | 12.7973 | 12.2684 | 14.9808 | 14.9493 | 14.7773 | 15.7954 | 15.5731 | 15.2555 | 11.3692 | 11.4864 | 11.5449 | 17.1477 | 16.8812 | 16.8236 | 17.2557 | 17.2695 | 17.263 | 17.9453 | 18.2663 | 18.7981 | 18.3316 | 18.467 | 18.6333 | 18.0898 | 17.93 | 15.3888 | 15.2316 | 14.376 | 16.9786 | 16.8976 | 16.7832 | 16.4797 | 16.7158 | 16.7295 | 16.7941 | 16.6939 | 16.6729 | 16.7389 | 17.1019 | 18.4491 | 18.8525 | 18.7704 | 13.8548 | 14.3446 | 14.6265 | 14.9816 | 13.5804 | 14.8653 | 15.1748 | 19.2237 | 20.0499 | 19.3508 | 15.5393 | 15.5293 | 15.1965 | 14.9407 | 15.1549 | 15.2405 | 15.1364 | 14.6628 | 12.468 | 12.9078 | 13.2549 | 14.0641 | 14.1239 | 14.8673 | 16.0009 | 16.1561 | 16.361 | 13.0496 | 14.5876 | 13.6658 | 17.8229 | 17.3381 | 17.6227 | 12.0038 | 11.7832 | 11.4284 | 14.2679 | 13.9934 | 13.5985 | 15.6402 | 14.9683 | 15.186 | 13.7282 | 13.9645 | 14.0237 | 16.7333 | 16.8359 | 16.6708 | 18.177 | 18.2612 | 19.2329 | 19.4394 | 19.0394 | 18.4852 | 17.5775 | 17.7874 | 18.1119 | 18.222 | 17.8873 | 17.7857 | 15.5527 | 15.514 | 15.4571 | 16.5659 | 16.4167 | 16.2779 | 13.2602 | 12.073 | 10.0483 | 13.7469 | 13.6043 | 13.481 | 13.5088 | 13.6009 | 13.1505 | 14.7542 | 16.5898 | 15.9957 | 18.983 | 18.7162 | 18.4693 | 15.8354 | 15.7533 | 15.8323 | 16.0615 | 16.3192 | 15.4266 | 17.228 | 17.3372 | 17.3043 | 17.9562 | 17.6273 | 17.447 | 17.2767 | 17.3291 | 17.5956 | 17.6495 | 17.6124 | 17.8886 | 17.406 | 17.3156 | 17.5391 | 16.6276 | 16.9192 | 16.9259 | 16.3122 | 16.1987 | 16.0969 | 16.9385 | 16.7031 | 16.5126 | 12.2178 | 12.2589 | 12.139 | 11.9474 | 11.752 | 11.4318 | 14.6232 | 14.166 | 14.7633 | 14.3266 | 14.3295 | 14.4626 | 14.6045 | 14.5004 | 14.1354 | 14.2462 | 14.51 | 14.3244 | 14.8263 | 14.7981 | 14.5194 | 17.5783 | 17.7379 | 17.7548 | 17.6878 | 17.7246 | 18.0654
64 | Suction flow meter (High) Pressure | BarA | 3.7034 | 3.6923 | 3.6945 | 3.7203 | 3.714 | 3.7085 | 3.838 | 3.8489 | 3.8445 | 3.8266 | 3.8474 | 3.8475 | 3.8504 | 3.8402 | 3.8378 | 3.8766 | 3.8707 | 3.8579 | 3.8729 | 3.8773 | 3.8707 | 3.8401 | 3.8472 | 3.8453 | 3.8317 | 3.8354 | 3.8423 | 3.8442 | 3.84 | 3.8494 | 3.7088 | 3.6999 | 3.6933 | 3.7075 | 3.7073 | 3.705 | 3.7095 | 3.6166 | 3.6173 | 3.6182 | 3.6183 | 3.6219 | 3.6229 | 3.6276 | 3.626 | 3.3766 | 3.3696 | 3.3647 | 3.6655 | 3.6717 | 3.6681 | 3.6711 | 3.6699 | 3.6726 | 3.3914 | 3.3951 | 3.3922 | 3.7038 | 3.7028 | 3.6968 | 3.706 | 3.7068 | 3.7008 | 3.8443 | 3.8449 | 3.846 | 3.8561 | 3.8584 | 3.8732 | 3.8782 | 3.8653 | 3.7247 | 3.7226 | 3.7296 | 3.8468 | 3.8505 | 3.847 | 3.8552 | 3.8521 | 3.8563 | 3.8524 | 3.6494 | 3.6417 | 3.6543 | 3.8501 | 3.8812 | 3.8781 | 3.8795 | 3.6076 | 3.6189 | 3.6282 | 3.6153 | 3.6727 | 3.6845 | 3.6905 | 3.6679 | 3.6665 | 3.6912 | 3.6817 | 3.6906 | 3.6771 | 3.6759 | 3.6839 | 3.6895 | 3.6808 | 3.686 | 3.4138 | 3.416 | 3.4132 | 3.7119 | 3.6981 | 3.705 | 3.7002 | 3.6967 | 3.6994 | 3.6569 | 3.6451 | 3.6564 | 3.8468 | 3.8471 | 3.833 | 3.4136 | 3.4147 | 3.4154 | 3.7124 | 3.7009 | 3.6995 | 3.6977 | 3.7083 | 3.7157 | 3.6591 | 3.6511 | 3.6491 | 3.8374 | 3.8464 | 3.8401 | 3.8424 | 3.8403 | 3.8358 | 3.8416 | 3.8331 | 3.8347 | 3.8566 | 3.8593 | 3.8737 | 3.8539 | 3.8544 | 3.8526 | 3.6984 | 3.7057 | 3.704 | 3.7281 | 3.7293 | 3.728 | 3.3997 | 3.3977 | 3.395 | 3.6944 | 3.6901 | 3.6801 | 3.6926 | 3.6883 | 3.6831 | 3.6604 | 3.6516 | 3.6532 | 3.8359 | 3.8301 | 3.8405 | 3.6934 | 3.6947 | 3.687 | 3.693 | 3.7021 | 3.6962 | 3.8478 | 3.8382 | 3.8389 | 3.8417 | 3.8401 | 3.8399 | 3.8637 | 3.7947 | 3.7922 | 3.8103 | 3.8065 | 3.7971 | 3.8437 | 3.8405 | 3.8274 | 3.8249 | 3.8148 | 3.817 | 3.7051 | 3.7058 | 3.7009 | 3.7274 | 3.7179 | 3.7156 | 3.3919 | 3.3992 | 3.4037 | 3.4088 | 3.4047 | 3.3939 | 3.6978 | 3.694 | 3.6965 | 3.6924 | 3.6853 | 3.6995 | 3.6906 | 3.6826 | 3.686 | 3.6824 | 3.6849 | 3.6841 | 3.6469 | 3.6277 | 3.6387 | 3.8471 | 3.8369 | 3.8421 | 3.8539 | 3.8477 | 3.849
65 | Suction flow meter (High) gauge | ºC | 6.6636 | 6.5762 | 6.5942 | 6.7968 | 6.7472 | 6.704 | 7.7088 | 7.7926 | 7.7593 | 7.6219 | 7.7814 | 7.7816 | 7.8039 | 7.7263 | 7.7079 | 8.0041 | 7.9587 | 7.8612 | 7.9759 | 8.0093 | 7.9587 | 7.7253 | 7.7793 | 7.7649 | 7.6607 | 7.6889 | 7.7421 | 7.7566 | 7.7242 | 7.7963 | 6.7069 | 6.6365 | 6.5843 | 6.6961 | 6.695 | 6.6765 | 6.7118 | 5.9749 | 5.9801 | 5.9872 | 5.9885 | 6.0172 | 6.0248 | 6.0628 | 6.0495 | 3.9998 | 3.9406 | 3.8991 | 6.3647 | 6.4135 | 6.3853 | 6.4089 | 6.3994 | 6.4211 | 4.1247 | 4.1555 | 4.1317 | 6.667 | 6.659 | 6.6121 | 6.6848 | 6.6907 | 6.6434 | 7.7574 | 7.7621 | 7.7702 | 7.8475 | 7.8654 | 7.9779 | 8.016 | 7.9178 | 6.8313 | 6.8149 | 6.8697 | 7.7766 | 7.8049 | 7.7779 | 7.841 | 7.8167 | 7.8494 | 7.8194 | 6.2362 | 6.1754 | 6.2753 | 7.8018 | 8.0389 | 8.0153 | 8.0256 | 5.9023 | 5.9932 | 6.0674 | 5.9644 | 6.4217 | 6.5147 | 6.5627 | 6.3833 | 6.3724 | 6.5675 | 6.4931 | 6.5634 | 6.4562 | 6.4467 | 6.5106 | 6.5547 | 6.4858 | 6.5269 | 4.3131 | 4.3313 | 4.3074 | 6.7307 | 6.6221 | 6.6766 | 6.6388 | 6.6114 | 6.6326 | 6.2966 | 6.2021 | 6.2919 | 7.7766 | 7.7789 | 7.6709 | 4.3114 | 4.3199 | 4.3263 | 6.7351 | 6.6444 | 6.6333 | 6.6192 | 6.7026 | 6.7604 | 6.3137 | 6.2503 | 6.2342 | 7.7049 | 7.7738 | 7.7254 | 7.7431 | 7.7265 | 7.6923 | 7.7364 | 7.6713 | 7.6836 | 7.8512 | 7.8719 | 7.9818 | 7.8309 | 7.835 | 7.821 | 6.6249 | 6.6822 | 6.6689 | 6.8582 | 6.8673 | 6.8572 | 4.1944 | 4.178 | 4.1547 | 6.5929 | 6.5595 | 6.48 | 6.5789 | 6.5447 | 6.5038 | 6.3239 | 6.254 | 6.2665 | 7.6932 | 7.649 | 7.7286 | 6.5856 | 6.5953 | 6.5344 | 6.5821 | 6.6538 | 6.6074 | 7.7843 | 7.7107 | 7.7159 | 7.7379 | 7.7256 | 7.724 | 7.9055 | 7.3759 | 7.357 | 7.4963 | 7.467 | 7.3946 | 7.7529 | 7.7284 | 7.6279 | 7.6083 | 7.5307 | 7.5476 | 6.6775 | 6.6825 | 6.6444 | 6.8529 | 6.778 | 6.7599 | 4.129 | 4.1905 | 4.2277 | 4.2711 | 4.2363 | 4.1458 | 6.6199 | 6.5897 | 6.61 | 6.5776 | 6.5211 | 6.6335 | 6.5629 | 6.5002 | 6.5268 | 6.4984 | 6.5183 | 6.5121 | 6.2168 | 6.0633 | 6.1509 | 7.7792 | 7.7006 | 7.7404 | 7.8304 | 7.7831 | 7.7933
66 | Suction flow meter (low) SH | ºC | 8.5661 | 8.7936 | 8.9626 | 10.815 | 10.8619 | 10.7999 | 12.6926 | 12.5202 | 12.3801 | 11.5223 | 11.282 | 11.085 | 10.8112 | 10.7609 | 10.8517 | 9.0329 | 9.0334 | 8.8782 | 11.1915 | 10.5397 | 10.4231 | 9.8678 | 9.1261 | 8.9483 | 8.3943 | 8.3396 | 8.309 | 8.5321 | 8.4221 | 8.3002 | 10.5943 | 10.5315 | 10.4191 | 10.0513 | 9.8978 | 9.6269 | 10.2762 | 8.6703 | 8.6542 | 8.6475 | 8.6659 | 8.6999 | 8.7277 | 8.7515 | 9.2796 | 8.3967 | 8.8567 | 8.3693 | 8.6161 | 8.5358 | 8.392 | 9.3865 | 9.1737 | 8.8344 | 7.2446 | 7.3309 | 7.4132 | 10.4807 | 10.2223 | 10.2115 | 10.5709 | 10.5788 | 10.6197 | 10.188 | 10.5042 | 11.028 | 10.4841 | 10.6016 | 10.6553 | 10.0738 | 10.0122 | 8.5575 | 8.4166 | 7.5063 | 9.2021 | 9.0927 | 9.0053 | 8.6387 | 8.8991 | 8.8801 | 8.9747 | 10.4577 | 10.4975 | 10.4636 | 9.3001 | 10.4102 | 10.8372 | 10.7448 | 7.9525 | 8.3514 | 8.5591 | 9.0172 | 7.1587 | 8.3505 | 8.6121 | 12.8404 | 13.6775 | 12.7833 | 9.0462 | 8.9659 | 8.7403 | 8.494 | 8.6443 | 8.6858 | 8.6506 | 8.1359 | 8.1549 | 8.5765 | 8.9475 | 7.3334 | 7.5018 | 8.1907 | 9.3621 | 9.5447 | 9.7284 | 6.753 | 8.3855 | 7.3739 | 10.0463 | 9.5592 | 9.9518 | 7.6925 | 7.4632 | 7.1021 | 7.5329 | 7.349 | 6.9652 | 9.021 | 8.2657 | 8.4255 | 7.4146 | 7.7142 | 7.7896 | 9.0284 | 9.0621 | 8.9454 | 10.4339 | 10.5347 | 11.5406 | 11.703 | 11.3681 | 10.8017 | 9.7264 | 9.9155 | 10.1301 | 10.3911 | 10.0523 | 9.9647 | 8.9278 | 8.8318 | 8.7882 | 9.7077 | 9.5494 | 9.4206 | 9.0658 | 7.895 | 5.8936 | 7.154 | 7.0448 | 7.001 | 6.93 | 7.0563 | 6.6468 | 8.4303 | 10.3358 | 9.7291 | 11.2898 | 11.0672 | 10.7407 | 9.2498 | 9.158 | 9.2979 | 9.4794 | 9.6654 | 8.8192 | 9.4437 | 9.6265 | 9.5883 | 10.2183 | 9.9017 | 9.7231 | 9.3712 | 9.9531 | 10.2386 | 10.1532 | 10.1455 | 10.494 | 9.653 | 9.5872 | 9.9112 | 9.0193 | 9.3885 | 9.3783 | 9.6347 | 9.5162 | 9.4524 | 10.0856 | 9.9251 | 9.7527 | 8.0888 | 8.0684 | 7.9113 | 7.6763 | 7.5157 | 7.2859 | 8.0032 | 7.5763 | 8.1534 | 7.7489 | 7.8083 | 7.8292 | 8.0416 | 8.0003 | 7.6086 | 7.7478 | 7.9917 | 7.8123 | 8.6095 | 8.7348 | 8.3685 | 9.7991 | 10.0373 | 10.0144 | 9.8574 | 9.9415 | 10.2722
67 | suction flow meter (high) Low SH warning |  | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok
68 | Suction flow meter (High) enthalpy | KJ/kg | 410.3268 | 410.4818 | 410.6473 | 412.4651 | 412.4774 | 412.3941 | 414.7479 | 414.6418 | 414.4926 | 413.6209 | 413.4986 | 413.3179 | 413.0802 | 412.9864 | 413.0584 | 411.5673 | 411.5403 | 411.3384 | 413.5351 | 412.9565 | 412.8184 | 412.1657 | 411.5168 | 411.3446 | 410.7722 | 410.7389 | 410.7428 | 410.9569 | 410.8361 | 410.7674 | 412.208 | 412.1073 | 411.9726 | 411.705 | 411.564 | 411.305 | 411.9202 | 410.0037 | 409.9922 | 409.9905 | 410.008 | 410.0565 | 410.0864 | 410.1313 | 410.6049 | 408.5511 | 408.9306 | 408.4647 | 410.1912 | 410.1474 | 409.9988 | 410.9219 | 410.7217 | 410.4249 | 407.5845 | 407.6813 | 407.7415 | 412.0797 | 411.8385 | 411.8 | 412.173 | 412.1839 | 412.1921 | 412.4793 | 412.7726 | 413.2585 | 412.8064 | 412.9253 | 413.0436 | 412.5322 | 412.4157 | 410.4205 | 410.2816 | 409.4803 | 411.585 | 411.5016 | 411.4049 | 411.1059 | 411.3308 | 411.333 | 411.4019 | 411.7939 | 411.7928 | 411.8234 | 411.6905 | 412.8555 | 413.2337 | 413.155 | 409.3048 | 409.7239 | 409.9585 | 410.3137 | 408.8926 | 410.0393 | 410.3076 | 414.0577 | 414.8139 | 414.1205 | 410.6623 | 410.6317 | 410.3602 | 410.1293 | 410.3055 | 410.3702 | 410.2961 | 409.8503 | 408.5234 | 408.9163 | 409.2376 | 409.2383 | 409.3273 | 409.991 | 411.0398 | 411.1901 | 411.371 | 408.4461 | 409.8818 | 409.0114 | 412.3609 | 411.9147 | 412.2096 | 408.1035 | 407.901 | 407.5775 | 409.4237 | 409.2007 | 408.8423 | 410.7159 | 410.0754 | 410.2567 | 409.0617 | 409.2975 | 409.3567 | 411.3819 | 411.4547 | 411.318 | 412.6964 | 412.7789 | 413.6811 | 413.8572 | 413.5098 | 412.9976 | 412.1123 | 412.2988 | 412.5631 | 412.7108 | 412.402 | 412.313 | 410.6342 | 410.5812 | 410.5332 | 411.4899 | 411.3506 | 411.2265 | 409.2754 | 408.2058 | 406.3782 | 408.9911 | 408.871 | 408.7832 | 408.7774 | 408.8726 | 408.4729 | 409.9965 | 411.6936 | 411.1478 | 413.4515 | 413.22 | 412.9693 | 410.9047 | 410.8267 | 410.9175 | 411.1125 | 411.3263 | 410.5242 | 411.8118 | 411.9351 | 411.9032 | 412.4953 | 412.197 | 412.0318 | 411.8188 | 412.0308 | 412.281 | 412.2879 | 412.2629 | 412.5383 | 411.9851 | 411.9097 | 412.1461 | 411.315 | 411.607 | 411.608 | 411.3127 | 411.2074 | 411.1259 | 411.8324 | 411.6398 | 411.471 | 408.3514 | 408.3704 | 408.2508 | 408.0644 | 407.8977 | 407.6348 | 409.7851 | 409.376 | 409.9165 | 409.5268 | 409.5471 | 409.6339 | 409.7858 | 409.71 | 409.3677 | 409.478 | 409.7132 | 409.5453 | 410.0952 | 410.1164 | 409.8352 | 412.1354 | 412.3063 | 412.3095 | 412.2201 | 412.2686 | 412.5786
69 | Suction flow meter (High) specific Vol | m3/kg | 0.057697 | 0.057929 | 0.057943 | 0.058077 | 0.058185 | 0.058251 | 0.056867 | 0.056664 | 0.056688 | 0.056711 | 0.056349 | 0.056295 | 0.056179 | 0.056309 | 0.056368 | 0.055328 | 0.05541 | 0.055546 | 0.055966 | 0.055728 | 0.055789 | 0.056066 | 0.055763 | 0.055741 | 0.055779 | 0.055713 | 0.055606 | 0.055641 | 0.055671 | 0.055505 | 0.058188 | 0.058306 | 0.058375 | 0.058056 | 0.058014 | 0.057973 | 0.058089 | 0.059063 | 0.059048 | 0.059032 | 0.059035 | 0.058989 | 0.058982 | 0.058914 | 0.059092 | 0.063024 | 0.063292 | 0.06323 | 0.058287 | 0.058169 | 0.058182 | 0.058421 | 0.058379 | 0.05824 | 0.062405 | 0.062367 | 0.062442 | 0.058232 | 0.058175 | 0.058262 | 0.058224 | 0.058215 | 0.058317 | 0.056095 | 0.056173 | 0.056301 | 0.05601 | 0.056009 | 0.055817 | 0.055589 | 0.055752 | 0.057375 | 0.057366 | 0.057004 | 0.055789 | 0.055707 | 0.055733 | 0.055517 | 0.055633 | 0.055568 | 0.055648 | 0.059064 | 0.059195 | 0.058989 | 0.05577 | 0.055639 | 0.055798 | 0.055754 | 0.058997 | 0.058935 | 0.058849 | 0.059184 | 0.057758 | 0.057921 | 0.057904 | 0.05945 | 0.059706 | 0.059072 | 0.058161 | 0.058003 | 0.058145 | 0.058093 | 0.058013 | 0.05794 | 0.058063 | 0.057836 | 0.062288 | 0.062378 | 0.062541 | 0.057218 | 0.057473 | 0.057565 | 0.057971 | 0.058075 | 0.058086 | 0.057881 | 0.058536 | 0.05807 | 0.056021 | 0.055883 | 0.05619 | 0.06215 | 0.062062 | 0.061938 | 0.057267 | 0.057386 | 0.057298 | 0.057911 | 0.057537 | 0.057472 | 0.058039 | 0.058249 | 0.058302 | 0.055873 | 0.055756 | 0.055813 | 0.056189 | 0.056247 | 0.056585 | 0.056547 | 0.056577 | 0.056399 | 0.055796 | 0.05581 | 0.055667 | 0.056015 | 0.055915 | 0.055917 | 0.057874 | 0.057737 | 0.05775 | 0.057648 | 0.057586 | 0.057569 | 0.062816 | 0.062493 | 0.061925 | 0.057429 | 0.057461 | 0.0576 | 0.057391 | 0.057493 | 0.057453 | 0.058312 | 0.058994 | 0.058796 | 0.056515 | 0.056536 | 0.056299 | 0.058041 | 0.057996 | 0.058153 | 0.058113 | 0.058028 | 0.057877 | 0.055841 | 0.056027 | 0.056007 | 0.056139 | 0.056075 | 0.056029 | 0.0556 | 0.056739 | 0.056853 | 0.056569 | 0.056622 | 0.056853 | 0.055957 | 0.055984 | 0.056258 | 0.056049 | 0.056294 | 0.05626 | 0.057974 | 0.05793 | 0.057985 | 0.057765 | 0.057863 | 0.057849 | 0.062655 | 0.062519 | 0.062393 | 0.06223 | 0.062254 | 0.062373 | 0.05762 | 0.057556 | 0.057682 | 0.057628 | 0.057754 | 0.057545 | 0.05774 | 0.057849 | 0.057686 | 0.05778 | 0.057812 | 0.057772 | 0.058572 | 0.058908 | 0.058631 | 0.055948 | 0.056159 | 0.056079 | 0.05587 | 0.05598 | 0.056052
70 | Suction flow meter (High) vol Flow | m^3/hr | 708.5533 | 708.239 | 708.9824 | 753.3499 | 754.6669 | 753.9793 | 459.6092 | 459.1117 | 458.4765 | 402.5823 | 402.5339 | 405.1102 | 404.9291 | 403.8661 | 404.6599 | 179.8175 | 180.006 | 180.6444 | 192.8903 | 193.2239 | 196.0088 | 402.7638 | 402.2725 | 402.9232 | 432.2026 | 432.5648 | 432.9053 | 431.5543 | 433.2524 | 432.0915 | 717.0727 | 716.8703 | 717.2743 | 752.582 | 752.1472 | 750.0536 | 744.4851 | 1058.93 | 1061.3358 | 1060.2397 | 1059.7164 | 1057.6105 | 1057.1208 | 1059.3345 | 1060.6859 | 1120.7046 | 1122.7851 | 1125.4913 | 1126.2432 | 1125.8052 | 1122.9724 | 1128.7409 | 1127.6508 | 1125.5224 | 1094.5429 | 1094.4888 | 1094.2393 | 682.6334 | 679.5682 | 680.3845 | 695.7665 | 697.6081 | 696.4332 | 389.4074 | 389.6914 | 388.8562 | 163.5925 | 166.9995 | 155.5166 | 179.5908 | 180.9583 | 735.1244 | 734.6323 | 734.4339 | 421.724 | 421.0643 | 422.7079 | 422.476 | 444.7665 | 446.4117 | 445.5893 | 444.5517 | 445.6618 | 445.5565 | 175.3381 | 180.2559 | 176.42 | 182.0249 | 1032.9634 | 1033.6461 | 1034.0407 | 1036.3232 | 1100.9827 | 1103.1869 | 1101.1818 | 1107.5314 | 1112.7848 | 1109.5549 | 1106.4373 | 1107.5957 | 1107.953 | 1106.9884 | 1107.5945 | 1107.8572 | 1108.7734 | 1107.5527 | 1138.231 | 1138.4527 | 1142.0461 | 1141.9203 | 1141.2077 | 1141.1278 | 1145.9468 | 1145.4018 | 1146.4713 | 1066.1123 | 1071.2948 | 1069.3823 | 457.3374 | 457.0021 | 458.2307 | 1135.4609 | 1134.0225 | 1134.7348 | 1144.781 | 1140.8975 | 1140.9929 | 1147.2442 | 1141.9289 | 1147.5331 | 1068.0927 | 1069.1057 | 1069.6966 | 458.1127 | 459.1281 | 460.5906 | 432.0657 | 432.1927 | 432.6537 | 402.8876 | 402.368 | 402.4024 | 165.5452 | 166.7393 | 175.6701 | 189.3809 | 185.1499 | 186.6649 | 721.4893 | 722.4118 | 722.2458 | 763.2945 | 764.0845 | 765.0877 | 1133.5116 | 1132.8965 | 1126.0625 | 1134.0115 | 1136.7857 | 1137.393 | 1134.7679 | 1137.4385 | 1134.6126 | 1063.7015 | 1072.4233 | 1068.1636 | 455.8056 | 454.8754 | 455.8404 | 1141.5298 | 1139.8152 | 1139.1977 | 1141.3384 | 1142.9751 | 1143.4111 | 456.1142 | 453.9677 | 458.4884 | 186.2945 | 187.6422 | 189.594 | 174.9865 | 174.8234 | 175.5865 | 186.106 | 188.1258 | 189.2072 | 431.7579 | 431.3527 | 431.2683 | 400.6899 | 400.7723 | 400.0052 | 715.6684 | 710.2543 | 701.2182 | 765.1471 | 764.9557 | 764.682 | 1131.1487 | 1130.6586 | 1131.5999 | 1131.7888 | 1131.9556 | 1130.0768 | 1134.7434 | 1136.2509 | 1136.3222 | 1135.5056 | 1134.2828 | 1134.8401 | 1137.0787 | 1136.5509 | 1135.5334 | 1136.037 | 1137.9212 | 1135.7186 | 1063.9666 | 1063.7318 | 1064.1486 | 456.6768 | 458.1315 | 459.0695 | 456.3715 | 458.1036 | 457.2845
71 | Suction flow meter (High) mass Flow | kg/s | 3.4113 | 3.3961 | 3.3989 | 3.6032 | 3.6028 | 3.5954 | 2.245 | 2.2506 | 2.2466 | 1.9719 | 1.9843 | 1.9989 | 2.0022 | 1.9923 | 1.9941 | 0.90279 | 0.90239 | 0.90339 | 0.95738 | 0.96313 | 0.97594 | 1.9955 | 2.0039 | 2.0079 | 2.1523 | 2.1567 | 2.1625 | 2.1544 | 2.1618 | 2.1624 | 3.4232 | 3.4153 | 3.4132 | 3.6009 | 3.6014 | 3.5939 | 3.5601 | 4.9802 | 4.9928 | 4.989 | 4.9863 | 4.9803 | 4.9786 | 4.9947 | 4.986 | 4.9395 | 4.9277 | 4.9444 | 5.3674 | 5.3761 | 5.3614 | 5.3669 | 5.3656 | 5.3682 | 4.872 | 4.8748 | 4.8678 | 3.2563 | 3.2448 | 3.2439 | 3.3194 | 3.3287 | 3.3173 | 1.9283 | 1.927 | 1.9185 | 0.81133 | 0.82824 | 0.77394 | 0.89741 | 0.9016 | 3.5591 | 3.5572 | 3.5789 | 2.0998 | 2.0996 | 2.1068 | 2.1139 | 2.2208 | 2.2316 | 2.2242 | 2.0907 | 2.0913 | 2.0981 | 0.87332 | 0.89993 | 0.87827 | 0.90689 | 4.8635 | 4.8719 | 4.8808 | 4.8639 | 5.295 | 5.2907 | 5.2826 | 5.1749 | 5.1771 | 5.2175 | 5.2843 | 5.3043 | 5.293 | 5.2932 | 5.3034 | 5.3113 | 5.3045 | 5.3194 | 5.076 | 5.0697 | 5.0724 | 5.5437 | 5.5157 | 5.5064 | 5.491 | 5.4786 | 5.4826 | 5.1164 | 5.0837 | 5.1154 | 2.2677 | 2.2716 | 2.2653 | 5.0749 | 5.0757 | 5.089 | 5.5529 | 5.5225 | 5.5315 | 5.5029 | 5.513 | 5.5463 | 5.1119 | 5.0984 | 5.0966 | 2.2775 | 2.2874 | 2.2923 | 2.136 | 2.1344 | 2.1239 | 1.9791 | 1.9755 | 1.9819 | 0.82416 | 0.8299 | 0.87659 | 0.93914 | 0.9198 | 0.92729 | 3.4629 | 3.4756 | 3.474 | 3.6779 | 3.6857 | 3.6916 | 5.0125 | 5.0357 | 5.0512 | 5.4851 | 5.4954 | 5.4851 | 5.4924 | 5.4956 | 5.4857 | 5.0671 | 5.0496 | 5.0464 | 2.2403 | 2.2349 | 2.2491 | 5.4632 | 5.4592 | 5.4415 | 5.4556 | 5.4714 | 5.4878 | 2.2689 | 2.2507 | 2.274 | 0.92179 | 0.92952 | 0.93996 | 0.87424 | 0.85589 | 0.85789 | 0.91385 | 0.92291 | 0.92444 | 2.1433 | 2.1403 | 2.1294 | 1.9858 | 1.9776 | 1.975 | 3.4291 | 3.4057 | 3.3592 | 3.6794 | 3.6723 | 3.6718 | 5.0149 | 5.0236 | 5.038 | 5.052 | 5.0508 | 5.0328 | 5.4704 | 5.4838 | 5.4722 | 5.4733 | 5.4556 | 5.4781 | 5.4703 | 5.4575 | 5.468 | 5.4615 | 5.4676 | 5.4607 | 5.0459 | 5.016 | 5.0417 | 2.2674 | 2.2661 | 2.2739 | 2.269 | 2.2731 | 2.2662
72
73 | Suction flow meter (low) Temp | ºC | 23.5147 | 23.4328 | 23.3883 | 22.9184 | 22.8296 | 22.7641 | 21.2502 | 21.2102 | 21.1259 | 20.913 | 20.8716 | 20.7969 | 20.6793 | 20.5983 | 20.5379 | 19.7559 | 19.7553 | 19.741 | 18.9023 | 18.6581 | 18.3921 | 22.3693 | 22.388 | 22.3845 | 22.4817 | 22.5132 | 22.542 | 22.6549 | 22.6767 | 22.7055 | 23.3211 | 23.3074 | 23.2991 | 23.2309 | 23.2364 | 23.2459 | 23.7533 | 23.7272 | 23.714 | 23.6977 | 23.5702 | 23.5569 | 23.5119 | 23.4423 | 23.2982 | 22.3945 | 22.3239 | 22.2083 | 21.0039 | 20.8648 | 20.7187 | 20.3358 | 20.0463 | 19.8197 | 23.4144 | 23.3217 | 23.2528 | 21.6434 | 21.6334 | 21.607 | 21.4336 | 21.4112 | 21.3888 | 20.0598 | 20.0167 | 19.9864 | 17.9231 | 17.8527 | 17.7983 | 17.5471 | 17.4421 | 22.4259 | 22.3736 | 22.3127 | 20.8064 | 20.7962 | 20.7794 | 20.5932 | 20.5328 | 20.5193 | 20.5045 | 19.9872 | 19.9415 | 19.9055 | 18.7521 | 18.6795 | 18.665 | 18.6497 | 26.1837 | 26.1401 | 26.1129 | 26.0928 | 25.9967 | 25.9339 | 25.9055 | 25.1433 | 24.9805 | 24.3988 | 25.1837 | 25.1726 | 25.0833 | 25.0247 | 24.8882 | 24.7915 | 24.7017 | 24.6017 | 23.3242 | 23.2553 | 23.1951 | 22.7517 | 22.6698 | 22.5846 | 22.4558 | 22.354 | 22.258 | 21.7372 | 21.5049 | 21.3427 | 18.9132 | 18.8514 | 18.7742 | 23.0502 | 22.933 | 22.8201 | 22.2498 | 22.1316 | 22.046 | 21.4822 | 21.3977 | 21.3175 | 21.0842 | 20.9579 | 20.8466 | 17.4399 | 17.384 | 17.2631 | 19.094 | 19.0085 | 18.8638 | 17.8161 | 17.6353 | 17.4635 | 19.5179 | 19.4865 | 19.4576 | 19.451 | 19.392 | 19.3776 | 21.1707 | 21.1609 | 21.1385 | 20.7782 | 20.7431 | 20.7168 | 22.9411 | 22.7288 | 22.594 | 22.2581 | 22.1752 | 22.0486 | 21.7812 | 21.6279 | 21.4427 | 22.0095 | 21.928 | 21.811 | 19.1893 | 19.053 | 18.9404 | 23.1801 | 23.0555 | 22.9106 | 22.49 | 22.3149 | 22.1282 | 20.5268 | 20.4491 | 20.3808 | 20.9852 | 20.9849 | 20.972 | 20.9918 | 20.9613 | 20.9482 | 20.9766 | 20.972 | 20.9724 | 20.7065 | 20.656 | 20.5653 | 21.0683 | 21.0529 | 21.0454 | 20.7916 | 20.7235 | 20.5816 | 19.8399 | 19.681 | 19.5202 | 24.3405 | 24.2527 | 24.1675 | 23.9421 | 23.8604 | 23.6399 | 23.0358 | 22.9666 | 22.8859 | 22.7883 | 22.7051 | 22.6297 | 22.3788 | 22.2923 | 22.2061 | 22.0063 | 21.9375 | 21.7938 | 21.4171 | 21.2857 | 21.1613 | 18.6941 | 18.6455 | 18.608 | 18.477 | 18.3875 | 18.3212
74 | Suction flow meter (low) Pressure | BarA | 3.7034 | 3.6923 | 3.6945 | 3.7203 | 3.714 | 3.7085 | 3.838 | 3.8489 | 3.8445 | 3.8266 | 3.8474 | 3.8475 | 3.8504 | 3.8402 | 3.8378 | 3.8766 | 3.8707 | 3.8579 | 3.8729 | 3.8773 | 3.8707 | 3.8401 | 3.8472 | 3.8453 | 3.8317 | 3.8354 | 3.8423 | 3.8442 | 3.84 | 3.8494 | 3.7088 | 3.6999 | 3.6933 | 3.7075 | 3.7073 | 3.705 | 3.7095 | 3.6166 | 3.6173 | 3.6182 | 3.6183 | 3.6219 | 3.6229 | 3.6276 | 3.626 | 3.3766 | 3.3696 | 3.3647 | 3.6655 | 3.6717 | 3.6681 | 3.6711 | 3.6699 | 3.6726 | 3.3914 | 3.3951 | 3.3922 | 3.7038 | 3.7028 | 3.6968 | 3.706 | 3.7068 | 3.7008 | 3.8443 | 3.8449 | 3.846 | 3.8561 | 3.8584 | 3.8732 | 3.8782 | 3.8653 | 3.7247 | 3.7226 | 3.7296 | 3.8468 | 3.8505 | 3.847 | 3.8552 | 3.8521 | 3.8563 | 3.8524 | 3.6494 | 3.6417 | 3.6543 | 3.8501 | 3.8812 | 3.8781 | 3.8795 | 3.6076 | 3.6189 | 3.6282 | 3.6153 | 3.6727 | 3.6845 | 3.6905 | 3.6679 | 3.6665 | 3.6912 | 3.6817 | 3.6906 | 3.6771 | 3.6759 | 3.6839 | 3.6895 | 3.6808 | 3.686 | 3.4138 | 3.416 | 3.4132 | 3.7119 | 3.6981 | 3.705 | 3.7002 | 3.6967 | 3.6994 | 3.6569 | 3.6451 | 3.6564 | 3.8468 | 3.8471 | 3.833 | 3.4136 | 3.4147 | 3.4154 | 3.7124 | 3.7009 | 3.6995 | 3.6977 | 3.7083 | 3.7157 | 3.6591 | 3.6511 | 3.6491 | 3.8374 | 3.8464 | 3.8401 | 3.8424 | 3.8403 | 3.8358 | 3.8416 | 3.8331 | 3.8347 | 3.8566 | 3.8593 | 3.8737 | 3.8539 | 3.8544 | 3.8526 | 3.6984 | 3.7057 | 3.704 | 3.7281 | 3.7293 | 3.728 | 3.3997 | 3.3977 | 3.395 | 3.6944 | 3.6901 | 3.6801 | 3.6926 | 3.6883 | 3.6831 | 3.6604 | 3.6516 | 3.6532 | 3.8359 | 3.8301 | 3.8405 | 3.6934 | 3.6947 | 3.687 | 3.693 | 3.7021 | 3.6962 | 3.8478 | 3.8382 | 3.8389 | 3.8417 | 3.8401 | 3.8399 | 3.8637 | 3.7947 | 3.7922 | 3.8103 | 3.8065 | 3.7971 | 3.8437 | 3.8405 | 3.8274 | 3.8249 | 3.8148 | 3.817 | 3.7051 | 3.7058 | 3.7009 | 3.7274 | 3.7179 | 3.7156 | 3.3919 | 3.3992 | 3.4037 | 3.4088 | 3.4047 | 3.3939 | 3.6978 | 3.694 | 3.6965 | 3.6924 | 3.6853 | 3.6995 | 3.6906 | 3.6826 | 3.686 | 3.6824 | 3.6849 | 3.6841 | 3.6469 | 3.6277 | 3.6387 | 3.8471 | 3.8369 | 3.8421 | 3.8539 | 3.8477 | 3.849
75 | Suction flow meter (low) gauge | ºC | 6.6636 | 6.5762 | 6.5942 | 6.7968 | 6.7472 | 6.704 | 7.7088 | 7.7926 | 7.7593 | 7.6219 | 7.7814 | 7.7816 | 7.8039 | 7.7263 | 7.7079 | 8.0041 | 7.9587 | 7.8612 | 7.9759 | 8.0093 | 7.9587 | 7.7253 | 7.7793 | 7.7649 | 7.6607 | 7.6889 | 7.7421 | 7.7566 | 7.7242 | 7.7963 | 6.7069 | 6.6365 | 6.5843 | 6.6961 | 6.695 | 6.6765 | 6.7118 | 5.9749 | 5.9801 | 5.9872 | 5.9885 | 6.0172 | 6.0248 | 6.0628 | 6.0495 | 3.9998 | 3.9406 | 3.8991 | 6.3647 | 6.4135 | 6.3853 | 6.4089 | 6.3994 | 6.4211 | 4.1247 | 4.1555 | 4.1317 | 6.667 | 6.659 | 6.6121 | 6.6848 | 6.6907 | 6.6434 | 7.7574 | 7.7621 | 7.7702 | 7.8475 | 7.8654 | 7.9779 | 8.016 | 7.9178 | 6.8313 | 6.8149 | 6.8697 | 7.7766 | 7.8049 | 7.7779 | 7.841 | 7.8167 | 7.8494 | 7.8194 | 6.2362 | 6.1754 | 6.2753 | 7.8018 | 8.0389 | 8.0153 | 8.0256 | 5.9023 | 5.9932 | 6.0674 | 5.9644 | 6.4217 | 6.5147 | 6.5627 | 6.3833 | 6.3724 | 6.5675 | 6.4931 | 6.5634 | 6.4562 | 6.4467 | 6.5106 | 6.5547 | 6.4858 | 6.5269 | 4.3131 | 4.3313 | 4.3074 | 6.7307 | 6.6221 | 6.6766 | 6.6388 | 6.6114 | 6.6326 | 6.2966 | 6.2021 | 6.2919 | 7.7766 | 7.7789 | 7.6709 | 4.3114 | 4.3199 | 4.3263 | 6.7351 | 6.6444 | 6.6333 | 6.6192 | 6.7026 | 6.7604 | 6.3137 | 6.2503 | 6.2342 | 7.7049 | 7.7738 | 7.7254 | 7.7431 | 7.7265 | 7.6923 | 7.7364 | 7.6713 | 7.6836 | 7.8512 | 7.8719 | 7.9818 | 7.8309 | 7.835 | 7.821 | 6.6249 | 6.6822 | 6.6689 | 6.8582 | 6.8673 | 6.8572 | 4.1944 | 4.178 | 4.1547 | 6.5929 | 6.5595 | 6.48 | 6.5789 | 6.5447 | 6.5038 | 6.3239 | 6.254 | 6.2665 | 7.6932 | 7.649 | 7.7286 | 6.5856 | 6.5953 | 6.5344 | 6.5821 | 6.6538 | 6.6074 | 7.7843 | 7.7107 | 7.7159 | 7.7379 | 7.7256 | 7.724 | 7.9055 | 7.3759 | 7.357 | 7.4963 | 7.467 | 7.3946 | 7.7529 | 7.7284 | 7.6279 | 7.6083 | 7.5307 | 7.5476 | 6.6775 | 6.6825 | 6.6444 | 6.8529 | 6.778 | 6.7599 | 4.129 | 4.1905 | 4.2277 | 4.2711 | 4.2363 | 4.1458 | 6.6199 | 6.5897 | 6.61 | 6.5776 | 6.5211 | 6.6335 | 6.5629 | 6.5002 | 6.5268 | 6.4984 | 6.5183 | 6.5121 | 6.2168 | 6.0633 | 6.1509 | 7.7792 | 7.7006 | 7.7404 | 7.8304 | 7.7831 | 7.7933
76 | Suction flow meter (low) SH | ºC | 16.8511 | 16.8565 | 16.7941 | 16.1216 | 16.0824 | 16.0601 | 13.5414 | 13.4176 | 13.3666 | 13.2911 | 13.0901 | 13.0153 | 12.8754 | 12.872 | 12.83 | 11.7518 | 11.7966 | 11.8799 | 10.9264 | 10.6488 | 10.4334 | 14.644 | 14.6087 | 14.6196 | 14.8211 | 14.8243 | 14.7999 | 14.8982 | 14.9525 | 14.9093 | 16.6142 | 16.671 | 16.7148 | 16.5348 | 16.5414 | 16.5694 | 17.0415 | 17.7523 | 17.7339 | 17.7105 | 17.5817 | 17.5397 | 17.4871 | 17.3794 | 17.2487 | 18.3946 | 18.3833 | 18.3092 | 14.6392 | 14.4513 | 14.3334 | 13.9269 | 13.6469 | 13.3986 | 19.2897 | 19.1662 | 19.1211 | 14.9763 | 14.9744 | 14.9949 | 14.7488 | 14.7206 | 14.7455 | 12.3025 | 12.2547 | 12.2162 | 10.0756 | 9.9872 | 9.8204 | 9.5312 | 9.5243 | 15.5946 | 15.5587 | 15.443 | 13.0299 | 12.9912 | 13.0016 | 12.7522 | 12.7161 | 12.6699 | 12.6851 | 13.751 | 13.7661 | 13.6302 | 10.9503 | 10.6406 | 10.6497 | 10.624 | 20.2814 | 20.1469 | 20.0455 | 20.1284 | 19.5749 | 19.4191 | 19.3428 | 18.76 | 18.608 | 17.8313 | 18.6906 | 18.6092 | 18.6271 | 18.578 | 18.3776 | 18.2368 | 18.216 | 18.0748 | 19.011 | 18.924 | 18.8877 | 16.0209 | 16.0476 | 15.9081 | 15.817 | 15.7425 | 15.6253 | 15.4406 | 15.3028 | 15.0508 | 11.1365 | 11.0725 | 11.1033 | 18.7388 | 18.613 | 18.4938 | 15.5148 | 15.4872 | 15.4128 | 14.863 | 14.6952 | 14.5571 | 14.7705 | 14.7076 | 14.6124 | 9.735 | 9.6103 | 9.5377 | 11.3509 | 11.2819 | 11.1715 | 10.0797 | 9.9641 | 9.78 | 11.6668 | 11.6147 | 11.4758 | 11.62 | 11.557 | 11.5566 | 14.5458 | 14.4787 | 14.4696 | 13.9201 | 13.8758 | 13.8595 | 18.7467 | 18.5509 | 18.4393 | 15.6652 | 15.6157 | 15.5686 | 15.2023 | 15.0832 | 14.9389 | 15.6857 | 15.674 | 15.5444 | 11.4961 | 11.4041 | 11.2118 | 16.5945 | 16.4603 | 16.3762 | 15.9079 | 15.6611 | 15.5208 | 12.7425 | 12.7384 | 12.6648 | 13.2473 | 13.2592 | 13.248 | 13.0862 | 13.5853 | 13.5912 | 13.4803 | 13.505 | 13.5778 | 12.9536 | 12.9276 | 12.9374 | 13.4599 | 13.5222 | 13.4978 | 14.1141 | 14.041 | 13.9371 | 12.987 | 12.903 | 12.7603 | 20.2115 | 20.0622 | 19.9398 | 19.671 | 19.6241 | 19.494 | 16.4158 | 16.3768 | 16.2759 | 16.2107 | 16.1839 | 15.9963 | 15.8159 | 15.7922 | 15.6794 | 15.5079 | 15.4191 | 15.2817 | 15.2003 | 15.2224 | 15.0104 | 10.9149 | 10.9449 | 10.8676 | 10.6466 | 10.6045 | 10.5279
77 | suction flow meter (low) Low SH warning |  | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok
78 | Suction flow meter (low) enthalpy | KJ/kg | 417.8918 | 417.8409 | 417.7955 | 417.3111 | 417.2438 | 417.196 | 415.5262 | 415.4649 | 415.3974 | 415.2425 | 415.1576 | 415.0891 | 414.9747 | 414.9233 | 414.8733 | 414.0672 | 414.0803 | 414.0966 | 413.2915 | 413.0568 | 412.8279 | 416.5471 | 416.5487 | 416.5496 | 416.6687 | 416.6894 | 416.7005 | 416.7998 | 416.8291 | 416.8348 | 417.7033 | 417.7102 | 417.7169 | 417.624 | 417.6293 | 417.6431 | 418.0963 | 418.2709 | 418.2575 | 418.2408 | 418.1245 | 418.1047 | 418.0618 | 417.9882 | 417.8607 | 417.5756 | 417.5269 | 417.4331 | 415.6854 | 415.545 | 415.4198 | 415.0642 | 414.803 | 414.5902 | 418.465 | 418.3736 | 418.3173 | 416.1838 | 416.177 | 416.166 | 415.9874 | 415.9654 | 415.9583 | 414.4202 | 414.3793 | 414.349 | 412.4311 | 412.3608 | 412.2759 | 412.033 | 411.967 | 416.852 | 416.8088 | 416.738 | 415.0993 | 415.0815 | 415.0742 | 414.8847 | 414.8365 | 414.8144 | 414.8097 | 414.7953 | 414.7709 | 414.7098 | 413.2066 | 413.0674 | 413.0613 | 413.044 | 420.5245 | 420.4615 | 420.4176 | 420.4259 | 420.2196 | 420.1379 | 420.0994 | 419.4519 | 419.3064 | 418.7241 | 419.4596 | 419.4309 | 419.3779 | 419.327 | 419.1856 | 419.0857 | 419.0222 | 418.92 | 418.3361 | 418.2692 | 418.2209 | 417.1773 | 417.1325 | 417.0398 | 416.9328 | 416.8475 | 416.754 | 416.3724 | 416.187 | 416.0144 | 413.3621 | 413.3048 | 413.2666 | 418.0889 | 417.9808 | 417.8772 | 416.7181 | 416.6355 | 416.5606 | 416.0502 | 415.9497 | 415.8602 | 415.7729 | 415.6755 | 415.5786 | 412.0312 | 411.9585 | 411.8624 | 413.5382 | 413.4648 | 413.3424 | 412.367 | 412.2211 | 412.0595 | 413.8948 | 413.8597 | 413.7999 | 413.8394 | 413.784 | 413.775 | 415.7644 | 415.7393 | 415.7227 | 415.3401 | 415.3054 | 415.2842 | 418.02 | 417.8324 | 417.7165 | 416.7652 | 416.6988 | 416.6055 | 416.3342 | 416.2039 | 416.0464 | 416.613 | 416.5579 | 416.4479 | 413.6407 | 413.5291 | 413.4017 | 417.608 | 417.4917 | 417.3762 | 416.9796 | 416.8001 | 416.6427 | 414.8406 | 414.7911 | 414.7269 | 415.2746 | 415.2779 | 415.2666 | 415.2313 | 415.3584 | 415.3519 | 415.3374 | 415.3417 | 415.3632 | 415.0146 | 414.9756 | 414.9221 | 415.3887 | 415.3973 | 415.3855 | 415.4037 | 415.3401 | 415.2214 | 414.4846 | 414.3611 | 414.2195 | 419.3005 | 419.206 | 419.1197 | 418.9052 | 418.84 | 418.6634 | 417.4669 | 417.4121 | 417.333 | 417.2529 | 417.1925 | 417.0929 | 416.8836 | 416.822 | 416.7361 | 416.5618 | 416.4935 | 416.3642 | 416.1029 | 416.0257 | 415.8883 | 413.1602 | 413.1396 | 413.093 | 412.9452 | 412.8776 | 412.8135
79 | Suction flow meter (low) specific Vol | m3/kg | 0.060011 | 0.060186 | 0.060133 | 0.059548 | 0.059635 | 0.059714 | 0.057097 | 0.056906 | 0.056955 | 0.057192 | 0.056839 | 0.056818 | 0.056739 | 0.056883 | 0.056906 | 0.056066 | 0.056161 | 0.056364 | 0.055894 | 0.055758 | 0.055792 | 0.057363 | 0.057252 | 0.057282 | 0.057532 | 0.05748 | 0.057373 | 0.057372 | 0.057447 | 0.0573 | 0.05986 | 0.060015 | 0.060131 | 0.05986 | 0.059864 | 0.059908 | 0.059968 | 0.061646 | 0.06163 | 0.061609 | 0.06157 | 0.0615 | 0.06147 | 0.061362 | 0.061353 | 0.066036 | 0.066164 | 0.066234 | 0.059991 | 0.059842 | 0.059864 | 0.059704 | 0.059644 | 0.059532 | 0.066023 | 0.065918 | 0.065958 | 0.059487 | 0.059503 | 0.059601 | 0.05939 | 0.05937 | 0.05947 | 0.056671 | 0.056649 | 0.056624 | 0.055898 | 0.055841 | 0.05559 | 0.055442 | 0.055619 | 0.059336 | 0.059358 | 0.059219 | 0.056832 | 0.056769 | 0.056822 | 0.056637 | 0.056672 | 0.056599 | 0.056659 | 0.059997 | 0.060122 | 0.059885 | 0.056221 | 0.055701 | 0.055747 | 0.055721 | 0.062499 | 0.062274 | 0.062094 | 0.062329 | 0.061242 | 0.061012 | 0.060895 | 0.061096 | 0.061076 | 0.060471 | 0.060856 | 0.060693 | 0.060913 | 0.060918 | 0.060735 | 0.060608 | 0.06074 | 0.060619 | 0.065525 | 0.06546 | 0.065502 | 0.05965 | 0.059872 | 0.059726 | 0.059775 | 0.059809 | 0.059735 | 0.06035 | 0.060501 | 0.060251 | 0.056318 | 0.056297 | 0.056505 | 0.06545 | 0.065394 | 0.065345 | 0.059502 | 0.059673 | 0.059675 | 0.05955 | 0.05934 | 0.059189 | 0.060129 | 0.060238 | 0.060243 | 0.056068 | 0.055907 | 0.055976 | 0.056439 | 0.056451 | 0.056484 | 0.056104 | 0.056193 | 0.056119 | 0.056325 | 0.056272 | 0.056032 | 0.056349 | 0.056325 | 0.05635 | 0.059451 | 0.05932 | 0.059344 | 0.058822 | 0.058792 | 0.058807 | 0.065709 | 0.065688 | 0.065706 | 0.059824 | 0.059876 | 0.060021 | 0.059724 | 0.059758 | 0.059799 | 0.060364 | 0.060501 | 0.060439 | 0.056571 | 0.056628 | 0.056428 | 0.060095 | 0.060039 | 0.060136 | 0.059912 | 0.059703 | 0.059755 | 0.05674 | 0.056876 | 0.056846 | 0.056963 | 0.056989 | 0.056989 | 0.056607 | 0.057736 | 0.057774 | 0.05748 | 0.057542 | 0.057699 | 0.056855 | 0.056894 | 0.057085 | 0.057263 | 0.057426 | 0.057388 | 0.059228 | 0.059198 | 0.059244 | 0.058574 | 0.058696 | 0.058691 | 0.066284 | 0.066103 | 0.065985 | 0.065811 | 0.065874 | 0.066036 | 0.059978 | 0.060027 | 0.059959 | 0.060005 | 0.06011 | 0.059835 | 0.059925 | 0.060043 | 0.059959 | 0.059967 | 0.059903 | 0.059878 | 0.060443 | 0.060757 | 0.060521 | 0.056253 | 0.056407 | 0.056312 | 0.056086 | 0.056161 | 0.056122
80 | Suction flow meter (low) vol Flow | m^3/hr | 337.5 | 337.5 | 337.5 | 63.271 | 337.5 | 337.5 | 337.5 | 79.3762 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 62.6372 | 337.5 | 337.5 | 337.5 | 337.5 | 34.8992 | 63.7147 | 337.5 | 337.5 | 337.5 | 283.0505 | 337.5 | 63.5516 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 327.8145 | 61.6379 | 62.2928 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 279.7698 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 61.9268 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 62.8289 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 280.1211 | 337.5 | 53.2033 | 337.5 | 286.7679 | 337.5 | 337.5 | 337.5 | 337.5 | 62.6991 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 61.0153 | 337.5 | 337.5 | 337.5 | 62.0509 | 307.1505 | 337.5 | 337.5 | 62.5315 | 337.5 | 23.8928 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 63.0696 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 311.0876 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 57.5395 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 62.3779 | 62.5444 | 337.5 | 62.3906 | 337.5 | 337.5 | 337.5 | 61.4216 | 337.5 | 337.5 | 337.5 | 337.5 | 69.6895 | 337.5 | 63.3226 | 63.5784 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 41.2871 | 337.5 | 337.5 | 337.5 | 337.5 | 55.1762 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 178.8154 | 337.5 | 337.5 | 337.5 | 59.5524 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 31.9574 | 337.5 | 60.6035 | 337.5 | 337.5 | 337.5 | 46.8926 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 302.3039 | 337.5 | 50.415 | 337.5 | 337.5 | 337.5 | 45.4871
81 | Suction flow meter (low) mass Flow | kg/s | 1.5622 | 1.5577 | 1.559 | 0.29514 | 1.5721 | 1.57 | 1.642 | 0.38746 | 1.646 | 1.6392 | 1.6494 | 1.65 | 1.6523 | 1.6481 | 1.6475 | 1.6721 | 1.6693 | 1.6633 | 0.31129 | 1.6814 | 1.6804 | 1.6343 | 1.6375 | 0.16924 | 0.30763 | 1.631 | 1.6341 | 1.6341 | 1.3686 | 1.6361 | 0.29491 | 1.5621 | 1.5591 | 1.5662 | 1.5661 | 1.5649 | 1.5633 | 1.5208 | 1.5212 | 1.5217 | 1.479 | 0.2784 | 0.2815 | 1.5278 | 1.528 | 1.4197 | 1.4169 | 1.4154 | 1.5627 | 1.5666 | 1.2982 | 1.5702 | 1.5718 | 1.5748 | 1.42 | 1.4222 | 1.4214 | 1.576 | 1.5756 | 1.573 | 1.5786 | 0.28974 | 1.5764 | 1.6543 | 1.6549 | 1.6557 | 1.6771 | 1.6789 | 1.6865 | 1.691 | 1.6856 | 1.58 | 1.5794 | 1.5831 | 1.6496 | 1.6514 | 1.6499 | 1.6553 | 1.6542 | 1.6564 | 0.30803 | 1.5626 | 1.5593 | 1.5655 | 1.6675 | 1.6831 | 1.6817 | 1.6825 | 1.5 | 1.2495 | 1.5098 | 0.23711 | 1.5308 | 1.3056 | 1.5395 | 1.5345 | 1.535 | 1.5503 | 0.28619 | 1.5447 | 1.5391 | 1.5389 | 1.5436 | 1.5468 | 1.5435 | 1.5465 | 1.4307 | 1.4322 | 0.25875 | 1.5717 | 1.5658 | 1.5697 | 0.28835 | 1.4265 | 1.5694 | 1.5534 | 0.2871 | 1.556 | 0.11785 | 1.6653 | 1.6591 | 1.4324 | 1.4336 | 1.4347 | 1.5756 | 1.5711 | 0.29358 | 1.5743 | 1.5799 | 1.5839 | 1.5591 | 1.5563 | 1.5562 | 1.6721 | 1.6769 | 1.6748 | 1.6611 | 1.6607 | 1.6598 | 1.671 | 1.6684 | 1.5398 | 1.6645 | 1.666 | 1.6731 | 1.6637 | 1.6645 | 0.28364 | 1.5769 | 1.5804 | 1.5798 | 1.5938 | 1.5946 | 1.5942 | 1.4267 | 1.4272 | 0.26371 | 0.29041 | 1.5657 | 0.28875 | 1.5697 | 1.5688 | 1.5678 | 0.28264 | 1.5496 | 1.5511 | 1.6572 | 1.6555 | 0.34306 | 1.56 | 0.29297 | 0.29368 | 1.5648 | 1.5703 | 1.5689 | 1.6523 | 1.6483 | 1.6492 | 1.6458 | 0.20124 | 1.6451 | 1.6562 | 1.6238 | 1.6227 | 0.26665 | 1.6292 | 1.6248 | 1.6489 | 1.6478 | 1.6423 | 0.86742 | 1.6325 | 1.6336 | 1.5829 | 0.27944 | 1.5824 | 1.6005 | 1.5972 | 1.5973 | 1.4144 | 1.4182 | 1.4208 | 1.4245 | 1.4232 | 1.4197 | 0.14801 | 1.5618 | 0.28076 | 1.5624 | 1.5597 | 1.5668 | 0.21737 | 1.5614 | 1.5636 | 1.5633 | 1.565 | 1.5657 | 1.5511 | 1.543 | 1.3875 | 1.6666 | 0.24827 | 1.6648 | 1.6716 | 1.6693 | 0.22514
82
83 | Active flow meter : NA adding apples & oranges! | m^3/hr
84 | Active flow meter | kg/s | 3.4113 | 3.3961 | 3.3989 | 3.6032 | 3.6028 | 3.5954 | 2.245 | 2.2506 | 2.2466 | 1.9719 | 1.9843 | 1.9989 | 2.0022 | 1.9923 | 1.9941 | 0.90279 | 0.90239 | 0.90339 | 0.95738 | 0.96313 | 0.97594 | 1.9955 | 2.0039 | 2.0079 | 2.1523 | 2.1567 | 2.1625 | 2.1544 | 2.1618 | 2.1624 | 3.4232 | 3.4153 | 3.4132 | 3.6009 | 3.6014 | 3.5939 | 3.5601 | 4.9802 | 4.9928 | 4.989 | 4.9863 | 4.9803 | 4.9786 | 4.9947 | 4.986 | 4.9395 | 4.9277 | 4.9444 | 5.3674 | 5.3761 | 5.3614 | 5.3669 | 5.3656 | 5.3682 | 4.872 | 4.8748 | 4.8678 | 3.2563 | 3.2448 | 3.2439 | 3.3194 | 3.3287 | 3.3173 | 1.9283 | 1.927 | 1.9185 | 0.81133 | 0.82824 | 0.77394 | 0.89741 | 0.9016 | 3.5591 | 3.5572 | 3.5789 | 2.0998 | 2.0996 | 2.1068 | 2.1139 | 2.2208 | 2.2316 | 2.2242 | 2.0907 | 2.0913 | 2.0981 | 0.87332 | 0.89993 | 0.87827 | 0.90689 | 4.8635 | 4.8719 | 4.8808 | 4.8639 | 5.295 | 5.2907 | 5.2826 | 5.1749 | 5.1771 | 5.2175 | 5.2843 | 5.3043 | 5.293 | 5.2932 | 5.3034 | 5.3113 | 5.3045 | 5.3194 | 5.076 | 5.0697 | 5.0724 | 5.5437 | 5.5157 | 5.5064 | 5.491 | 5.4786 | 5.4826 | 5.1164 | 5.0837 | 5.1154 | 2.2677 | 2.2716 | 2.2653 | 5.0749 | 5.0757 | 5.089 | 5.5529 | 5.5225 | 5.5315 | 5.5029 | 5.513 | 5.5463 | 5.1119 | 5.0984 | 5.0966 | 2.2775 | 2.2874 | 2.2923 | 2.136 | 2.1344 | 2.1239 | 1.9791 | 1.9755 | 1.9819 | 0.82416 | 0.8299 | 0.87659 | 0.93914 | 0.9198 | 0.92729 | 3.4629 | 3.4756 | 3.474 | 3.6779 | 3.6857 | 3.6916 | 5.0125 | 5.0357 | 5.0512 | 5.4851 | 5.4954 | 5.4851 | 5.4924 | 5.4956 | 5.4857 | 5.0671 | 5.0496 | 5.0464 | 2.2403 | 2.2349 | 2.2491 | 5.4632 | 5.4592 | 5.4415 | 5.4556 | 5.4714 | 5.4878 | 2.2689 | 2.2507 | 2.274 | 0.92179 | 0.92952 | 0.93996 | 0.87424 | 0.85589 | 0.85789 | 0.91385 | 0.92291 | 0.92444 | 2.1433 | 2.1403 | 2.1294 | 1.9858 | 1.9776 | 1.975 | 3.4291 | 3.4057 | 3.3592 | 3.6794 | 3.6723 | 3.6718 | 5.0149 | 5.0236 | 5.038 | 5.052 | 5.0508 | 5.0328 | 5.4704 | 5.4838 | 5.4722 | 5.4733 | 5.4556 | 5.4781 | 5.4703 | 5.4575 | 5.468 | 5.4615 | 5.4676 | 5.4607 | 5.0459 | 5.016 | 5.0417 | 2.2674 | 2.2661 | 2.2739 | 2.269 | 2.2731 | 2.2662
85 | Flow meter used, 1=large, 2=small, 3=both |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
86 | Total suction vol flow, at flow meter | m^3/hr | 708.5533 | 708.239 | 708.9824 | 753.3499 | 754.6669 | 753.9793 | 459.6092 | 459.1117 | 458.4765 | 402.5823 | 402.5339 | 405.1102 | 404.9291 | 403.8661 | 404.6599 | 179.8175 | 180.006 | 180.6444 | 192.8903 | 193.2239 | 196.0088 | 402.7638 | 402.2725 | 402.9232 | 432.2026 | 432.5648 | 432.9053 | 431.5543 | 433.2524 | 432.0915 | 717.0727 | 716.8703 | 717.2743 | 752.582 | 752.1472 | 750.0536 | 744.4851 | 1058.93 | 1061.3358 | 1060.2397 | 1059.7164 | 1057.6105 | 1057.1208 | 1059.3345 | 1060.6859 | 1120.7046 | 1122.7851 | 1125.4913 | 1126.2432 | 1125.8052 | 1122.9724 | 1128.7409 | 1127.6508 | 1125.5224 | 1094.5429 | 1094.4888 | 1094.2393 | 682.6334 | 679.5682 | 680.3845 | 695.7665 | 697.6081 | 696.4332 | 389.4074 | 389.6914 | 388.8562 | 163.5925 | 166.9995 | 155.5166 | 179.5908 | 180.9583 | 735.1244 | 734.6323 | 734.4339 | 421.724 | 421.0643 | 422.7079 | 422.476 | 444.7665 | 446.4117 | 445.5893 | 444.5517 | 445.6618 | 445.5565 | 175.3381 | 180.2559 | 176.42 | 182.0249 | 1032.9634 | 1033.6461 | 1034.0407 | 1036.3232 | 1100.9827 | 1103.1869 | 1101.1818 | 1107.5314 | 1112.7848 | 1109.5549 | 1106.4373 | 1107.5957 | 1107.953 | 1106.9884 | 1107.5945 | 1107.8572 | 1108.7734 | 1107.5527 | 1138.231 | 1138.4527 | 1142.0461 | 1141.9203 | 1141.2077 | 1141.1278 | 1145.9468 | 1145.4018 | 1146.4713 | 1066.1123 | 1071.2948 | 1069.3823 | 457.3374 | 457.0021 | 458.2307 | 1135.4609 | 1134.0225 | 1134.7348 | 1144.781 | 1140.8975 | 1140.9929 | 1147.2442 | 1141.9289 | 1147.5331 | 1068.0927 | 1069.1057 | 1069.6966 | 458.1127 | 459.1281 | 460.5906 | 432.0657 | 432.1927 | 432.6537 | 402.8876 | 402.368 | 402.4024 | 165.5452 | 166.7393 | 175.6701 | 189.3809 | 185.1499 | 186.6649 | 721.4893 | 722.4118 | 722.2458 | 763.2945 | 764.0845 | 765.0877 | 1133.5116 | 1132.8965 | 1126.0625 | 1134.0115 | 1136.7857 | 1137.393 | 1134.7679 | 1137.4385 | 1134.6126 | 1063.7015 | 1072.4233 | 1068.1636 | 455.8056 | 454.8754 | 455.8404 | 1141.5298 | 1139.8152 | 1139.1977 | 1141.3384 | 1142.9751 | 1143.4111 | 456.1142 | 453.9677 | 458.4884 | 186.2945 | 187.6422 | 189.594 | 174.9865 | 174.8234 | 175.5865 | 186.106 | 188.1258 | 189.2072 | 431.7579 | 431.3527 | 431.2683 | 400.6899 | 400.7723 | 400.0052 | 715.6684 | 710.2543 | 701.2182 | 765.1471 | 764.9557 | 764.682 | 1131.1487 | 1130.6586 | 1131.5999 | 1131.7888 | 1131.9556 | 1130.0768 | 1134.7434 | 1136.2509 | 1136.3222 | 1135.5056 | 1134.2828 | 1134.8401 | 1137.0787 | 1136.5509 | 1135.5334 | 1136.037 | 1137.9212 | 1135.7186 | 1063.9666 | 1063.7318 | 1064.1486 | 456.6768 | 458.1315 | 459.0695 | 456.3715 | 458.1036 | 457.2845
87 | Total Suction mass Flow | kg/s | 3.4113 | 3.3961 | 3.3989 | 3.6032 | 3.6028 | 3.5954 | 2.245 | 2.2506 | 2.2466 | 1.9719 | 1.9843 | 1.9989 | 2.0022 | 1.9923 | 1.9941 | 0.90279 | 0.90239 | 0.90339 | 0.95738 | 0.96313 | 0.97594 | 1.9955 | 2.0039 | 2.0079 | 2.1523 | 2.1567 | 2.1625 | 2.1544 | 2.1618 | 2.1624 | 3.4232 | 3.4153 | 3.4132 | 3.6009 | 3.6014 | 3.5939 | 3.5601 | 4.9802 | 4.9928 | 4.989 | 4.9863 | 4.9803 | 4.9786 | 4.9947 | 4.986 | 4.9395 | 4.9277 | 4.9444 | 5.3674 | 5.3761 | 5.3614 | 5.3669 | 5.3656 | 5.3682 | 4.872 | 4.8748 | 4.8678 | 3.2563 | 3.2448 | 3.2439 | 3.3194 | 3.3287 | 3.3173 | 1.9283 | 1.927 | 1.9185 | 0.81133 | 0.82824 | 0.77394 | 0.89741 | 0.9016 | 3.5591 | 3.5572 | 3.5789 | 2.0998 | 2.0996 | 2.1068 | 2.1139 | 2.2208 | 2.2316 | 2.2242 | 2.0907 | 2.0913 | 2.0981 | 0.87332 | 0.89993 | 0.87827 | 0.90689 | 4.8635 | 4.8719 | 4.8808 | 4.8639 | 5.295 | 5.2907 | 5.2826 | 5.1749 | 5.1771 | 5.2175 | 5.2843 | 5.3043 | 5.293 | 5.2932 | 5.3034 | 5.3113 | 5.3045 | 5.3194 | 5.076 | 5.0697 | 5.0724 | 5.5437 | 5.5157 | 5.5064 | 5.491 | 5.4786 | 5.4826 | 5.1164 | 5.0837 | 5.1154 | 2.2677 | 2.2716 | 2.2653 | 5.0749 | 5.0757 | 5.089 | 5.5529 | 5.5225 | 5.5315 | 5.5029 | 5.513 | 5.5463 | 5.1119 | 5.0984 | 5.0966 | 2.2775 | 2.2874 | 2.2923 | 2.136 | 2.1344 | 2.1239 | 1.9791 | 1.9755 | 1.9819 | 0.82416 | 0.8299 | 0.87659 | 0.93914 | 0.9198 | 0.92729 | 3.4629 | 3.4756 | 3.474 | 3.6779 | 3.6857 | 3.6916 | 5.0125 | 5.0357 | 5.0512 | 5.4851 | 5.4954 | 5.4851 | 5.4924 | 5.4956 | 5.4857 | 5.0671 | 5.0496 | 5.0464 | 2.2403 | 2.2349 | 2.2491 | 5.4632 | 5.4592 | 5.4415 | 5.4556 | 5.4714 | 5.4878 | 2.2689 | 2.2507 | 2.274 | 0.92179 | 0.92952 | 0.93996 | 0.87424 | 0.85589 | 0.85789 | 0.91385 | 0.92291 | 0.92444 | 2.1433 | 2.1403 | 2.1294 | 1.9858 | 1.9776 | 1.975 | 3.4291 | 3.4057 | 3.3592 | 3.6794 | 3.6723 | 3.6718 | 5.0149 | 5.0236 | 5.038 | 5.052 | 5.0508 | 5.0328 | 5.4704 | 5.4838 | 5.4722 | 5.4733 | 5.4556 | 5.4781 | 5.4703 | 5.4575 | 5.468 | 5.4615 | 5.4676 | 5.4607 | 5.0459 | 5.016 | 5.0417 | 2.2674 | 2.2661 | 2.2739 | 2.269 | 2.2731 | 2.2662
88
89 | Suction orifice Plate Temp | ºC | 15.2453 | 15.4783 | 15.4345 | 17.5607 | 17.521 | 17.4276 | 20.2842 | 20.2017 | 20.063 | 19.0741 | 18.9792 | 18.8013 | 18.5706 | 18.4883 | 18.493 | 17.1189 | 17.0125 | 16.7228 | 18.9759 | 18.5056 | 18.4042 | 17.3922 | 16.9391 | 16.7895 | 16.1943 | 16.1802 | 16.1937 | 16.3087 | 16.2008 | 16.1704 | 17.1666 | 17.0217 | 16.8172 | 16.5701 | 16.3831 | 16.1233 | 16.9093 | 14.3163 | 14.3056 | 14.2855 | 14.3732 | 14.3977 | 14.4554 | 14.6297 | 14.9905 | 12.1148 | 12.491 | 11.6225 | 14.4707 | 14.4767 | 14.447 | 15.2061 | 14.9845 | 14.7759 | 11.0711 | 11.1825 | 11.2949 | 16.9689 | 16.7949 | 16.82 | 17.2337 | 17.2418 | 17.2429 | 18.3113 | 18.719 | 19.14 | 18.3754 | 18.4238 | 18.4575 | 17.928 | 17.8053 | 15.2657 | 15.1213 | 14.6392 | 16.9474 | 16.8708 | 16.7454 | 16.3672 | 16.8494 | 16.8831 | 16.9756 | 16.818 | 16.8359 | 16.894 | 17.6224 | 18.5485 | 18.5994 | 18.336 | 13.6671 | 14.0142 | 14.3711 | 14.4289 | 13.5508 | 14.6941 | 15.0175 | 18.91 | 19.3815 | 18.9184 | 21.6936 | 21.6804 | 21.6293 | 21.5924 | 21.5042 | 21.445 | 21.4117 | 21.3538 | 12.1552 | 12.4514 | 12.4251 | 13.616 | 13.7924 | 14.5835 | 15.4833 | 15.6995 | 15.957 | 13.1966 | 13.8774 | 13.2902 | 17.6319 | 17.477 | 17.6169 | 11.4366 | 11.2606 | 11.0319 | 13.6057 | 13.3032 | 12.8859 | 14.7596 | 14.4407 | 14.5919 | 13.3308 | 13.5145 | 13.5078 | 16.7238 | 16.7508 | 16.4436 | 18.3129 | 18.5421 | 19.3375 | 19.1512 | 18.6899 | 18.3133 | 17.8738 | 18.0498 | 18.1805 | 18.1335 | 17.8199 | 17.7217 | 15.4962 | 15.4738 | 15.4137 | 16.3355 | 16.1358 | 15.6846 | 12.61 | 11.434 | 10.0759 | 13.2532 | 13.0466 | 13.0493 | 13.1758 | 12.8939 | 12.9535 | 14.8885 | 16.1038 | 15.307 | 18.7739 | 18.5876 | 18.4132 | 15.277 | 15.2205 | 15.4129 | 15.5764 | 15.5655 | 14.7076 | 17.317 | 17.3614 | 17.2785 | 17.975 | 17.7715 | 17.7131 | 17.6607 | 17.7695 | 17.9254 | 17.9538 | 18.0434 | 18.2548 | 17.5106 | 17.506 | 17.7587 | 16.8961 | 17.0643 | 17.0753 | 16.19 | 16.1314 | 16.3208 | 16.6937 | 16.4427 | 16.3142 | 11.8317 | 11.827 | 11.7316 | 11.6198 | 11.323 | 10.9422 | 13.9971 | 13.8499 | 14.136 | 13.8051 | 13.8426 | 14.0177 | 14.0055 | 13.9145 | 13.6531 | 13.8262 | 13.8955 | 13.8649 | 14.34 | 14.1076 | 14.024 | 17.6488 | 17.7462 | 17.7469 | 17.7016 | 17.8186 | 18.0213
90 | Suction orifice plate Pressure | BarA | 3.6758 | 3.6644 | 3.6705 | 3.6877 | 3.6863 | 3.6779 | 3.8293 | 3.8382 | 3.8343 | 3.8213 | 3.8409 | 3.8422 | 3.8433 | 3.8336 | 3.8282 | 3.8756 | 3.8735 | 3.856 | 3.8731 | 3.8784 | 3.8715 | 3.8344 | 3.8415 | 3.8397 | 3.8255 | 3.8266 | 3.8332 | 3.8361 | 3.8331 | 3.8404 | 3.6831 | 3.6728 | 3.6675 | 3.6826 | 3.6794 | 3.6735 | 3.6803 | 3.5481 | 3.5496 | 3.5505 | 3.5514 | 3.5526 | 3.5538 | 3.5599 | 3.5616 | 3.3022 | 3.2934 | 3.2919 | 3.5812 | 3.5881 | 3.5827 | 3.5863 | 3.5838 | 3.5866 | 3.3081 | 3.3152 | 3.3094 | 3.6831 | 3.6812 | 3.6711 | 3.6819 | 3.682 | 3.678 | 3.8382 | 3.8405 | 3.8411 | 3.8554 | 3.8625 | 3.8756 | 3.8783 | 3.8683 | 3.6928 | 3.688 | 3.6981 | 3.8405 | 3.8409 | 3.8385 | 3.8478 | 3.8444 | 3.849 | 3.8462 | 3.6404 | 3.6361 | 3.6467 | 3.8491 | 3.8824 | 3.8803 | 3.881 | 3.5336 | 3.5451 | 3.5526 | 3.5419 | 3.5812 | 3.5953 | 3.5991 | 3.5806 | 3.5825 | 3.6027 | 3.5932 | 3.5989 | 3.5887 | 3.5867 | 3.5919 | 3.598 | 3.5949 | 3.5978 | 3.3181 | 3.3226 | 3.3133 | 3.6081 | 3.5952 | 3.6013 | 3.5956 | 3.5958 | 3.599 | 3.5679 | 3.5541 | 3.567 | 3.8387 | 3.8398 | 3.8213 | 3.319 | 3.3222 | 3.3213 | 3.6086 | 3.599 | 3.598 | 3.5944 | 3.6047 | 3.6118 | 3.5723 | 3.5622 | 3.5611 | 3.832 | 3.8366 | 3.8303 | 3.837 | 3.8328 | 3.8283 | 3.8341 | 3.8272 | 3.8319 | 3.859 | 3.8605 | 3.8767 | 3.8528 | 3.8544 | 3.8517 | 3.6691 | 3.6747 | 3.6724 | 3.6921 | 3.6929 | 3.694 | 3.3126 | 3.306 | 3.3061 | 3.5963 | 3.5948 | 3.5821 | 3.5941 | 3.5918 | 3.5857 | 3.576 | 3.5635 | 3.5706 | 3.8283 | 3.8228 | 3.8324 | 3.5924 | 3.5943 | 3.5849 | 3.5937 | 3.6008 | 3.5953 | 3.8394 | 3.8303 | 3.8295 | 3.8425 | 3.8422 | 3.8425 | 3.8657 | 3.7945 | 3.7929 | 3.8127 | 3.8081 | 3.7995 | 3.8363 | 3.8331 | 3.8218 | 3.8187 | 3.8099 | 3.8116 | 3.6791 | 3.6785 | 3.6759 | 3.6959 | 3.6868 | 3.681 | 3.3031 | 3.3109 | 3.3146 | 3.3188 | 3.3176 | 3.3065 | 3.6044 | 3.5972 | 3.6006 | 3.5975 | 3.5878 | 3.6015 | 3.5933 | 3.5857 | 3.5894 | 3.5851 | 3.5889 | 3.5852 | 3.562 | 3.5474 | 3.5582 | 3.84 | 3.8297 | 3.8356 | 3.8454 | 3.8408 | 3.8402
91 | Suction orifice plate DP | mb | 79.8628 | 79.2624 | 79.6515 | 89.5666 | 89.0704 | 88.9981 | 31.0156 | 30.5822 | 30.9036 | 22.9183 | 22.818 | 23.0146 | 23.1846 | 23.0049 | 22.6776 | 1.6981 | 1.6955 | 1.8036 | 2.7025 | 2.6085 | 2.7387 | 23.3978 | 23.4844 | 23.4356 | 27.7894 | 27.7675 | 28.393 | 28.2084 | 27.9007 | 28.0143 | 81.7623 | 82.0445 | 81.8173 | 91.2603 | 89.7492 | 89.8254 | 86.746 | 179.0383 | 179.583 | 179.664 | 180.9687 | 179.2053 | 179.6663 | 179.2186 | 180.6522 | 191.7625 | 191.5935 | 191.1097 | 209.5718 | 209.675 | 211.0695 | 210.5388 | 210.2152 | 211.497 | 183.9637 | 184.935 | 184.1161 | 74.1054 | 74.3359 | 74.2546 | 75.61 | 75.6386 | 76.1941 | 21.5537 | 21.3326 | 21.1526 | 1.2244 | 1.4253 | 1.3989 | 1.7453 | 2.0865 | 86.2212 | 85.4827 | 85.6452 | 25.9342 | 26.4164 | 26.4108 | 26.4385 | 29.8578 | 29.7686 | 29.6787 | 27.3374 | 27.1385 | 27.5139 | 1.9117 | 1.8941 | 1.8606 | 1.8466 | 170.3776 | 171.9033 | 171.0744 | 171.6025 | 201.3058 | 202.6124 | 201.8391 | 200.2897 | 200.9652 | 201.5061 | 200.7868 | 201.8515 | 200.0367 | 200.6286 | 199.9383 | 201.6509 | 200.2157 | 201.3455 | 192.5661 | 192.1864 | 192.6156 | 214.0819 | 211.4244 | 211.8216 | 210.7527 | 211.1096 | 210.1364 | 179.8359 | 178.9393 | 181.5336 | 30.5956 | 30.5311 | 30.928 | 194.3187 | 194.8563 | 195.2655 | 215.2247 | 213.4955 | 214.481 | 213.8325 | 213.2737 | 213.851 | 182.0441 | 180.9149 | 180.9762 | 31.2741 | 31.0827 | 31.643 | 28.2064 | 27.6692 | 27.5663 | 23.5541 | 22.9075 | 23.2396 | 1.2654 | 1.2836 | 1.55 | 1.8736 | 2.0917 | 2.1546 | 82.7042 | 82.1155 | 81.4888 | 91.9118 | 92.3175 | 91.9847 | 194.9318 | 195.6006 | 196.4679 | 215.1084 | 216.1721 | 214.3456 | 214.4257 | 215.2081 | 214.3566 | 181.221 | 180.1475 | 181.7608 | 31.3086 | 30.9101 | 31.3611 | 213.419 | 212.7942 | 211.3186 | 212.3947 | 212.4331 | 212.7782 | 32.2349 | 31.8279 | 31.9432 | 2.0602 | 1.9208 | 1.9973 | 1.3927 | 1.2309 | 1.3608 | 1.9755 | 2.0032 | 1.9889 | 28.2178 | 27.7539 | 27.8916 | 23.4057 | 23.4288 | 23.137 | 81.4709 | 81.3406 | 79.1175 | 93.3887 | 93.1454 | 93.0689 | 197.4326 | 196.828 | 198.3573 | 198.6575 | 199.7505 | 198.4621 | 219.37 | 217.7167 | 217.2703 | 216.7777 | 216.7868 | 216.2337 | 217.453 | 216.0191 | 215.7277 | 216.4072 | 216.7406 | 215.8726 | 184.3014 | 184.1275 | 185.1108 | 31.7654 | 31.8817 | 32.1359 | 32.0572 | 31.9048 | 31.9735
92 | Suction orifice plate SH | ºC | 8.7993 | 9.1227 | 9.0304 | 11.0206 | 10.9916 | 10.9651 | 12.6415 | 12.4912 | 12.3824 | 11.4933 | 11.248 | 11.0599 | 10.8209 | 10.8126 | 10.8589 | 9.1229 | 9.0327 | 8.876 | 10.9984 | 10.4883 | 10.4394 | 9.7108 | 9.2029 | 9.067 | 8.5808 | 8.5581 | 8.5217 | 8.6141 | 8.5291 | 8.4427 | 10.6626 | 10.5991 | 10.4369 | 10.0699 | 9.9087 | 9.6951 | 10.4274 | 8.895 | 8.8723 | 8.8446 | 8.9246 | 8.9396 | 8.9878 | 9.1122 | 9.4598 | 8.7494 | 9.2006 | 8.3457 | 8.7809 | 8.7316 | 8.7455 | 9.4754 | 9.2736 | 9.0425 | 7.6547 | 7.7048 | 7.867 | 10.4654 | 10.3063 | 10.4112 | 10.7394 | 10.7469 | 10.7793 | 10.6009 | 10.9907 | 11.4071 | 10.5332 | 10.5271 | 10.4612 | 9.911 | 9.8649 | 8.685 | 8.5785 | 8.0168 | 9.2194 | 9.1392 | 9.0321 | 8.5834 | 9.0915 | 9.0901 | 9.2038 | 10.6528 | 10.7057 | 10.6792 | 9.8285 | 10.5008 | 10.5674 | 10.2991 | 8.3637 | 8.6173 | 8.9133 | 9.0584 | 7.8612 | 8.8909 | 9.1837 | 13.2253 | 13.6814 | 13.0551 | 15.9072 | 15.8482 | 15.8789 | 15.8579 | 15.7281 | 15.6197 | 15.6115 | 15.5306 | 8.6525 | 8.9106 | 8.964 | 7.7099 | 7.9897 | 8.7315 | 9.6773 | 9.8923 | 10.1241 | 7.6148 | 8.4072 | 7.7153 | 9.9174 | 9.7539 | 10.0362 | 7.9265 | 7.7237 | 7.5027 | 7.6957 | 7.4699 | 7.061 | 8.9635 | 8.5619 | 8.6561 | 7.7131 | 7.9784 | 7.9811 | 9.0605 | 9.0523 | 8.7932 | 10.6112 | 10.8724 | 11.7028 | 11.4721 | 11.0638 | 10.6505 | 10.0043 | 10.1685 | 10.176 | 10.3109 | 9.985 | 9.908 | 9.1033 | 9.0364 | 8.9942 | 9.7604 | 9.5543 | 9.0946 | 9.1546 | 8.0354 | 6.6767 | 7.4415 | 7.2475 | 7.3526 | 7.3824 | 7.1187 | 7.2273 | 9.241 | 10.5576 | 9.7032 | 11.1395 | 10.9949 | 10.7469 | 9.4973 | 9.4253 | 9.6932 | 9.7859 | 9.7182 | 8.9039 | 9.597 | 9.7111 | 9.6342 | 10.2317 | 10.0304 | 9.9692 | 9.7398 | 10.3951 | 10.5633 | 10.439 | 10.5639 | 10.8415 | 9.8142 | 9.8346 | 10.1739 | 9.3352 | 9.5713 | 9.5685 | 9.718 | 9.664 | 9.8736 | 10.0888 | 9.9099 | 9.8269 | 8.4578 | 8.3868 | 8.2596 | 8.1115 | 7.8249 | 7.5391 | 8.1207 | 8.0313 | 8.2897 | 7.9836 | 8.0994 | 8.1643 | 8.2183 | 8.1884 | 7.8976 | 8.1048 | 8.1433 | 8.1425 | 8.8061 | 8.692 | 8.5209 | 9.9241 | 10.1005 | 10.0562 | 9.9357 | 10.0878 | 10.295
93 | Suction orifice plate gauge | ºC | 6.446 | 6.3556 | 6.4041 | 6.5401 | 6.5294 | 6.4625 | 7.6427 | 7.7105 | 7.6806 | 7.5808 | 7.7313 | 7.7414 | 7.7497 | 7.6757 | 7.6341 | 7.996 | 7.9798 | 7.8468 | 7.9775 | 8.0173 | 7.9648 | 7.6814 | 7.7363 | 7.7225 | 7.6135 | 7.6221 | 7.672 | 7.6946 | 7.6716 | 7.7277 | 6.504 | 6.4226 | 6.3804 | 6.5001 | 6.4745 | 6.4281 | 6.4819 | 5.4213 | 5.4333 | 5.441 | 5.4486 | 5.4581 | 5.4676 | 5.5175 | 5.5307 | 3.3654 | 3.2904 | 3.2768 | 5.6898 | 5.7451 | 5.7014 | 5.7307 | 5.7109 | 5.7333 | 3.4163 | 3.4777 | 3.4279 | 6.5035 | 6.4886 | 6.4088 | 6.4943 | 6.4948 | 6.4636 | 7.7104 | 7.7284 | 7.7328 | 7.8422 | 7.8967 | 7.9963 | 8.017 | 7.9404 | 6.5807 | 6.5428 | 6.6224 | 7.7281 | 7.7316 | 7.7133 | 7.7838 | 7.7579 | 7.793 | 7.7718 | 6.1652 | 6.1302 | 6.2148 | 7.7939 | 8.0478 | 8.032 | 8.0369 | 5.3034 | 5.3969 | 5.4578 | 5.3706 | 5.6896 | 5.8032 | 5.8339 | 5.6846 | 5.7001 | 5.8633 | 5.7864 | 5.8322 | 5.7505 | 5.7345 | 5.7761 | 5.8253 | 5.8002 | 5.8231 | 3.5026 | 3.5408 | 3.4611 | 5.9061 | 5.8027 | 5.852 | 5.806 | 5.8072 | 5.8329 | 5.5818 | 5.4702 | 5.5749 | 7.7145 | 7.7231 | 7.5807 | 3.5101 | 3.537 | 3.5292 | 5.91 | 5.8333 | 5.8249 | 5.7961 | 5.8788 | 5.9358 | 5.6176 | 5.5361 | 5.5267 | 7.6633 | 7.6985 | 7.6504 | 7.7017 | 7.6697 | 7.6347 | 7.6791 | 7.6261 | 7.6628 | 7.8695 | 7.8813 | 8.0045 | 7.8225 | 7.8349 | 7.8137 | 6.3929 | 6.4374 | 6.4195 | 6.5751 | 6.5815 | 6.5901 | 3.4554 | 3.3986 | 3.3992 | 5.8117 | 5.7991 | 5.6967 | 5.7934 | 5.7752 | 5.7263 | 5.6475 | 5.5463 | 5.6038 | 7.6344 | 7.5927 | 7.6663 | 5.7797 | 5.7952 | 5.7197 | 5.7905 | 5.8473 | 5.8038 | 7.72 | 7.6503 | 7.6444 | 7.7434 | 7.741 | 7.7439 | 7.9209 | 7.3744 | 7.3621 | 7.5148 | 7.4795 | 7.4133 | 7.6964 | 7.6714 | 7.5849 | 7.561 | 7.493 | 7.5068 | 6.472 | 6.4674 | 6.4472 | 6.6048 | 6.5328 | 6.4873 | 3.3739 | 3.4402 | 3.4719 | 3.5083 | 3.4981 | 3.4031 | 5.8764 | 5.8186 | 5.8464 | 5.8215 | 5.7431 | 5.8534 | 5.7872 | 5.726 | 5.7555 | 5.7214 | 5.7522 | 5.7224 | 5.5339 | 5.4156 | 5.5031 | 7.7247 | 7.6457 | 7.6908 | 7.7659 | 7.7308 | 7.7263
94 | Suction orifice plate enthalpy | KJ/kg | 410.4079 | 410.6484 | 410.5937 | 412.4947 | 412.4617 | 412.3962 | 414.66 | 414.5643 | 414.4459 | 413.5689 | 413.4365 | 413.2702 | 413.0558 | 413.0028 | 413.0198 | 411.6452 | 411.5524 | 411.3277 | 413.3586 | 412.9141 | 412.8371 | 411.9947 | 411.5613 | 411.4281 | 410.9152 | 410.8996 | 410.8962 | 410.9948 | 410.9028 | 410.8572 | 412.1456 | 412.0376 | 411.8635 | 411.602 | 411.439 | 411.2156 | 411.9173 | 409.8711 | 409.8578 | 409.8373 | 409.9148 | 409.9342 | 409.9839 | 410.1275 | 410.4518 | 408.4809 | 408.8414 | 408.0627 | 409.931 | 409.9198 | 409.9059 | 410.5885 | 410.3926 | 410.1959 | 407.5248 | 407.6074 | 407.7233 | 411.9652 | 411.8108 | 411.8576 | 412.2097 | 412.217 | 412.2273 | 412.8298 | 413.1986 | 413.5836 | 412.8483 | 412.876 | 412.8764 | 412.3831 | 412.294 | 410.3852 | 410.2648 | 409.799 | 411.5715 | 411.5 | 411.3904 | 411.0204 | 411.472 | 411.492 | 411.5837 | 411.9281 | 411.9548 | 411.9827 | 412.1713 | 412.9442 | 412.9958 | 412.7521 | 409.316 | 409.6036 | 409.9101 | 409.9888 | 409.0928 | 410.1004 | 410.3859 | 413.9709 | 414.3951 | 413.9281 | 416.4725 | 416.4481 | 416.4239 | 416.3946 | 416.3032 | 416.236 | 416.2125 | 416.1536 | 408.4777 | 408.7339 | 408.7331 | 409.0857 | 409.2784 | 409.9848 | 410.8185 | 411.015 | 411.2419 | 408.803 | 409.4571 | 408.8904 | 412.2046 | 412.0597 | 412.2321 | 407.8272 | 407.6605 | 407.4563 | 409.0751 | 408.8228 | 408.4444 | 410.1622 | 409.8464 | 409.967 | 408.9143 | 409.1066 | 409.1033 | 411.3862 | 411.4 | 411.1327 | 412.8339 | 413.054 | 413.7943 | 413.6101 | 413.2029 | 412.8462 | 412.379 | 412.5371 | 412.6191 | 412.6321 | 412.3401 | 412.2564 | 410.6535 | 410.6195 | 410.5699 | 411.3651 | 411.1806 | 410.7655 | 408.9015 | 407.8574 | 406.6315 | 408.7838 | 408.5991 | 408.6333 | 408.7188 | 408.4672 | 408.5368 | 410.3242 | 411.4599 | 410.7181 | 413.2774 | 413.1191 | 412.9368 | 410.6384 | 410.5824 | 410.7801 | 410.9079 | 410.8811 | 410.1125 | 411.9136 | 411.976 | 411.9017 | 412.5109 | 412.3246 | 412.2701 | 412.1671 | 412.4351 | 412.5818 | 412.5614 | 412.6543 | 412.8683 | 412.0988 | 412.1023 | 412.361 | 411.5764 | 411.7519 | 411.7577 | 411.2633 | 411.2112 | 411.3902 | 411.6834 | 411.4758 | 411.3722 | 408.2232 | 408.1998 | 408.1045 | 407.9931 | 407.7282 | 407.4123 | 409.4426 | 409.326 | 409.5785 | 409.2842 | 409.3424 | 409.4684 | 409.4775 | 409.4132 | 409.1659 | 409.3341 | 409.3879 | 409.3691 | 409.8589 | 409.683 | 409.5806 | 412.217 | 412.3308 | 412.3176 | 412.2528 | 412.3711 | 412.5586
95 | Suction orifice plate specific Vol | m3/kg | 0.058182 | 0.058449 | 0.058329 | 0.05863 | 0.058643 | 0.058766 | 0.056977 | 0.056809 | 0.056835 | 0.05678 | 0.056433 | 0.056363 | 0.056282 | 0.056417 | 0.056507 | 0.055367 | 0.055372 | 0.055571 | 0.055911 | 0.0557 | 0.055782 | 0.056104 | 0.055864 | 0.055851 | 0.055918 | 0.055896 | 0.055794 | 0.055778 | 0.055797 | 0.05567 | 0.058599 | 0.05874 | 0.058776 | 0.058439 | 0.058443 | 0.058472 | 0.058576 | 0.060231 | 0.0602 | 0.060176 | 0.060184 | 0.06017 | 0.060165 | 0.060101 | 0.060176 | 0.064503 | 0.064808 | 0.06457 | 0.05966 | 0.059535 | 0.059626 | 0.059781 | 0.059761 | 0.059649 | 0.064049 | 0.063931 | 0.06409 | 0.058544 | 0.058528 | 0.058713 | 0.05864 | 0.058641 | 0.058711 | 0.056295 | 0.056368 | 0.056473 | 0.056033 | 0.055931 | 0.055731 | 0.055543 | 0.055671 | 0.05789 | 0.057932 | 0.057619 | 0.055883 | 0.055855 | 0.055859 | 0.055606 | 0.055793 | 0.055728 | 0.055799 | 0.059259 | 0.059343 | 0.059169 | 0.055929 | 0.055647 | 0.055694 | 0.055612 | 0.060312 | 0.060198 | 0.060163 | 0.060381 | 0.059391 | 0.059466 | 0.059491 | 0.060956 | 0.061055 | 0.060546 | 0.061512 | 0.061402 | 0.061578 | 0.061604 | 0.061482 | 0.061351 | 0.0614 | 0.061331 | 0.064173 | 0.06417 | 0.06436 | 0.058919 | 0.059205 | 0.059323 | 0.059689 | 0.059749 | 0.059765 | 0.059532 | 0.059989 | 0.059576 | 0.0561 | 0.056039 | 0.05638 | 0.06393 | 0.063809 | 0.063756 | 0.058907 | 0.058992 | 0.058889 | 0.059501 | 0.059221 | 0.059136 | 0.05949 | 0.059731 | 0.05975 | 0.055959 | 0.055892 | 0.055909 | 0.056314 | 0.056444 | 0.056736 | 0.056591 | 0.056578 | 0.056396 | 0.055839 | 0.055862 | 0.055638 | 0.056009 | 0.055897 | 0.055915 | 0.058372 | 0.058266 | 0.058289 | 0.058206 | 0.058135 | 0.057988 | 0.064432 | 0.064207 | 0.063778 | 0.059026 | 0.058994 | 0.059227 | 0.059045 | 0.059003 | 0.059132 | 0.059878 | 0.060465 | 0.060101 | 0.056583 | 0.056621 | 0.056416 | 0.059689 | 0.059638 | 0.059866 | 0.059752 | 0.059619 | 0.059469 | 0.056002 | 0.056162 | 0.056152 | 0.056133 | 0.056082 | 0.05606 | 0.055672 | 0.056864 | 0.056933 | 0.056614 | 0.056714 | 0.056914 | 0.056105 | 0.056157 | 0.05641 | 0.056224 | 0.056415 | 0.056388 | 0.058394 | 0.058387 | 0.058486 | 0.058242 | 0.05833 | 0.058395 | 0.064393 | 0.064226 | 0.064117 | 0.063992 | 0.063925 | 0.064041 | 0.059097 | 0.059185 | 0.059206 | 0.059166 | 0.059354 | 0.059155 | 0.059302 | 0.059414 | 0.059271 | 0.059399 | 0.059349 | 0.059408 | 0.059978 | 0.060182 | 0.059956 | 0.056083 | 0.056277 | 0.056182 | 0.05601 | 0.056117 | 0.056182
96 | Suction orifice Plate pipe dia | m | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15
97 | Suction orifice plate orifice dia | m | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
98 | Suction orifice plate Gamma (cp/cv) | - | 1.1721 | 1.1714 | 1.1717 | 1.1686 | 1.1687 | 1.1686 | 1.1675 | 1.1678 | 1.168 | 1.1692 | 1.1698 | 1.1701 | 1.1705 | 1.1704 | 1.1703 | 1.1737 | 1.1738 | 1.1739 | 1.1705 | 1.1714 | 1.1714 | 1.1722 | 1.1732 | 1.1734 | 1.1741 | 1.1741 | 1.1742 | 1.1741 | 1.1742 | 1.1745 | 1.1692 | 1.1692 | 1.1694 | 1.1701 | 1.1703 | 1.1706 | 1.1695 | 1.1706 | 1.1707 | 1.1707 | 1.1706 | 1.1706 | 1.1705 | 1.1704 | 1.1698 | 1.1683 | 1.1675 | 1.1688 | 1.1711 | 1.1713 | 1.1712 | 1.1701 | 1.1704 | 1.1708 | 1.1701 | 1.1701 | 1.1697 | 1.1695 | 1.1697 | 1.1694 | 1.169 | 1.169 | 1.1689 | 1.1708 | 1.1702 | 1.1696 | 1.1711 | 1.1712 | 1.1714 | 1.1723 | 1.1723 | 1.1725 | 1.1726 | 1.1737 | 1.1731 | 1.1733 | 1.1734 | 1.1743 | 1.1734 | 1.1734 | 1.1732 | 1.1687 | 1.1686 | 1.1688 | 1.1722 | 1.1714 | 1.1713 | 1.1717 | 1.1713 | 1.171 | 1.1706 | 1.1703 | 1.1727 | 1.1711 | 1.1707 | 1.1643 | 1.1637 | 1.1648 | 1.1608 | 1.1609 | 1.1608 | 1.1608 | 1.161 | 1.1612 | 1.1612 | 1.1613 | 1.1686 | 1.1682 | 1.168 | 1.1732 | 1.1726 | 1.1714 | 1.1698 | 1.1695 | 1.1692 | 1.1729 | 1.1715 | 1.1728 | 1.1719 | 1.1722 | 1.1716 | 1.1697 | 1.1701 | 1.1704 | 1.1732 | 1.1735 | 1.1742 | 1.171 | 1.1717 | 1.1717 | 1.1728 | 1.1723 | 1.1722 | 1.1733 | 1.1734 | 1.1737 | 1.1708 | 1.1703 | 1.169 | 1.1694 | 1.17 | 1.1707 | 1.172 | 1.1717 | 1.1719 | 1.1714 | 1.172 | 1.1721 | 1.1715 | 1.1717 | 1.1717 | 1.1707 | 1.171 | 1.1718 | 1.1677 | 1.1694 | 1.1716 | 1.1736 | 1.1739 | 1.1735 | 1.1736 | 1.1741 | 1.1738 | 1.1703 | 1.1681 | 1.1695 | 1.1698 | 1.17 | 1.1705 | 1.1701 | 1.1702 | 1.1697 | 1.1696 | 1.1698 | 1.1711 | 1.1725 | 1.1722 | 1.1723 | 1.1715 | 1.1718 | 1.1719 | 1.1725 | 1.1707 | 1.1704 | 1.1708 | 1.1706 | 1.17 | 1.1721 | 1.172 | 1.1713 | 1.1727 | 1.1722 | 1.1722 | 1.1706 | 1.1707 | 1.1703 | 1.1702 | 1.1704 | 1.1705 | 1.1687 | 1.1689 | 1.1692 | 1.1694 | 1.1699 | 1.1702 | 1.1725 | 1.1726 | 1.1722 | 1.1726 | 1.1723 | 1.1724 | 1.1722 | 1.1722 | 1.1727 | 1.1723 | 1.1723 | 1.1722 | 1.1709 | 1.1709 | 1.1713 | 1.1719 | 1.1715 | 1.1717 | 1.172 | 1.1717 | 1.1713
99 | Suction flow Viscosity | N.S/m^2 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05
100 | Suction orifice plate vol Flow | m^3/hr | 574.6581 | 573.8309 | 574.6278 | 610.2265 | 608.6315 | 609.0118 | 356.5127 | 353.5141 | 355.4337 | 306.2441 | 304.6454 | 305.7578 | 306.6587 | 305.8389 | 303.9101 | 82.7 | 82.6404 | 85.3794 | 104.7675 | 102.7379 | 105.3421 | 307.5694 | 307.4741 | 307.1227 | 334.4468 | 334.2507 | 337.661 | 336.5219 | 334.7497 | 335.0466 | 583.4045 | 585.0762 | 584.454 | 614.8399 | 609.8518 | 610.249 | 600.4497 | 864.8436 | 865.8893 | 865.9116 | 868.9769 | 864.8152 | 865.8486 | 864.3862 | 868.2314 | 923.2561 | 924.9799 | 922.1822 | 928.0772 | 927.373 | 930.9723 | 931.064 | 930.2241 | 932.0654 | 902.0713 | 903.5524 | 902.7213 | 555.6527 | 556.4233 | 556.9882 | 561.6205 | 561.7302 | 564.0836 | 295.7721 | 294.4516 | 293.487 | 70.6845 | 76.1736 | 75.3322 | 83.9721 | 91.8938 | 595.1832 | 592.89 | 591.8571 | 323.0684 | 325.9548 | 325.9324 | 325.3652 | 346.1992 | 345.4859 | 345.1844 | 341.4572 | 340.4612 | 342.2907 | 88.176 | 87.549 | 86.8096 | 86.4196 | 845.0474 | 847.9179 | 845.7364 | 848.468 | 908.4517 | 911.8905 | 910.4331 | 917.9765 | 920.1983 | 917.6681 | 923.2576 | 924.7921 | 922.0772 | 923.5643 | 921.1725 | 923.9756 | 921.1849 | 923.1526 | 922.8406 | 921.9794 | 924.2571 | 931.8863 | 928.5217 | 930.2994 | 930.8562 | 932.067 | 930.161 | 861.7824 | 862.9204 | 865.9745 | 351.3784 | 350.8211 | 354.1444 | 925.0953 | 925.457 | 926.0001 | 934.155 | 931.198 | 932.4256 | 935.8318 | 932.5448 | 933.1161 | 866.543 | 865.652 | 865.9273 | 354.7752 | 353.4854 | 356.6854 | 338.1214 | 335.2959 | 335.5387 | 309.9227 | 305.6289 | 307.3303 | 71.7296 | 72.2577 | 79.2161 | 87.3579 | 92.1952 | 93.5806 | 585.5386 | 582.9728 | 580.896 | 615.7726 | 616.7291 | 614.8665 | 930.0312 | 929.8977 | 928.7812 | 934.7856 | 936.7192 | 934.7056 | 933.5116 | 934.7915 | 934.0054 | 867.4639 | 869.1334 | 870.2708 | 356.9411 | 354.7977 | 356.7125 | 936.4167 | 934.7231 | 933.3509 | 934.7667 | 933.8577 | 933.3913 | 360.2824 | 358.5263 | 359.1372 | 91.6921 | 88.5063 | 90.2285 | 75.1264 | 71.3966 | 75.1026 | 90.179 | 90.8871 | 90.7226 | 337.5627 | 334.9491 | 336.5274 | 307.9444 | 308.6178 | 306.6306 | 581.3597 | 580.8714 | 573.5064 | 620.7887 | 620.4534 | 620.5374 | 935.3425 | 932.8283 | 935.4993 | 935.2917 | 937.2363 | 935.1426 | 944.127 | 941.3987 | 940.6613 | 939.3189 | 940.7657 | 938.1384 | 941.7523 | 939.6399 | 937.9373 | 940.3184 | 940.6364 | 939.2873 | 875.1515 | 876.1673 | 876.8129 | 357.9283 | 359.1949 | 360.309 | 359.3231 | 358.8135 | 359.4043
101 | Suction orifice plate mass Flow | kg/s | 2.7436 | 2.7271 | 2.7365 | 2.8911 | 2.8829 | 2.8787 | 1.7381 | 1.7286 | 1.7371 | 1.4982 | 1.4996 | 1.5069 | 1.5135 | 1.5058 | 1.494 | 0.41491 | 0.41457 | 0.42678 | 0.52051 | 0.51236 | 0.52457 | 1.5228 | 1.5289 | 1.5275 | 1.6614 | 1.6611 | 1.6811 | 1.6759 | 1.6665 | 1.6718 | 2.7655 | 2.7668 | 2.7622 | 2.9225 | 2.8986 | 2.8991 | 2.8475 | 3.9886 | 3.9954 | 3.9971 | 4.0107 | 3.9925 | 3.9976 | 3.9951 | 4.0078 | 3.976 | 3.9646 | 3.9672 | 4.3212 | 4.3269 | 4.3371 | 4.3263 | 4.3238 | 4.3405 | 3.9123 | 3.9259 | 3.9126 | 2.6364 | 2.6408 | 2.6352 | 2.6604 | 2.6609 | 2.6688 | 1.4594 | 1.451 | 1.4436 | 0.35041 | 0.37831 | 0.37548 | 0.41995 | 0.45852 | 2.8559 | 2.8428 | 2.8533 | 1.6059 | 1.621 | 1.6208 | 1.6254 | 1.7236 | 1.7221 | 1.7184 | 1.6006 | 1.5937 | 1.6069 | 0.43793 | 0.43702 | 0.43297 | 0.43166 | 3.892 | 3.9126 | 3.9049 | 3.9033 | 4.2489 | 4.2596 | 4.2511 | 4.1833 | 4.1866 | 4.2102 | 4.1693 | 4.1837 | 4.1595 | 4.1644 | 4.1619 | 4.1834 | 4.1675 | 4.1811 | 3.9946 | 3.991 | 3.9891 | 4.3934 | 4.3565 | 4.3561 | 4.332 | 4.3332 | 4.3232 | 4.0211 | 3.9957 | 4.0377 | 1.7398 | 1.739 | 1.7448 | 4.0196 | 4.0288 | 4.0345 | 4.405 | 4.3848 | 4.3982 | 4.3689 | 4.3741 | 4.3831 | 4.0462 | 4.0257 | 4.0257 | 1.7611 | 1.7568 | 1.7722 | 1.6678 | 1.6501 | 1.6428 | 1.5213 | 1.5005 | 1.5137 | 0.35683 | 0.35931 | 0.39549 | 0.43326 | 0.45816 | 0.4649 | 2.7865 | 2.7793 | 2.7683 | 2.9387 | 2.9468 | 2.9454 | 4.0095 | 4.023 | 4.0452 | 4.3991 | 4.4106 | 4.3838 | 4.3917 | 4.4008 | 4.3876 | 4.0242 | 3.9928 | 4.0223 | 1.7523 | 1.7406 | 1.7564 | 4.3578 | 4.3537 | 4.3307 | 4.3456 | 4.351 | 4.3598 | 1.7871 | 1.7733 | 1.7766 | 0.45375 | 0.43838 | 0.44708 | 0.37485 | 0.34877 | 0.36643 | 0.44247 | 0.44515 | 0.44279 | 1.6713 | 1.6568 | 1.6571 | 1.5214 | 1.5196 | 1.5105 | 2.7655 | 2.7635 | 2.7239 | 2.9608 | 2.9547 | 2.9518 | 4.0349 | 4.0345 | 4.0529 | 4.0599 | 4.0727 | 4.0562 | 4.4377 | 4.4183 | 4.4133 | 4.41 | 4.4028 | 4.4053 | 4.4113 | 4.3931 | 4.3957 | 4.3974 | 4.4025 | 4.3919 | 4.0531 | 4.044 | 4.0623 | 1.7728 | 1.7729 | 1.7815 | 1.782 | 1.7761 | 1.777
102
103
104 | Suction Temp | ºC | 15.2453 | 15.4783 | 15.4345 | 17.5607 | 17.521 | 17.4276 | 20.2842 | 20.2017 | 20.063 | 19.0741 | 18.9792 | 18.8013 | 18.5706 | 18.4883 | 18.493 | 17.1189 | 17.0125 | 16.7228 | 18.9759 | 18.5056 | 18.4042 | 17.3922 | 16.9391 | 16.7895 | 16.1943 | 16.1802 | 16.1937 | 16.3087 | 16.2008 | 16.1704 | 17.1666 | 17.0217 | 16.8172 | 16.5701 | 16.3831 | 16.1233 | 16.9093 | 14.3163 | 14.3056 | 14.2855 | 14.3732 | 14.3977 | 14.4554 | 14.6297 | 14.9905 | 12.1148 | 12.491 | 11.6225 | 14.4707 | 14.4767 | 14.447 | 15.2061 | 14.9845 | 14.7759 | 11.0711 | 11.1825 | 11.2949 | 16.9689 | 16.7949 | 16.82 | 17.2337 | 17.2418 | 17.2429 | 18.3113 | 18.719 | 19.14 | 18.3754 | 18.4238 | 18.4575 | 17.928 | 17.8053 | 15.2657 | 15.1213 | 14.6392 | 16.9474 | 16.8708 | 16.7454 | 16.3672 | 16.8494 | 16.8831 | 16.9756 | 16.818 | 16.8359 | 16.894 | 17.6224 | 18.5485 | 18.5994 | 18.336 | 13.6671 | 14.0142 | 14.3711 | 14.4289 | 13.5508 | 14.6941 | 15.0175 | 18.91 | 19.3815 | 18.9184 | 21.6936 | 21.6804 | 21.6293 | 21.5924 | 21.5042 | 21.445 | 21.4117 | 21.3538 | 12.1552 | 12.4514 | 12.4251 | 13.616 | 13.7924 | 14.5835 | 15.4833 | 15.6995 | 15.957 | 13.1966 | 13.8774 | 13.2902 | 17.6319 | 17.477 | 17.6169 | 11.4366 | 11.2606 | 11.0319 | 13.6057 | 13.3032 | 12.8859 | 14.7596 | 14.4407 | 14.5919 | 13.3308 | 13.5145 | 13.5078 | 16.7238 | 16.7508 | 16.4436 | 18.3129 | 18.5421 | 19.3375 | 19.1512 | 18.6899 | 18.3133 | 17.8738 | 18.0498 | 18.1805 | 18.1335 | 17.8199 | 17.7217 | 15.4962 | 15.4738 | 15.4137 | 16.3355 | 16.1358 | 15.6846 | 12.61 | 11.434 | 10.0759 | 13.2532 | 13.0466 | 13.0493 | 13.1758 | 12.8939 | 12.9535 | 14.8885 | 16.1038 | 15.307 | 18.7739 | 18.5876 | 18.4132 | 15.277 | 15.2205 | 15.4129 | 15.5764 | 15.5655 | 14.7076 | 17.317 | 17.3614 | 17.2785 | 17.975 | 17.7715 | 17.7131 | 17.6607 | 17.7695 | 17.9254 | 17.9538 | 18.0434 | 18.2548 | 17.5106 | 17.506 | 17.7587 | 16.8961 | 17.0643 | 17.0753 | 16.19 | 16.1314 | 16.3208 | 16.6937 | 16.4427 | 16.3142 | 11.8317 | 11.827 | 11.7316 | 11.6198 | 11.323 | 10.9422 | 13.9971 | 13.8499 | 14.136 | 13.8051 | 13.8426 | 14.0177 | 14.0055 | 13.9145 | 13.6531 | 13.8262 | 13.8955 | 13.8649 | 14.34 | 14.1076 | 14.024 | 17.6488 | 17.7462 | 17.7469 | 17.7016 | 17.8186 | 18.0213
105 | Suction Pressure | BarA | 3.5968 | 3.5873 | 3.5884 | 3.6017 | 3.5943 | 3.5891 | 3.7889 | 3.7995 | 3.794 | 3.7862 | 3.8072 | 3.807 | 3.811 | 3.7996 | 3.7987 | 3.8575 | 3.8547 | 3.8411 | 3.8506 | 3.8567 | 3.8494 | 3.799 | 3.8079 | 3.8029 | 3.7896 | 3.7916 | 3.8008 | 3.7998 | 3.7963 | 3.8064 | 3.6017 | 3.5936 | 3.5869 | 3.5897 | 3.5944 | 3.587 | 3.594 | 3.3789 | 3.3815 | 3.3771 | 3.3791 | 3.3818 | 3.3835 | 3.3868 | 3.3888 | 3.1203 | 3.1137 | 3.1083 | 3.3788 | 3.3818 | 3.3794 | 3.38 | 3.378 | 3.3809 | 3.1144 | 3.1155 | 3.1128 | 3.5974 | 3.5923 | 3.5883 | 3.5973 | 3.5935 | 3.5906 | 3.8027 | 3.8042 | 3.8035 | 3.8404 | 3.8418 | 3.8577 | 3.8611 | 3.8468 | 3.5918 | 3.5918 | 3.5974 | 3.7965 | 3.8012 | 3.7992 | 3.8079 | 3.7993 | 3.8028 | 3.8017 | 3.6002 | 3.591 | 3.6037 | 3.8266 | 3.857 | 3.8543 | 3.8554 | 3.3572 | 3.3671 | 3.3747 | 3.365 | 3.3672 | 3.383 | 3.3887 | 3.3732 | 3.3736 | 3.3916 | 3.3847 | 3.3921 | 3.3787 | 3.3781 | 3.3858 | 3.3898 | 3.3829 | 3.3872 | 3.1149 | 3.1188 | 3.1122 | 3.384 | 3.3732 | 3.3782 | 3.3736 | 3.369 | 3.3743 | 3.3834 | 3.3709 | 3.3776 | 3.803 | 3.8043 | 3.788 | 3.1147 | 3.116 | 3.1191 | 3.3869 | 3.3778 | 3.3733 | 3.37 | 3.3797 | 3.3825 | 3.3777 | 3.373 | 3.3691 | 3.79 | 3.8016 | 3.7897 | 3.8016 | 3.8004 | 3.7965 | 3.8041 | 3.7984 | 3.7979 | 3.852 | 3.8523 | 3.8661 | 3.8482 | 3.8472 | 3.844 | 3.5865 | 3.5939 | 3.5897 | 3.6003 | 3.5993 | 3.5985 | 3.1162 | 3.1087 | 3.1058 | 3.3819 | 3.3775 | 3.3687 | 3.3765 | 3.3746 | 3.3702 | 3.3889 | 3.3777 | 3.381 | 3.792 | 3.7928 | 3.7994 | 3.378 | 3.3731 | 3.3674 | 3.374 | 3.3809 | 3.3759 | 3.8014 | 3.7902 | 3.7934 | 3.8394 | 3.8376 | 3.8404 | 3.8626 | 3.794 | 3.7913 | 3.8104 | 3.8042 | 3.7946 | 3.8043 | 3.8029 | 3.7912 | 3.7974 | 3.788 | 3.7866 | 3.6 | 3.5988 | 3.5962 | 3.599 | 3.5911 | 3.5855 | 3.1069 | 3.1137 | 3.118 | 3.1204 | 3.1154 | 3.1086 | 3.3846 | 3.3807 | 3.385 | 3.3785 | 3.3734 | 3.3813 | 3.3765 | 3.37 | 3.3721 | 3.3698 | 3.3726 | 3.3709 | 3.3801 | 3.3639 | 3.375 | 3.7952 | 3.7838 | 3.7898 | 3.8022 | 3.7946 | 3.7985
106 | Suction SH | ºC | 9.4295 | 9.7396 | 9.6865 | 11.7056 | 11.726 | 11.674 | 12.9533 | 12.7888 | 12.6923 | 11.7635 | 11.5063 | 11.3301 | 11.0687 | 11.0747 | 11.0859 | 9.2609 | 9.1758 | 8.9897 | 11.1705 | 10.6531 | 10.6074 | 9.9831 | 9.4613 | 9.3503 | 8.8574 | 8.8284 | 8.7703 | 8.893 | 8.8127 | 8.7044 | 11.3115 | 11.2317 | 11.0813 | 10.8116 | 10.5869 | 10.387 | 11.1162 | 10.2972 | 10.2646 | 10.2818 | 10.352 | 10.3537 | 10.3973 | 10.5441 | 10.8877 | 10.3469 | 10.7823 | 9.9621 | 10.4527 | 10.4328 | 10.4233 | 11.178 | 10.9729 | 10.7394 | 9.3561 | 9.4578 | 9.5938 | 11.149 | 11.0158 | 11.073 | 11.4144 | 11.4532 | 11.477 | 10.8738 | 11.2698 | 11.6959 | 10.6476 | 10.6856 | 10.5975 | 10.0422 | 10.029 | 9.4905 | 9.3458 | 8.8189 | 9.5578 | 9.4444 | 9.3344 | 8.8894 | 9.4378 | 9.4443 | 9.5455 | 10.9755 | 11.067 | 11.0231 | 10.001 | 10.694 | 10.7658 | 10.494 | 9.8315 | 10.0948 | 10.3873 | 10.5276 | 9.6302 | 10.6404 | 10.9159 | 14.939 | 15.4072 | 14.7917 | 17.6256 | 17.5501 | 17.6117 | 17.58 | 17.4269 | 17.3341 | 17.3591 | 17.2641 | 10.4357 | 10.6962 | 10.7296 | 9.5537 | 9.8212 | 10.5705 | 11.509 | 11.7638 | 11.9763 | 9.1395 | 9.9261 | 9.2822 | 10.1917 | 10.0266 | 10.2927 | 9.7184 | 9.5313 | 9.2746 | 9.5186 | 9.2937 | 8.9144 | 10.8157 | 10.4146 | 10.5421 | 9.3214 | 9.5454 | 9.5714 | 9.3838 | 9.3217 | 9.1065 | 10.8836 | 11.1218 | 11.9472 | 11.7024 | 11.2851 | 10.9128 | 10.0575 | 10.2315 | 10.2563 | 10.3459 | 10.0403 | 9.9667 | 9.7641 | 9.6814 | 9.6553 | 10.4915 | 10.3002 | 9.8552 | 10.8786 | 9.7704 | 8.4378 | 9.2086 | 9.0391 | 9.1167 | 9.1771 | 8.9107 | 9.0079 | 10.7852 | 12.0946 | 11.2698 | 11.4184 | 11.2262 | 11.0012 | 11.2656 | 11.2507 | 11.491 | 11.5988 | 11.5299 | 10.7134 | 9.8895 | 10.0204 | 9.9124 | 10.2554 | 10.0656 | 9.9853 | 9.7632 | 10.3985 | 10.5757 | 10.4565 | 10.5944 | 10.8792 | 10.0605 | 10.0664 | 10.4098 | 9.4996 | 9.7399 | 9.7618 | 10.3485 | 10.2999 | 10.5105 | 10.8608 | 10.6732 | 10.5899 | 10.184 | 10.1183 | 9.9836 | 9.8506 | 9.5988 | 9.2792 | 9.9301 | 9.8152 | 10.0654 | 9.7893 | 9.8697 | 9.9779 | 10.0065 | 9.9707 | 9.6914 | 9.8839 | 9.9297 | 9.9134 | 10.3108 | 10.215 | 10.0378 | 10.2687 | 10.4544 | 10.4088 | 10.2674 | 10.4436 | 10.6161
107 | Suction Gauge | ºC | 5.8159 | 5.7387 | 5.7481 | 5.855 | 5.795 | 5.7536 | 7.3309 | 7.4129 | 7.3707 | 7.3106 | 7.4729 | 7.4713 | 7.5019 | 7.4136 | 7.4071 | 7.8581 | 7.8367 | 7.733 | 7.8054 | 7.8525 | 7.7967 | 7.4091 | 7.4779 | 7.4393 | 7.337 | 7.3518 | 7.4234 | 7.4157 | 7.3881 | 7.4661 | 5.8551 | 5.79 | 5.7359 | 5.7585 | 5.7962 | 5.7363 | 5.7931 | 4.0191 | 4.041 | 4.0037 | 4.0212 | 4.044 | 4.0581 | 4.0857 | 4.1028 | 1.7679 | 1.7087 | 1.6604 | 4.018 | 4.0439 | 4.0237 | 4.0281 | 4.0116 | 4.0364 | 1.7149 | 1.7248 | 1.7011 | 5.8199 | 5.7791 | 5.747 | 5.8193 | 5.7885 | 5.7659 | 7.4376 | 7.4492 | 7.4441 | 7.7278 | 7.7381 | 7.86 | 7.8858 | 7.7763 | 5.7751 | 5.7756 | 5.8203 | 7.3896 | 7.4265 | 7.411 | 7.4778 | 7.4116 | 7.4388 | 7.4301 | 5.8425 | 5.7689 | 5.8709 | 7.6214 | 7.8545 | 7.8336 | 7.8419 | 3.8356 | 3.9195 | 3.9838 | 3.9014 | 3.9206 | 4.0538 | 4.1016 | 3.971 | 3.9743 | 4.1267 | 4.068 | 4.1303 | 4.0176 | 4.0123 | 4.0773 | 4.1109 | 4.0527 | 4.0896 | 1.7195 | 1.7552 | 1.6955 | 4.0623 | 3.9712 | 4.013 | 3.9743 | 3.9357 | 3.9807 | 4.0571 | 3.9514 | 4.0081 | 7.4402 | 7.4504 | 7.3242 | 1.7182 | 1.7293 | 1.7573 | 4.0871 | 4.0095 | 3.9715 | 3.9439 | 4.0261 | 4.0498 | 4.0094 | 3.9691 | 3.9364 | 7.34 | 7.4291 | 7.3371 | 7.4293 | 7.4202 | 7.3903 | 7.4488 | 7.4048 | 7.4005 | 7.8163 | 7.8183 | 7.9242 | 7.7876 | 7.7795 | 7.755 | 5.7321 | 5.7925 | 5.7584 | 5.844 | 5.8357 | 5.8295 | 1.7314 | 1.6637 | 1.6382 | 4.0446 | 4.0075 | 3.9326 | 3.9987 | 3.9832 | 3.9456 | 4.1033 | 4.0092 | 4.0372 | 7.3554 | 7.3613 | 7.412 | 4.0114 | 3.9698 | 3.9219 | 3.9776 | 4.0357 | 3.9942 | 7.4275 | 7.341 | 7.3661 | 7.7196 | 7.7059 | 7.7278 | 7.8975 | 7.3709 | 7.3497 | 7.4973 | 7.449 | 7.3756 | 7.4501 | 7.4396 | 7.349 | 7.3966 | 7.3244 | 7.3135 | 5.8415 | 5.8315 | 5.8103 | 5.8329 | 5.7695 | 5.7243 | 1.6477 | 1.7087 | 1.748 | 1.7692 | 1.7242 | 1.663 | 4.067 | 4.0347 | 4.0707 | 4.0158 | 3.9729 | 4.0398 | 3.999 | 3.9438 | 3.9618 | 3.9423 | 3.9658 | 3.9515 | 4.0292 | 3.8926 | 3.9862 | 7.38 | 7.2918 | 7.3381 | 7.4342 | 7.375 | 7.4052
108 | Suction Enthalpy | KJ/kg | 410.5988 | 410.834 | 410.7913 | 412.6953 | 412.6765 | 412.6035 | 414.7517 | 414.6521 | 414.5375 | 413.6497 | 413.5144 | 413.3518 | 413.131 | 413.0822 | 413.0885 | 411.6885 | 411.5973 | 411.3634 | 413.411 | 412.9647 | 412.8886 | 412.0786 | 411.6417 | 411.5163 | 411.0019 | 410.9843 | 410.9743 | 411.0823 | 410.9918 | 410.9396 | 412.3366 | 412.2237 | 412.0534 | 411.8219 | 411.6407 | 411.4218 | 412.1205 | 410.2804 | 410.2645 | 410.257 | 410.3312 | 410.3468 | 410.395 | 410.5446 | 410.8656 | 408.9269 | 409.2793 | 408.5159 | 410.4202 | 410.4182 | 410.3971 | 411.0814 | 410.8859 | 410.6906 | 408.0078 | 408.1048 | 408.2118 | 412.1669 | 412.0205 | 412.0527 | 412.408 | 412.4243 | 412.4319 | 412.9127 | 413.283 | 413.6703 | 412.8833 | 412.9246 | 412.9183 | 412.4238 | 412.3448 | 410.6295 | 410.4979 | 410.0451 | 411.6766 | 411.5949 | 411.4846 | 411.1166 | 411.5799 | 411.6023 | 411.6899 | 412.023 | 412.0608 | 412.0838 | 412.2246 | 413.0035 | 413.0567 | 412.8122 | 409.7464 | 410.036 | 410.3399 | 410.4155 | 409.6171 | 410.6118 | 410.8904 | 414.4393 | 414.8638 | 414.4055 | 416.9257 | 416.8978 | 416.8806 | 416.8486 | 416.7523 | 416.6903 | 416.6752 | 416.6134 | 408.9761 | 409.2313 | 409.2239 | 409.6353 | 409.8208 | 410.5235 | 411.3467 | 411.5526 | 411.7725 | 409.2577 | 409.9033 | 409.3565 | 412.2889 | 412.1437 | 412.3106 | 408.3339 | 408.1734 | 407.9611 | 409.6189 | 409.3679 | 409.0017 | 410.702 | 410.3908 | 410.5206 | 409.3928 | 409.5704 | 409.5737 | 411.4868 | 411.4839 | 411.2306 | 412.9167 | 413.1295 | 413.8673 | 413.6792 | 413.2696 | 412.9258 | 412.3954 | 412.5565 | 412.644 | 412.6428 | 412.3572 | 412.2746 | 410.8522 | 410.8139 | 410.7693 | 411.5833 | 411.404 | 410.9949 | 409.3795 | 408.3465 | 407.1389 | 409.3125 | 409.1365 | 409.1607 | 409.2558 | 409.0055 | 409.0704 | 410.7734 | 411.8971 | 411.17 | 413.3614 | 413.1889 | 413.0139 | 411.1501 | 411.1108 | 411.2978 | 411.4298 | 411.4038 | 410.6409 | 412.004 | 412.0712 | 411.9875 | 412.5182 | 412.3355 | 412.2751 | 412.1744 | 412.4362 | 412.5856 | 412.5667 | 412.6636 | 412.8797 | 412.1746 | 412.1736 | 412.4331 | 411.6273 | 411.8038 | 411.8173 | 411.4516 | 411.4011 | 411.5798 | 411.9126 | 411.7028 | 411.5991 | 408.7064 | 408.6856 | 408.5895 | 408.4838 | 408.2306 | 407.9068 | 409.9783 | 409.8546 | 410.1028 | 409.8195 | 409.8657 | 410.0048 | 410.0054 | 409.9389 | 409.6977 | 409.8596 | 409.9155 | 409.892 | 410.2989 | 410.1279 | 410.0258 | 412.3228 | 412.4389 | 412.4255 | 412.3547 | 412.48 | 412.6567
109 | Suction specific volume | m3/kg | 0.059598 | 0.059841 | 0.059807 | 0.060176 | 0.060303 | 0.060371 | 0.057649 | 0.057449 | 0.057502 | 0.057361 | 0.056985 | 0.05694 | 0.056811 | 0.056978 | 0.056993 | 0.055656 | 0.055672 | 0.055811 | 0.056274 | 0.056047 | 0.056137 | 0.056685 | 0.056413 | 0.056454 | 0.056507 | 0.056471 | 0.056322 | 0.056371 | 0.0564 | 0.056225 | 0.060063 | 0.06017 | 0.060235 | 0.060112 | 0.059972 | 0.060034 | 0.060131 | 0.063564 | 0.063508 | 0.063593 | 0.063577 | 0.063528 | 0.063511 | 0.063497 | 0.063565 | 0.068638 | 0.068919 | 0.068765 | 0.063614 | 0.063553 | 0.063593 | 0.063813 | 0.063786 | 0.063662 | 0.068438 | 0.068448 | 0.068549 | 0.060087 | 0.06013 | 0.060211 | 0.060164 | 0.060237 | 0.06029 | 0.056878 | 0.056965 | 0.057091 | 0.056275 | 0.056267 | 0.056018 | 0.055819 | 0.056017 | 0.059696 | 0.059654 | 0.059411 | 0.056604 | 0.056504 | 0.056502 | 0.056254 | 0.056529 | 0.056481 | 0.056525 | 0.059992 | 0.060165 | 0.059949 | 0.056295 | 0.056054 | 0.056112 | 0.056023 | 0.063817 | 0.063717 | 0.063668 | 0.063888 | 0.063572 | 0.063595 | 0.063576 | 0.065071 | 0.065204 | 0.064687 | 0.065657 | 0.065498 | 0.065764 | 0.065767 | 0.065578 | 0.065477 | 0.065612 | 0.065503 | 0.068781 | 0.068781 | 0.068933 | 0.063245 | 0.063522 | 0.063661 | 0.064029 | 0.06419 | 0.064157 | 0.06313 | 0.063597 | 0.063278 | 0.056685 | 0.05662 | 0.05693 | 0.068549 | 0.068462 | 0.068312 | 0.063182 | 0.063278 | 0.063243 | 0.063884 | 0.063585 | 0.063573 | 0.063287 | 0.063442 | 0.06352 | 0.056648 | 0.056465 | 0.056576 | 0.056896 | 0.056978 | 0.057261 | 0.057084 | 0.057052 | 0.056958 | 0.055951 | 0.055995 | 0.055807 | 0.056082 | 0.056014 | 0.056039 | 0.059862 | 0.059717 | 0.059778 | 0.059849 | 0.05981 | 0.059694 | 0.068897 | 0.068695 | 0.068316 | 0.063178 | 0.063205 | 0.063389 | 0.063266 | 0.063217 | 0.063327 | 0.063532 | 0.064131 | 0.063821 | 0.057182 | 0.057118 | 0.056961 | 0.063876 | 0.063961 | 0.064137 | 0.06405 | 0.063903 | 0.063745 | 0.056625 | 0.056823 | 0.056746 | 0.056183 | 0.056157 | 0.056094 | 0.055721 | 0.056871 | 0.05696 | 0.056651 | 0.056779 | 0.056995 | 0.05663 | 0.056651 | 0.056916 | 0.056575 | 0.056776 | 0.056803 | 0.059813 | 0.059819 | 0.059922 | 0.059978 | 0.06005 | 0.060117 | 0.068868 | 0.068702 | 0.068566 | 0.068473 | 0.068496 | 0.068535 | 0.06335 | 0.063384 | 0.063383 | 0.063417 | 0.063533 | 0.063423 | 0.063519 | 0.063626 | 0.063502 | 0.063603 | 0.063567 | 0.063592 | 0.063547 | 0.063811 | 0.063556 | 0.056818 | 0.057035 | 0.056936 | 0.056717 | 0.056876 | 0.056867
110
111 | Discharge Temp | ºC | 64.9206 | 65.4558 | 65.7251 | 67.6261 | 67.6046 | 67.6164 | 56.3924 | 56.3225 | 56.2193 | 56.017 | 55.9235 | 55.7537 | 55.4961 | 55.3446 | 55.1113 | 45.7004 | 45.4766 | 45.3926 | 46.4671 | 46.0189 | 45.609 | 53.5322 | 53.2481 | 53.3954 | 52.6919 | 52.6848 | 52.5961 | 53.6881 | 53.541 | 53.3669 | 66.9299 | 66.7963 | 66.7029 | 66.5891 | 66.413 | 66.1839 | 67.2566 | 79.4 | 79.3899 | 79.3811 | 79.4592 | 79.4766 | 79.5019 | 79.6386 | 79.8189 | 83.6596 | 83.69 | 83.1033 | 80.6129 | 80.5601 | 80.7132 | 80.4026 | 80.0417 | 79.8318 | 82.6253 | 82.7389 | 82.8015 | 66.8161 | 66.7456 | 66.7452 | 67.1784 | 67.198 | 67.1985 | 55.9889 | 56.3751 | 56.574 | 46.7646 | 46.6674 | 46.5323 | 45.7305 | 45.2656 | 65.4899 | 65.4777 | 65.9108 | 53.5212 | 53.4746 | 53.3858 | 53.0156 | 53.6689 | 53.7036 | 53.7298 | 56.208 | 56.2506 | 56.3103 | 47.6678 | 48.0269 | 47.9808 | 47.9414 | 79.0585 | 79.3621 | 79.6115 | 79.6811 | 80.2055 | 80.973 | 81.2442 | 84.6134 | 84.8795 | 84.1783 | 81.3351 | 81.2728 | 80.9674 | 80.7776 | 80.4931 | 80.4914 | 80.2766 | 79.5949 | 81.6492 | 81.8133 | 81.7659 | 78.36 | 78.5664 | 79.1082 | 79.3911 | 79.5723 | 79.7772 | 77.2175 | 77.1545 | 76.8154 | 54.0542 | 53.963 | 53.9896 | 81.1123 | 80.8792 | 80.8373 | 77.4235 | 77.1664 | 76.8264 | 79.0837 | 78.7779 | 79.2053 | 76.5866 | 76.7418 | 76.5902 | 52.7574 | 52.5277 | 52.4436 | 54.6356 | 55.0605 | 55.1597 | 54.7452 | 54.0465 | 53.7595 | 46.5342 | 46.5135 | 46.384 | 46.505 | 45.5963 | 45.1859 | 64.4279 | 64.2532 | 64.3681 | 65.2223 | 64.9016 | 64.4856 | 82.3417 | 81.291 | 80.4547 | 78.0616 | 77.9128 | 77.841 | 77.0956 | 77.092 | 77.3296 | 78.4717 | 79.1191 | 78.5143 | 54.4239 | 54.1733 | 53.8665 | 79.6024 | 79.6789 | 79.8482 | 80.4132 | 80.318 | 79.6525 | 53.2308 | 53.4036 | 53.8557 | 46.8378 | 46.7412 | 46.8191 | 46.4041 | 47.0398 | 46.9755 | 46.7694 | 46.714 | 46.6495 | 53.6349 | 53.649 | 53.7512 | 53.5421 | 53.736 | 54.1174 | 65.0396 | 64.7326 | 64.928 | 65.7567 | 65.5189 | 65.2597 | 81.891 | 81.6127 | 81.551 | 81.3886 | 81.121 | 80.9454 | 78.01 | 77.8995 | 78.0808 | 77.851 | 77.8788 | 77.9965 | 78.6803 | 78.5979 | 78.6633 | 78.8859 | 78.9505 | 78.9132 | 77.7743 | 77.6319 | 77.0981 | 53.3605 | 53.4136 | 53.4166 | 53.4228 | 53.4506 | 53.2936
112 | Discharge Pressure | BarA | 10.7394 | 10.715 | 10.7405 | 10.6993 | 10.719 | 10.6929 | 8.4618 | 8.4893 | 8.4636 | 8.4292 | 8.4677 | 8.4714 | 8.4773 | 8.4653 | 8.4388 | 7.2964 | 7.2976 | 7.2541 | 7.2574 | 7.285 | 7.2595 | 8.4489 | 8.4733 | 8.4528 | 8.435 | 8.4315 | 8.4407 | 8.4481 | 8.4501 | 8.4633 | 10.7535 | 10.7405 | 10.7212 | 10.7149 | 10.7299 | 10.7144 | 10.7206 | 13.3851 | 13.3886 | 13.3936 | 13.3867 | 13.3856 | 13.3864 | 13.3784 | 13.3776 | 13.745 | 13.7197 | 13.7147 | 13.4178 | 13.3795 | 13.3704 | 13.2181 | 13.1762 | 13.1516 | 13.7187 | 13.746 | 13.7199 | 10.7201 | 10.7179 | 10.7487 | 10.7184 | 10.7094 | 10.7013 | 8.4341 | 8.457 | 8.4502 | 7.2563 | 7.2664 | 7.2934 | 7.3274 | 7.271 | 10.7071 | 10.697 | 10.7165 | 8.4371 | 8.4414 | 8.4467 | 8.4713 | 8.4527 | 8.4438 | 8.4403 | 8.4262 | 8.4255 | 8.434 | 7.3284 | 7.3412 | 7.3145 | 7.2958 | 13.3169 | 13.3768 | 13.3935 | 13.3714 | 13.3907 | 13.3788 | 13.3652 | 13.1906 | 13.1972 | 13.2068 | 13.3664 | 13.389 | 13.3506 | 13.3523 | 13.2343 | 13.2717 | 13.2391 | 13.1672 | 13.7284 | 13.7237 | 13.7373 | 13.3937 | 13.3318 | 13.3524 | 13.1849 | 13.1481 | 13.1656 | 13.421 | 13.3407 | 13.3763 | 8.4878 | 8.4893 | 8.4299 | 13.7673 | 13.7713 | 13.7562 | 13.2264 | 13.1938 | 13.1836 | 13.3636 | 13.372 | 13.3756 | 13.3576 | 13.334 | 13.3241 | 8.4772 | 8.4949 | 8.4357 | 8.4877 | 8.451 | 8.4772 | 8.4476 | 8.4216 | 8.4372 | 7.2724 | 7.2728 | 7.2681 | 7.2915 | 7.2806 | 7.2693 | 10.7296 | 10.6876 | 10.683 | 10.7049 | 10.7139 | 10.6824 | 13.7816 | 13.7425 | 13.773 | 13.4206 | 13.421 | 13.3788 | 13.2315 | 13.1645 | 13.1949 | 13.4541 | 13.3976 | 13.362 | 8.4305 | 8.487 | 8.4393 | 13.2092 | 13.2131 | 13.2024 | 13.405 | 13.4526 | 13.4653 | 8.4564 | 8.4328 | 8.4492 | 7.3105 | 7.304 | 7.2915 | 7.2684 | 7.2899 | 7.2883 | 7.2852 | 7.2523 | 7.2289 | 8.4692 | 8.4563 | 8.4225 | 8.4682 | 8.4424 | 8.4431 | 10.7534 | 10.7388 | 10.6701 | 10.7201 | 10.7 | 10.6855 | 13.7548 | 13.6947 | 13.7058 | 13.7238 | 13.721 | 13.6836 | 13.1796 | 13.1356 | 13.1836 | 13.1569 | 13.1216 | 13.142 | 13.3403 | 13.3216 | 13.3353 | 13.4026 | 13.413 | 13.4123 | 13.3658 | 13.3976 | 13.3621 | 8.441 | 8.4216 | 8.4325 | 8.4581 | 8.4487 | 8.434
113 | Discharge SH | ºC | 22.8601 | 23.4816 | 23.6609 | 25.7072 | 25.6162 | 25.72 | 23.0797 | 22.8942 | 22.8991 | 22.8417 | 22.5862 | 22.4006 | 22.1182 | 22.0169 | 21.8955 | 17.5703 | 17.3411 | 17.4621 | 18.5212 | 17.9426 | 17.6529 | 20.2737 | 19.887 | 20.1205 | 19.492 | 19.4996 | 19.3723 | 20.4333 | 20.2775 | 20.0479 | 24.8198 | 24.7321 | 24.7068 | 24.6152 | 24.3861 | 24.2117 | 25.2625 | 28.7816 | 28.7612 | 28.7373 | 28.836 | 28.8567 | 28.8797 | 29.0404 | 29.2228 | 31.978 | 32.0823 | 31.5104 | 29.897 | 29.9585 | 30.1387 | 30.2849 | 30.0503 | 29.9147 | 31.0208 | 31.0542 | 31.1932 | 24.8238 | 24.761 | 24.6522 | 25.192 | 25.2434 | 25.2726 | 22.7931 | 23.0824 | 23.31 | 18.8238 | 18.6786 | 18.4163 | 17.455 | 17.2553 | 23.5433 | 23.5668 | 23.9311 | 20.3127 | 20.2481 | 20.1366 | 19.6627 | 20.3947 | 20.4667 | 20.5079 | 23.0456 | 23.0911 | 23.1146 | 19.3874 | 19.6867 | 19.7657 | 19.8144 | 28.644 | 28.7683 | 28.9679 | 29.1037 | 29.5704 | 30.3734 | 30.6853 | 34.5785 | 34.8248 | 34.0946 | 30.7725 | 30.6428 | 30.4519 | 30.2572 | 30.3266 | 30.2124 | 30.0958 | 29.6308 | 30.0162 | 30.194 | 30.1069 | 27.7159 | 28.1072 | 28.5874 | 29.3735 | 29.6658 | 29.8178 | 26.4922 | 26.6689 | 26.2233 | 20.6321 | 20.5345 | 20.8115 | 29.3654 | 29.1206 | 29.123 | 27.2808 | 27.1218 | 26.8128 | 28.5295 | 28.1986 | 28.6154 | 26.0503 | 26.2762 | 26.1543 | 19.3798 | 19.0757 | 19.2409 | 21.2141 | 21.7933 | 21.7821 | 21.4923 | 20.9033 | 20.5507 | 18.5174 | 18.4945 | 18.3873 | 18.398 | 17.5406 | 17.1837 | 22.4022 | 22.3757 | 22.5068 | 23.2834 | 22.931 | 22.6264 | 30.553 | 29.6166 | 28.6912 | 27.3374 | 27.1873 | 27.2415 | 26.9376 | 27.136 | 27.282 | 27.6477 | 28.4635 | 27.9648 | 21.2429 | 20.7547 | 20.6487 | 29.5114 | 29.5762 | 29.7777 | 29.7355 | 29.4985 | 28.7954 | 19.9406 | 20.2131 | 20.5962 | 18.6414 | 18.5754 | 18.712 | 18.4059 | 18.9403 | 18.8837 | 18.6919 | 18.7919 | 18.838 | 20.2908 | 20.3594 | 20.6041 | 20.2023 | 20.5052 | 20.8835 | 22.93 | 22.6742 | 23.1124 | 23.7644 | 23.5974 | 23.3896 | 30.1806 | 30.0783 | 29.9841 | 29.769 | 29.5098 | 29.4436 | 28.0083 | 28.0309 | 28.067 | 27.918 | 28.0525 | 28.1087 | 28.1958 | 28.1692 | 28.1938 | 28.2152 | 28.2489 | 28.2137 | 27.2136 | 26.9761 | 26.5484 | 20.1355 | 20.2704 | 20.2274 | 20.1256 | 20.1929 | 20.098
114 | Discharge Gauge | ºC | 42.0605 | 41.9742 | 42.0643 | 41.9189 | 41.9884 | 41.8964 | 33.3127 | 33.4284 | 33.3203 | 33.1753 | 33.3374 | 33.3531 | 33.3778 | 33.3276 | 33.2157 | 28.1301 | 28.1355 | 27.9304 | 27.9459 | 28.0763 | 27.9561 | 33.2585 | 33.3611 | 33.2748 | 33.1999 | 33.1852 | 33.2237 | 33.2548 | 33.2635 | 33.3189 | 42.11 | 42.0642 | 41.9961 | 41.9739 | 42.0269 | 41.9722 | 41.9941 | 50.6184 | 50.6287 | 50.6438 | 50.6231 | 50.6199 | 50.6222 | 50.5983 | 50.596 | 51.6816 | 51.6077 | 51.5929 | 50.7159 | 50.6016 | 50.5745 | 50.1176 | 49.9914 | 49.9171 | 51.6045 | 51.6847 | 51.6083 | 41.9923 | 41.9847 | 42.093 | 41.9864 | 41.9546 | 41.9259 | 33.1958 | 33.2926 | 33.264 | 27.9408 | 27.9887 | 28.116 | 28.2755 | 28.0103 | 41.9466 | 41.9109 | 41.9798 | 33.2086 | 33.2265 | 33.2491 | 33.3529 | 33.2742 | 33.2369 | 33.2219 | 33.1624 | 33.1595 | 33.1957 | 28.2804 | 28.3402 | 28.2151 | 28.127 | 50.4144 | 50.5938 | 50.6435 | 50.5774 | 50.635 | 50.5996 | 50.5589 | 50.0349 | 50.0548 | 50.0837 | 50.5626 | 50.6299 | 50.5155 | 50.5203 | 50.1665 | 50.279 | 50.1808 | 49.9641 | 51.633 | 51.6193 | 51.659 | 50.6441 | 50.4592 | 50.5208 | 50.0177 | 49.9065 | 49.9594 | 50.7253 | 50.4856 | 50.5921 | 33.4221 | 33.4285 | 33.1781 | 51.7468 | 51.7586 | 51.7144 | 50.1428 | 50.0446 | 50.0136 | 50.5542 | 50.5793 | 50.5899 | 50.5363 | 50.4656 | 50.4359 | 33.3776 | 33.4519 | 33.2027 | 33.4215 | 33.2672 | 33.3777 | 33.253 | 33.1432 | 33.2089 | 28.0168 | 28.019 | 27.9967 | 28.1069 | 28.0557 | 28.0022 | 42.0257 | 41.8775 | 41.8613 | 41.9388 | 41.9706 | 41.8592 | 51.7887 | 51.6744 | 51.7636 | 50.7242 | 50.7255 | 50.5996 | 50.158 | 49.956 | 50.0477 | 50.824 | 50.6556 | 50.5495 | 33.1809 | 33.4186 | 33.2179 | 50.091 | 50.1027 | 50.0705 | 50.6778 | 50.8195 | 50.8571 | 33.2901 | 33.1905 | 33.2595 | 28.1964 | 28.1658 | 28.1071 | 27.9981 | 28.0995 | 28.0917 | 28.0774 | 27.9221 | 27.8115 | 33.344 | 33.2896 | 33.147 | 33.3398 | 33.2308 | 33.2338 | 42.1095 | 42.0584 | 41.8156 | 41.9923 | 41.9215 | 41.8701 | 51.7103 | 51.5343 | 51.5669 | 51.6196 | 51.6112 | 51.5018 | 50.0017 | 49.8686 | 50.0138 | 49.933 | 49.8263 | 49.8879 | 50.4845 | 50.4287 | 50.4695 | 50.6707 | 50.7016 | 50.6995 | 50.5607 | 50.6558 | 50.5497 | 33.225 | 33.1433 | 33.1891 | 33.2972 | 33.2577 | 33.1957
115 | Discharge enthalpy | KJ/kg | 445.4445 | 446.0554 | 446.298 | 448.3834 | 448.3281 | 448.3837 | 440.5108 | 440.3911 | 440.331 | 440.185 | 440.0218 | 439.8417 | 439.5681 | 439.4345 | 439.2435 | 431.8391 | 431.6126 | 431.6124 | 432.6814 | 432.1801 | 431.8186 | 437.6111 | 437.2757 | 437.4639 | 436.7764 | 436.7755 | 436.6678 | 437.7722 | 437.6179 | 437.4156 | 447.5552 | 447.4353 | 447.3686 | 447.2585 | 447.0464 | 446.8294 | 447.9567 | 456.784 | 456.7674 | 456.7499 | 456.8465 | 456.8674 | 456.8939 | 457.0566 | 457.2557 | 460.9192 | 460.9901 | 460.3526 | 458.0657 | 458.0665 | 458.2483 | 458.1407 | 457.8099 | 457.618 | 459.8206 | 459.9044 | 460.0126 | 447.4904 | 447.4194 | 447.3674 | 447.8774 | 447.9132 | 447.9272 | 440.1478 | 440.5014 | 440.7164 | 432.9809 | 432.8645 | 432.678 | 431.8097 | 431.4526 | 446.1049 | 446.1092 | 446.5359 | 437.6214 | 437.566 | 437.4652 | 437.041 | 437.7442 | 437.7958 | 437.829 | 440.3852 | 440.4299 | 440.4757 | 433.7484 | 434.0839 | 434.0876 | 434.0832 | 456.5149 | 456.7551 | 457.0032 | 457.114 | 457.6601 | 458.5204 | 458.8384 | 462.7759 | 463.056 | 462.2787 | 458.9361 | 458.8335 | 458.5571 | 458.3465 | 458.215 | 458.156 | 457.9708 | 457.335 | 458.7307 | 458.9187 | 458.8457 | 455.6264 | 455.9509 | 456.5142 | 457.0845 | 457.3396 | 457.5368 | 454.3236 | 454.3828 | 453.9516 | 438.0746 | 437.9785 | 438.1135 | 458.0786 | 457.815 | 457.7922 | 454.8611 | 454.6303 | 454.2731 | 456.4698 | 456.1204 | 456.5848 | 453.7293 | 453.9386 | 453.7874 | 436.7656 | 436.4973 | 436.5209 | 438.6698 | 439.1699 | 439.2245 | 438.8538 | 438.1866 | 437.865 | 432.72 | 432.6983 | 432.5778 | 432.6543 | 431.7653 | 431.3761 | 444.9373 | 444.8241 | 444.9542 | 445.8244 | 445.4681 | 445.0801 | 459.413 | 458.314 | 457.3433 | 455.2552 | 455.0904 | 455.0785 | 454.4925 | 454.5953 | 454.8081 | 455.6541 | 456.4557 | 455.8461 | 438.5561 | 438.198 | 437.9706 | 457.2784 | 457.3561 | 457.558 | 457.8661 | 457.6883 | 456.9369 | 437.2888 | 437.5089 | 437.9416 | 432.9513 | 432.867 | 432.9687 | 432.5973 | 433.1925 | 433.1313 | 432.9308 | 432.9379 | 432.9176 | 437.6791 | 437.7171 | 437.8831 | 437.586 | 437.8315 | 438.2202 | 445.5472 | 445.2455 | 445.5714 | 446.3662 | 446.1478 | 445.8973 | 458.9569 | 458.7418 | 458.6569 | 458.4503 | 458.1596 | 458.0233 | 455.5791 | 455.5272 | 455.6504 | 455.4405 | 455.5265 | 455.6236 | 456.0628 | 456.0015 | 456.052 | 456.1912 | 456.2461 | 456.2061 | 455.0256 | 454.818 | 454.2863 | 437.4499 | 437.5395 | 437.5227 | 437.4823 | 437.5279 | 437.3941
116 | Discharge specific volume | m3/kg | 0.021725 | 0.021847 | 0.021815 | 0.022133 | 0.022082 | 0.022148 | 0.027606 | 0.027492 | 0.027575 | 0.027679 | 0.027519 | 0.027482 | 0.027424 | 0.027448 | 0.027518 | 0.031101 | 0.03106 | 0.031264 | 0.031417 | 0.031208 | 0.031271 | 0.02726 | 0.027128 | 0.027226 | 0.027195 | 0.027208 | 0.02716 | 0.027285 | 0.027257 | 0.027182 | 0.02192 | 0.021937 | 0.021974 | 0.021977 | 0.02192 | 0.021932 | 0.022039 | 0.017936 | 0.017929 | 0.01792 | 0.017939 | 0.017942 | 0.017944 | 0.01797 | 0.017988 | 0.017753 | 0.017796 | 0.01775 | 0.017997 | 0.018055 | 0.018084 | 0.01831 | 0.018346 | 0.018368 | 0.0177 | 0.017667 | 0.017714 | 0.02199 | 0.021987 | 0.021911 | 0.022035 | 0.02206 | 0.02208 | 0.027657 | 0.027622 | 0.027675 | 0.03147 | 0.031404 | 0.031247 | 0.030953 | 0.031159 | 0.02187 | 0.021894 | 0.021895 | 0.027303 | 0.027281 | 0.027248 | 0.027103 | 0.027265 | 0.027303 | 0.02732 | 0.027717 | 0.027726 | 0.027701 | 0.031252 | 0.031245 | 0.031369 | 0.031457 | 0.018016 | 0.017946 | 0.017942 | 0.017985 | 0.018003 | 0.018095 | 0.018143 | 0.018752 | 0.018765 | 0.018684 | 0.01815 | 0.018106 | 0.018141 | 0.018121 | 0.018291 | 0.018228 | 0.018262 | 0.018319 | 0.017594 | 0.017617 | 0.017591 | 0.017823 | 0.017944 | 0.017962 | 0.018269 | 0.018349 | 0.018339 | 0.017669 | 0.017794 | 0.017703 | 0.027185 | 0.027167 | 0.027396 | 0.017484 | 0.017456 | 0.017475 | 0.01801 | 0.01804 | 0.018024 | 0.017941 | 0.017898 | 0.017933 | 0.017711 | 0.017765 | 0.017767 | 0.027045 | 0.026946 | 0.027158 | 0.027266 | 0.027464 | 0.027378 | 0.027433 | 0.027436 | 0.027336 | 0.031353 | 0.031347 | 0.03135 | 0.031253 | 0.031163 | 0.031155 | 0.021693 | 0.021776 | 0.0218 | 0.021845 | 0.021786 | 0.021815 | 0.017575 | 0.017539 | 0.017414 | 0.01775 | 0.017735 | 0.017798 | 0.01797 | 0.018082 | 0.018054 | 0.017735 | 0.017889 | 0.01789 | 0.027454 | 0.027205 | 0.027343 | 0.018248 | 0.018249 | 0.018283 | 0.017999 | 0.017912 | 0.017829 | 0.027189 | 0.027303 | 0.027304 | 0.03121 | 0.031228 | 0.031302 | 0.031352 | 0.031345 | 0.031343 | 0.031325 | 0.031482 | 0.03159 | 0.027197 | 0.027248 | 0.027391 | 0.027188 | 0.027313 | 0.027364 | 0.021705 | 0.021705 | 0.021897 | 0.021869 | 0.021891 | 0.021897 | 0.017575 | 0.017644 | 0.017621 | 0.017578 | 0.017557 | 0.0176 | 0.018146 | 0.01821 | 0.018146 | 0.018169 | 0.018231 | 0.018208 | 0.017941 | 0.017964 | 0.017948 | 0.017858 | 0.017847 | 0.017845 | 0.017812 | 0.017747 | 0.017753 | 0.027266 | 0.027347 | 0.027306 | 0.02721 | 0.027249 | 0.027283
117
118 | Comp PR |  | 2.9858 | 2.9869 | 2.9931 | 2.9706 | 2.9823 | 2.9793 | 2.2333 | 2.2343 | 2.2308 | 2.2263 | 2.2241 | 2.2252 | 2.2244 | 2.228 | 2.2215 | 1.8915 | 1.8932 | 1.8885 | 1.8847 | 1.8889 | 1.8859 | 2.224 | 2.2252 | 2.2227 | 2.2258 | 2.2238 | 2.2207 | 2.2233 | 2.2259 | 2.2235 | 2.9857 | 2.9888 | 2.989 | 2.9849 | 2.9852 | 2.987 | 2.9829 | 3.9614 | 3.9594 | 3.9661 | 3.9616 | 3.9581 | 3.9564 | 3.9502 | 3.9476 | 4.4051 | 4.4063 | 4.4123 | 3.9712 | 3.9563 | 3.9564 | 3.9107 | 3.9006 | 3.8899 | 4.405 | 4.4122 | 4.4076 | 2.98 | 2.9836 | 2.9955 | 2.9796 | 2.9802 | 2.9803 | 2.2179 | 2.2231 | 2.2217 | 1.8894 | 1.8914 | 1.8906 | 1.8977 | 1.8902 | 2.981 | 2.9781 | 2.979 | 2.2224 | 2.2207 | 2.2233 | 2.2247 | 2.2248 | 2.2204 | 2.2201 | 2.3405 | 2.3463 | 2.3404 | 1.9151 | 1.9033 | 1.8978 | 1.8924 | 3.9666 | 3.9728 | 3.9688 | 3.9737 | 3.9768 | 3.9547 | 3.9441 | 3.9104 | 3.9119 | 3.8939 | 3.9491 | 3.9471 | 3.9514 | 3.9526 | 3.9088 | 3.9152 | 3.9136 | 3.8873 | 4.4074 | 4.4003 | 4.414 | 3.958 | 3.9523 | 3.9526 | 3.9083 | 3.9026 | 3.9017 | 3.9667 | 3.9576 | 3.9603 | 2.2319 | 2.2315 | 2.2254 | 4.4201 | 4.4196 | 4.4103 | 3.9051 | 3.9061 | 3.9083 | 3.9655 | 3.9565 | 3.9543 | 3.9546 | 3.9532 | 3.9548 | 2.2367 | 2.2346 | 2.226 | 2.2327 | 2.2237 | 2.2329 | 2.2206 | 2.2171 | 2.2216 | 1.8879 | 1.8879 | 1.8799 | 1.8948 | 1.8924 | 1.8911 | 2.9917 | 2.9738 | 2.976 | 2.9733 | 2.9767 | 2.9685 | 4.4226 | 4.4207 | 4.4346 | 3.9684 | 3.9736 | 3.9716 | 3.9187 | 3.901 | 3.9152 | 3.9701 | 3.9665 | 3.9521 | 2.2232 | 2.2377 | 2.2212 | 3.9104 | 3.9173 | 3.9207 | 3.9731 | 3.9791 | 3.9886 | 2.2246 | 2.2249 | 2.2273 | 1.9041 | 1.9033 | 1.8986 | 1.8817 | 1.9214 | 1.9224 | 1.9119 | 1.9064 | 1.905 | 2.2262 | 2.2236 | 2.2216 | 2.23 | 2.2287 | 2.2297 | 2.987 | 2.984 | 2.9671 | 2.9787 | 2.9796 | 2.9802 | 4.4272 | 4.3983 | 4.3957 | 4.3981 | 4.4042 | 4.4019 | 3.894 | 3.8854 | 3.8947 | 3.8943 | 3.8897 | 3.8866 | 3.9509 | 3.953 | 3.9546 | 3.9773 | 3.9771 | 3.9789 | 3.9543 | 3.9827 | 3.9591 | 2.2241 | 2.2257 | 2.2251 | 2.2245 | 2.2265 | 2.2204
119 | Comp PD |  | 7.1426 | 7.1277 | 7.1521 | 7.0976 | 7.1247 | 7.1038 | 4.6729 | 4.6898 | 4.6696 | 4.643 | 4.6604 | 4.6644 | 4.6663 | 4.6658 | 4.6401 | 3.4389 | 3.4429 | 3.413 | 3.4068 | 3.4282 | 3.4101 | 4.65 | 4.6654 | 4.6499 | 4.6454 | 4.64 | 4.6399 | 4.6482 | 4.6539 | 4.6569 | 7.1518 | 7.1469 | 7.1342 | 7.1252 | 7.1355 | 7.1274 | 7.1266 | 10.0062 | 10.0071 | 10.0166 | 10.0075 | 10.0038 | 10.0029 | 9.9916 | 9.9888 | 10.6247 | 10.6061 | 10.6064 | 10.039 | 9.9977 | 9.991 | 9.8381 | 9.7982 | 9.7707 | 10.6043 | 10.6306 | 10.6071 | 7.1227 | 7.1257 | 7.1604 | 7.1212 | 7.1159 | 7.1106 | 4.6314 | 4.6529 | 4.6467 | 3.4158 | 3.4246 | 3.4357 | 3.4663 | 3.4242 | 7.1153 | 7.1052 | 7.1191 | 4.6406 | 4.6401 | 4.6475 | 4.6635 | 4.6534 | 4.641 | 4.6386 | 4.826 | 4.8345 | 4.8304 | 3.5019 | 3.4841 | 3.4602 | 3.4404 | 9.9597 | 10.0097 | 10.0188 | 10.0064 | 10.0234 | 9.9958 | 9.9765 | 9.8174 | 9.8236 | 9.8151 | 9.9817 | 9.9969 | 9.9719 | 9.9742 | 9.8485 | 9.882 | 9.8562 | 9.7799 | 10.6135 | 10.6049 | 10.6251 | 10.0097 | 9.9586 | 9.9743 | 9.8113 | 9.7791 | 9.7913 | 10.0376 | 9.9698 | 9.9987 | 4.6848 | 4.685 | 4.6419 | 10.6526 | 10.6554 | 10.6371 | 9.8395 | 9.8161 | 9.8103 | 9.9936 | 9.9923 | 9.993 | 9.9799 | 9.961 | 9.9549 | 4.6872 | 4.6934 | 4.646 | 4.6861 | 4.6506 | 4.6807 | 4.6435 | 4.6232 | 4.6393 | 3.4204 | 3.4206 | 3.402 | 3.4432 | 3.4334 | 3.4253 | 7.1431 | 7.0936 | 7.0933 | 7.1046 | 7.1146 | 7.0838 | 10.6654 | 10.6339 | 10.6672 | 10.0387 | 10.0435 | 10.0101 | 9.855 | 9.7899 | 9.8247 | 10.0653 | 10.0199 | 9.981 | 4.6385 | 4.6942 | 4.6399 | 9.8312 | 9.84 | 9.835 | 10.031 | 10.0718 | 10.0894 | 4.6551 | 4.6426 | 4.6558 | 3.4712 | 3.4664 | 3.4511 | 3.4058 | 3.4959 | 3.497 | 3.4748 | 3.4482 | 3.4343 | 4.665 | 4.6534 | 4.6313 | 4.6709 | 4.6543 | 4.6565 | 7.1534 | 7.1401 | 7.0739 | 7.1211 | 7.1089 | 7.1 | 10.6479 | 10.5811 | 10.5878 | 10.6034 | 10.6056 | 10.575 | 9.795 | 9.7549 | 9.7986 | 9.7784 | 9.7482 | 9.7606 | 9.9638 | 9.9517 | 9.9631 | 10.0328 | 10.0404 | 10.0414 | 9.9857 | 10.0337 | 9.9871 | 4.6458 | 4.6378 | 4.6427 | 4.6559 | 4.6542 | 4.6356
120
121 | Discharge side partial condenser Pressure
122
123 | Oil Circuit
124 | Oil pressure pre filter | BarA | 1.2158 | 1.2164 | 1.2023 | 1.2079 | 1.2044 | 1.1998 | 1.2012 | 1.1976 | 1.2079 | 1.204 | 1.1869 | 1.1732 | 1.2083 | 1.209 | 1.2032 | 1.182 | 1.1908 | 1.1945 | 1.1816 | 1.1712 | 1.1769 | 1.1667 | 1.1556 | 1.1686 | 1.1584 | 1.163 | 1.1547 | 1.1606 | 1.1532 | 1.1561 | 1.1476 | 1.1666 | 1.1465 | 1.143 | 1.1435 | 1.1466 | 1.1243 | 1.1309 | 1.1396 | 1.1247 | 1.1212 | 1.117 | 1.1181 | 1.1227 | 1.1094 | 1.082 | 1.0847 | 1.0887 | 1.0733 | 1.0728 | 1.0741 | 1.0651 | 1.0669 | 1.0699 | 0.91052 | 0.93129 | 0.92282 | 0.91516 | 0.92679 | 0.92836 | 0.92679 | 0.93817 | 0.92998 | 0.8985 | 0.91869 | 0.91141 | 0.90095 | 0.91709 | 0.91281 | 0.89994 | 0.9025 | 0.9261 | 0.93016 | 0.92952 | 0.92121 | 0.91657 | 0.91577 | 0.93264 | 0.92574 | 0.91022 | 0.91568 | 0.90625 | 0.91928 | 0.90763 | 0.90292 | 0.89394 | 0.90489 | 0.90279 | 0.9189 | 0.92286 | 0.91737 | 0.91588 | 0.9168 | 0.9129 | 0.91852 | 0.90519 | 0.91281 | 0.91609 | 0.88559 | 0.88498 | 0.88389 | 0.88176 | 0.8919 | 0.87614 | 0.87399 | 0.87985 | 0.6283 | 0.62624 | 0.62551 | 0.60476 | 0.61187 | 0.61688 | 0.61235 | 0.61089 | 0.60354 | 0.6105 | 0.59755 | 0.60622 | 0.59709 | 0.59932 | 0.6013 | 1.3153 | 1.311 | 1.3154 | 1.3099 | 1.3001 | 1.3141 | 1.2917 | 1.2968 | 1.294 | 1.2985 | 1.2853 | 1.3012 | 1.2703 | 1.2699 | 1.2669 | 1.4928 | 1.4956 | 1.4845 | 1.4847 | 1.493 | 1.4872 | 1.4892 | 1.4912 | 1.4955 | 1.5056 | 1.4967 | 1.4897 | 1.4862 | 1.4874 | 1.4873 | 1.4798 | 1.4831 | 1.4824 | 1.4499 | 1.4513 | 1.4425 | 1.4483 | 1.4403 | 1.4353 | 1.4318 | 1.4318 | 1.4294 | 1.35 | 1.3615 | 1.3581 | 1.3264 | 1.3225 | 1.3178 | 1.6148 | 1.6174 | 1.6154 | 1.5892 | 1.589 | 1.582 | 4.0568 | 4.0516 | 4.0521 | 2.4468 | 2.4588 | 2.4511 | 2.4493 | 2.4499 | 2.447 | 2.4552 | 2.4475 | 2.4579 | 2.4459 | 2.4449 | 2.4509 | 2.4403 | 2.4397 | 2.436 | 2.4105 | 2.4127 | 2.4056 | 2.4059 | 2.4058 | 2.4018 | 2.3665 | 2.367 | 2.3636 | 2.3636 | 2.3558 | 2.346 | 2.2395 | 2.2313 | 2.2325 | 2.2286 | 2.2207 | 2.22 | 2.208 | 2.2137 | 2.201 | 2.1969 | 2.2023 | 2.1864 | 2.1819 | 2.1829 | 2.1841 | 2.1329 | 2.1307 | 2.1369 | 2.1181 | 2.1082 | 2.1152
125 | Oil pressure out filter | BarA | 10.3318 | 10.3334 | 10.358 | 10.3154 | 10.3145 | 10.286 | 8.2295 | 8.2504 | 8.2258 | 8.1367 | 8.1735 | 8.1776 | 8.2004 | 8.1419 | 8.129 | 7.0726 | 7.1045 | 7.0104 | 7.0514 | 7.0848 | 7.0579 | 8.2123 | 8.23 | 8.219 | 8.2035 | 8.2064 | 8.2146 | 8.1952 | 8.1869 | 8.2162 | 10.4047 | 10.3885 | 10.3603 | 10.3393 | 10.3528 | 10.3372 | 10.338 | 12.9722 | 12.9819 | 12.9745 | 12.9804 | 12.9856 | 12.9718 | 12.9867 | 12.9601 | 13.3032 | 13.2621 | 13.2544 | 13.002 | 12.9624 | 12.9438 | 12.7952 | 12.7402 | 12.7233 | 13.2001 | 13.2259 | 13.2142 | 10.3281 | 10.3341 | 10.3626 | 10.3341 | 10.3232 | 10.3246 | 8.203 | 8.237 | 8.2253 | 7.0717 | 7.0913 | 7.118 | 7.1549 | 7.1006 | 10.3118 | 10.2989 | 10.3176 | 8.2258 | 8.2302 | 8.2305 | 8.2644 | 8.2589 | 8.2439 | 8.2434 | 8.1861 | 8.1903 | 8.1908 | 7.1299 | 7.1645 | 7.1438 | 7.1282 | 12.8459 | 12.9072 | 12.9125 | 12.9008 | 12.9519 | 12.928 | 12.9337 | 12.729 | 12.7487 | 12.743 | 12.8739 | 12.915 | 12.8684 | 12.8634 | 12.761 | 12.7849 | 12.7565 | 12.6899 | 13.2905 | 13.3129 | 13.3063 | 13.1136 | 13.0541 | 13.0623 | 12.857 | 12.8454 | 12.8592 | 13.122 | 13.0064 | 13.0623 | 8.3176 | 8.3149 | 8.2616 | 13.3269 | 13.327 | 13.3208 | 12.8922 | 12.8451 | 12.8421 | 12.9918 | 13.0278 | 13.0137 | 12.9628 | 12.9271 | 12.9294 | 8.2856 | 8.2992 | 8.2471 | 8.3406 | 8.3013 | 8.3234 | 8.296 | 8.2667 | 8.2858 | 7.1031 | 7.0863 | 7.0961 | 7.0882 | 7.1131 | 7.1066 | 10.4289 | 10.3936 | 10.377 | 10.3956 | 10.3988 | 10.3812 | 13.378 | 13.3579 | 13.3662 | 13.1 | 13.0781 | 13.0447 | 12.9051 | 12.8445 | 12.8643 | 13.0584 | 12.9766 | 12.9731 | 8.2752 | 8.3348 | 8.2806 | 12.7796 | 12.7804 | 12.7777 | 12.9636 | 13.0022 | 13.0159 | 8.2458 | 8.2289 | 8.2433 | 7.1369 | 7.1263 | 7.1248 | 7.0997 | 7.1183 | 7.122 | 7.1223 | 7.0915 | 7.0643 | 8.2881 | 8.2663 | 8.2497 | 8.2887 | 8.2628 | 8.2697 | 10.4 | 10.3931 | 10.3301 | 10.3715 | 10.3506 | 10.3332 | 13.2983 | 13.2425 | 13.2418 | 13.276 | 13.2646 | 13.2303 | 12.8073 | 12.783 | 12.8164 | 12.7797 | 12.7617 | 12.7901 | 12.9727 | 12.9396 | 12.9616 | 13.0083 | 13.0401 | 13.0239 | 12.9331 | 12.9792 | 12.9383 | 8.2442 | 8.243 | 8.2555 | 8.2732 | 8.2567 | 8.2453
126 | Oil filter DP |  | -9.116 | -9.1171 | -9.1557 | -9.1075 | -9.1101 | -9.0862 | -7.0283 | -7.0528 | -7.0178 | -6.9328 | -6.9867 | -7.0045 | -6.9921 | -6.9329 | -6.9258 | -5.8906 | -5.9137 | -5.8159 | -5.8698 | -5.9136 | -5.8811 | -7.0457 | -7.0744 | -7.0504 | -7.0451 | -7.0434 | -7.06 | -7.0346 | -7.0338 | -7.0601 | -9.257 | -9.2219 | -9.2137 | -9.1963 | -9.2093 | -9.1906 | -9.2137 | -11.8412 | -11.8423 | -11.8498 | -11.8592 | -11.8685 | -11.8537 | -11.8641 | -11.8507 | -12.2212 | -12.1774 | -12.1657 | -11.9287 | -11.8895 | -11.8697 | -11.7301 | -11.6733 | -11.6534 | -12.2896 | -12.2947 | -12.2914 | -9.4129 | -9.4073 | -9.4342 | -9.4073 | -9.3851 | -9.3947 | -7.3045 | -7.3183 | -7.3139 | -6.1707 | -6.1742 | -6.2051 | -6.255 | -6.1981 | -9.3857 | -9.3688 | -9.3881 | -7.3046 | -7.3136 | -7.3147 | -7.3317 | -7.3332 | -7.3337 | -7.3278 | -7.2798 | -7.2711 | -7.2832 | -6.2269 | -6.2706 | -6.2389 | -6.2254 | -11.927 | -11.9843 | -11.9951 | -11.9849 | -12.0351 | -12.0151 | -12.0152 | -11.8238 | -11.8359 | -11.8269 | -11.9883 | -12.03 | -11.9846 | -11.9817 | -11.8691 | -11.9088 | -11.8825 | -11.8101 | -12.6622 | -12.6867 | -12.6807 | -12.5088 | -12.4423 | -12.4454 | -12.2447 | -12.2345 | -12.2557 | -12.5115 | -12.4089 | -12.456 | -7.7205 | -7.7156 | -7.6603 | -12.0116 | -12.016 | -12.0055 | -11.5823 | -11.545 | -11.5281 | -11.7001 | -11.731 | -11.7197 | -11.6643 | -11.6418 | -11.6282 | -7.0153 | -7.0292 | -6.9802 | -6.8478 | -6.8056 | -6.839 | -6.8113 | -6.7737 | -6.7986 | -5.6139 | -5.5951 | -5.6005 | -5.5827 | -5.6164 | -5.6168 | -8.9427 | -8.9062 | -8.8897 | -8.9158 | -8.9157 | -8.8987 | -11.9281 | -11.9067 | -11.9237 | -11.6517 | -11.6378 | -11.6095 | -11.4733 | -11.4127 | -11.4349 | -11.7085 | -11.6151 | -11.615 | -6.9488 | -7.0123 | -6.9628 | -11.1649 | -11.163 | -11.1623 | -11.3744 | -11.4133 | -11.434 | -4.189 | -4.1773 | -4.1911 | -4.6901 | -4.6675 | -4.6737 | -4.6503 | -4.6684 | -4.675 | -4.667 | -4.644 | -4.6063 | -5.8422 | -5.8214 | -5.7988 | -5.8484 | -5.8231 | -5.8337 | -7.9895 | -7.9804 | -7.9244 | -7.9656 | -7.9448 | -7.9314 | -10.9318 | -10.8755 | -10.8783 | -10.9124 | -10.9089 | -10.8843 | -10.5678 | -10.5517 | -10.5839 | -10.5511 | -10.541 | -10.5701 | -10.7647 | -10.7259 | -10.7606 | -10.8114 | -10.8378 | -10.8375 | -10.7512 | -10.7963 | -10.7542 | -6.1113 | -6.1124 | -6.1186 | -6.1551 | -6.1484 | -6.1301
127 | High Oil Filter DP warning
128 | Oil orifice plate Temp | ºC | 31.7175 | 31.8898 | 31.898 | 30.4307 | 30.1481 | 30.0147 | 24.8227 | 24.7174 | 24.3974 | 23.3593 | 23.0792 | 22.7127 | 22.251 | 22.0818 | 22.005 | 19.4261 | 19.5224 | 19.6483 | 18.59 | 18.1689 | 17.5883 | 26.1989 | 26.0528 | 25.8626 | 26.2855 | 26.4289 | 26.5404 | 26.657 | 26.7897 | 27.0011 | 33.3966 | 33.4712 | 33.4535 | 32.9174 | 32.8211 | 32.6756 | 37.2602 | 41.3436 | 41.3477 | 41.2798 | 40.9855 | 40.976 | 40.9601 | 40.6978 | 40.1321 | 36.1842 | 35.2439 | 34.6642 | 26.6952 | 25.6215 | 24.4677 | 21.4709 | 19.9685 | 18.9235 | 41.7329 | 41.6097 | 41.5205 | 32.3824 | 32.2807 | 32.2552 | 31.3883 | 31.2228 | 31.1445 | 24.9212 | 25.064 | 25.1768 | 16.5444 | 16.4665 | 16.4009 | 16.1617 | 16.1241 | 30.5172 | 30.4709 | 30.8901 | 24.9111 | 24.9004 | 24.893 | 24.5651 | 24.7244 | 24.6987 | 24.6131 | 23.3695 | 23.2757 | 23.0251 | 18.9694 | 18.8393 | 18.7843 | 18.8262 | 43.0611 | 43.0568 | 42.9161 | 42.9186 | 43.1771 | 43.3292 | 43.3649 | 43.3368 | 42.8804 | 41.2072 | 36.5552 | 36.3188 | 35.7905 | 35.438 | 34.4068 | 33.7584 | 33.1812 | 32.4522 | 41.4939 | 41.2797 | 40.9057 | 38.6219 | 38.6503 | 38.6909 | 38.6359 | 38.4659 | 38.206 | 34.4619 | 33.2104 | 32.5343 | 18.0675 | 17.9035 | 17.738 | 36.3144 | 35.6583 | 35.0687 | 30.0558 | 29.2215 | 28.3415 | 22.3259 | 21.3972 | 20.8953 | 19.6278 | 18.9572 | 18.5365 | 14.9461 | 14.8862 | 14.8184 | 22.6244 | 22.443 | 22.7439 | 20.505 | 20.2009 | 19.8564 | 19.7192 | 19.7019 | 19.6793 | 19.5719 | 19.5581 | 19.5728 | 30.8866 | 30.818 | 30.7885 | 30.2571 | 30.4709 | 30.2027 | 40.8035 | 40.2832 | 40.2979 | 38.1685 | 37.8408 | 37.385 | 36.5859 | 36.095 | 35.3836 | 29.3898 | 28.8142 | 27.8532 | 16.9053 | 16.8412 | 16.8044 | 39.3221 | 39.1511 | 38.9259 | 37.5414 | 36.5293 | 35.4607 | 17.2559 | 17.1959 | 17.1106 | 21.8564 | 21.865 | 21.9015 | 21.9321 | 21.9093 | 21.8952 | 21.8224 | 21.737 | 21.6601 | 22.3665 | 22.1738 | 21.7896 | 25.669 | 25.6817 | 25.6991 | 28.5533 | 28.2263 | 27.7281 | 25.2304 | 24.4599 | 23.9154 | 42.0782 | 41.9855 | 41.899 | 41.0498 | 40.7095 | 39.7962 | 40.2775 | 40.3258 | 40.3212 | 40.6234 | 40.6384 | 40.4532 | 39.8324 | 39.6299 | 39.3119 | 38.8758 | 38.7321 | 38.2855 | 34.7077 | 33.9007 | 33.1879 | 17.2199 | 17.1337 | 17.0577 | 16.8681 | 16.7465 | 16.6563
129 | Oil orifice plate Pressure | BarA | 10.3318 | 10.3334 | 10.358 | 10.3154 | 10.3145 | 10.286 | 8.2295 | 8.2504 | 8.2258 | 8.1367 | 8.1735 | 8.1776 | 8.2004 | 8.1419 | 8.129 | 7.0726 | 7.1045 | 7.0104 | 7.0514 | 7.0848 | 7.0579 | 8.2123 | 8.23 | 8.219 | 8.2035 | 8.2064 | 8.2146 | 8.1952 | 8.1869 | 8.2162 | 10.4047 | 10.3885 | 10.3603 | 10.3393 | 10.3528 | 10.3372 | 10.338 | 12.9722 | 12.9819 | 12.9745 | 12.9804 | 12.9856 | 12.9718 | 12.9867 | 12.9601 | 13.3032 | 13.2621 | 13.2544 | 13.002 | 12.9624 | 12.9438 | 12.7952 | 12.7402 | 12.7233 | 13.2001 | 13.2259 | 13.2142 | 10.3281 | 10.3341 | 10.3626 | 10.3341 | 10.3232 | 10.3246 | 8.203 | 8.237 | 8.2253 | 7.0717 | 7.0913 | 7.118 | 7.1549 | 7.1006 | 10.3118 | 10.2989 | 10.3176 | 8.2258 | 8.2302 | 8.2305 | 8.2644 | 8.2589 | 8.2439 | 8.2434 | 8.1861 | 8.1903 | 8.1908 | 7.1299 | 7.1645 | 7.1438 | 7.1282 | 12.8459 | 12.9072 | 12.9125 | 12.9008 | 12.9519 | 12.928 | 12.9337 | 12.729 | 12.7487 | 12.743 | 12.8739 | 12.915 | 12.8684 | 12.8634 | 12.761 | 12.7849 | 12.7565 | 12.6899 | 13.2905 | 13.3129 | 13.3063 | 13.1136 | 13.0541 | 13.0623 | 12.857 | 12.8454 | 12.8592 | 13.122 | 13.0064 | 13.0623 | 8.3176 | 8.3149 | 8.2616 | 13.3269 | 13.327 | 13.3208 | 12.8922 | 12.8451 | 12.8421 | 12.9918 | 13.0278 | 13.0137 | 12.9628 | 12.9271 | 12.9294 | 8.2856 | 8.2992 | 8.2471 | 8.3406 | 8.3013 | 8.3234 | 8.296 | 8.2667 | 8.2858 | 7.1031 | 7.0863 | 7.0961 | 7.0882 | 7.1131 | 7.1066 | 10.4289 | 10.3936 | 10.377 | 10.3956 | 10.3988 | 10.3812 | 13.378 | 13.3579 | 13.3662 | 13.1 | 13.0781 | 13.0447 | 12.9051 | 12.8445 | 12.8643 | 13.0584 | 12.9766 | 12.9731 | 8.2752 | 8.3348 | 8.2806 | 12.7796 | 12.7804 | 12.7777 | 12.9636 | 13.0022 | 13.0159 | 8.2458 | 8.2289 | 8.2433 | 7.1369 | 7.1263 | 7.1248 | 7.0997 | 7.1183 | 7.122 | 7.1223 | 7.0915 | 7.0643 | 8.2881 | 8.2663 | 8.2497 | 8.2887 | 8.2628 | 8.2697 | 10.4 | 10.3931 | 10.3301 | 10.3715 | 10.3506 | 10.3332 | 13.2983 | 13.2425 | 13.2418 | 13.276 | 13.2646 | 13.2303 | 12.8073 | 12.783 | 12.8164 | 12.7797 | 12.7617 | 12.7901 | 12.9727 | 12.9396 | 12.9616 | 13.0083 | 13.0401 | 13.0239 | 12.9331 | 12.9792 | 12.9383 | 8.2442 | 8.243 | 8.2555 | 8.2732 | 8.2567 | 8.2453
130 | Oil orifice plate DP | Bar | -0.003964 | -0.004101 | -0.00406 | -0.004015 | -0.003903 | -0.003871 | -0.003902 | -0.004061 | -0.004073 | -0.003981 | -0.00408 | -0.003983 | -0.003647 | -0.003697 | -0.003797 | -0.002994 | -0.003814 | -0.003802 | -0.003855 | -0.003614 | -0.003618 | -0.003997 | -0.004024 | -0.004103 | -0.004089 | -0.004088 | -0.004075 | -0.0041 | -0.004095 | -0.004094 | -0.004049 | -0.003982 | -0.003946 | -0.004015 | -0.004097 | -0.003977 | -0.004006 | -0.003866 | -0.003883 | -0.003928 | -0.004047 | -0.004055 | -0.004141 | -0.00386 | -0.003867 | -0.003881 | -0.003756 | -0.003929 | -0.003617 | -0.003612 | -0.003509 | -0.003567 | -0.003456 | -0.003492 | -0.003926 | -0.004055 | -0.003996 | -0.003848 | -0.003888 | -0.003694 | -0.003799 | -0.003816 | -0.003851 | -0.003693 | -0.003756 | -0.003719 | -0.00363 | -0.003548 | -0.003597 | -0.003629 | -0.003566 | -0.00408 | -0.003829 | -0.004061 | -0.003951 | -0.003765 | -0.003781 | -0.003735 | -0.003795 | -0.00378 | -0.003838 | -0.003707 | -0.003752 | -0.003824 | -0.003608 | -0.003602 | -0.003634 | -0.003554 | -0.003822 | -0.00383 | -0.003744 | -0.003837 | -0.003792 | -0.003814 | -0.003814 | -0.003721 | -0.003794 | -0.003723 | -0.004021 | -0.00405 | -0.003947 | -0.003973 | -0.003955 | -0.004024 | -0.004003 | -0.004008 | -0.003798 | -0.003946 | -0.003973 | -0.003882 | -0.00386 | -0.003891 | -0.003911 | -0.003874 | -0.003747 | -0.003879 | -0.003868 | -0.003896 | -0.003598 | -0.003583 | -0.00359 | -0.003945 | -0.003954 | -0.00393 | -0.003865 | -0.003909 | -0.003793 | -0.003898 | -0.003821 | -0.003856 | -0.003925 | -0.003861 | -0.003746 | -0.00361 | -0.003639 | -0.003635 | -0.007724 | -0.007803 | -0.007699 | -0.007629 | -0.007555 | -0.007752 | -0.008664 | -0.008714 | -0.009337 | -0.008703 | -0.009099 | -0.009209 | -0.006575 | -0.006665 | -0.006587 | -0.006335 | -0.006317 | -0.0062 | -0.005584 | -0.005637 | -0.005542 | -0.00569 | -0.005617 | -0.005581 | -0.005621 | -0.005635 | -0.005471 | -0.005903 | -0.005926 | -0.005913 | -0.008688 | -0.008748 | -0.008667 | -0.004154 | -0.00401 | -0.00405 | -0.00409 | -0.004014 | -0.004035 | -0.003991 | -0.003866 | -0.003895 | -0.00409 | -0.003946 | -0.003943 | -0.003924 | -0.004056 | -0.003879 | -0.003944 | -0.003947 | -0.004053 | -0.003711 | -0.003814 | -0.003733 | -0.00389 | -0.004002 | -0.00384 | -0.003757 | -0.003752 | -0.0037 | -0.003599 | -0.003552 | -0.003609 | -0.004009 | -0.003989 | -0.004049 | -0.004019 | -0.00402 | -0.00391 | -0.004008 | -0.004052 | -0.003984 | -0.004041 | -0.003899 | -0.00401 | -0.003957 | -0.00396 | -0.004041 | -0.00393 | -0.003876 | -0.003954 | -0.003941 | -0.00391 | -0.003889 | -0.003745 | -0.003745 | -0.003765 | -0.003677 | -0.003625 | -0.003648
131 | Oil Specific Volume | m3/kg | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985
132 | oil orifice Plate pipe dia | m | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894
133 | oil orifice plate orifice dia | m | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152
134 | oil orifice plate Gamma (cp/cv) | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
135 | oil flow Viscosity | Pa.s | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125
136 | Oil orifice plate vol flow | m^3/hr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
137 | Oil Density (manual input) | kg/m3 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000
138 | Oil orifice plate mass flow | kg/s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
139
140 | Economiser
141 | Econ on/off |  | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | econ | econ | econ | econ | econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | econ | econ | econ | econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | econ | econ | econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | econ | econ | econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | econ | econ | econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | econ | econ | econ | non econ | non econ | non econ | non econ | non econ | non econ
142 | Econ flow meter temp | ºC | 20.1535 | 20.0278 | 19.9371 | 19.5368 | 19.47 | 19.3929 | 18.4614 | 18.4495 | 18.3912 | 18.23 | 18.1992 | 18.1358 | 18.0441 | 18.0096 | 17.9529 | 17.222 | 17.1901 | 17.1633 | 16.6275 | 16.5101 | 16.3762 | 19.8748 | 19.8541 | 19.9038 | 19.9711 | 20.0154 | 20.0184 | 20.1064 | 20.165 | 20.1863 | 20.5085 | 20.5206 | 20.496 | 20.4816 | 20.4876 | 20.4556 | 20.5798 | 20.4911 | 20.4617 | 20.4527 | 20.314 | 20.3134 | 20.2445 | 20.1679 | 20.0281 | 18.6473 | 18.5668 | 18.421 | 17.626 | 17.5138 | 17.3988 | 17.1151 | 16.9485 | 16.8119 | 20.4248 | 20.3386 | 20.2922 | 19.1581 | 19.1341 | 19.0917 | 18.8376 | 18.791 | 18.7583 | 17.6398 | 17.6151 | 17.574 | 16.454 | 16.4191 | 16.3969 | 16.249 | 16.2016 | 19.3667 | 19.3183 | 19.2715 | 18.293 | 18.2607 | 18.2461 | 18.0021 | 17.8893 | 17.8928 | 17.8683 | 17.2925 | 17.2638 | 17.2338 | 16.4118 | 16.3593 | 16.3619 | 16.3501 | 22.7509 | 22.6864 | 22.669 | 22.6609 | 22.259 | 22.1419 | 22.1063 | 21.5907 | 21.4975 | 21.2153 | 22.2312 | 22.1809 | 22.1396 | 22.0743 | 22.0051 | 21.9113 | 21.866 | 21.7742 | 20.3673 | 20.2953 | 20.2134 | 19.6299 | 19.558 | 19.4647 | 19.3563 | 19.2454 | 19.1962 | 18.7113 | 18.5413 | 18.3979 | 16.5204 | 16.4726 | 16.4283 | 20.0736 | 19.9616 | 19.8733 | 19.3902 | 19.3205 | 19.2398 | 18.6629 | 18.5668 | 18.5253 | 18.3186 | 18.1914 | 18.0475 | 15.3278 | 15.2785 | 15.1971 | 16.9871 | 16.9418 | 16.845 | 16.3478 | 16.2808 | 16.2235 | 17.9042 | 17.9047 | 17.9032 | 17.8792 | 17.8524 | 17.8293 | 18.7127 | 18.6337 | 18.6054 | 18.1197 | 18.0648 | 18.0132 | 19.8962 | 19.6397 | 19.476 | 19.0832 | 19.0016 | 18.8722 | 18.5714 | 18.4379 | 18.2552 | 19.1342 | 19.1011 | 18.9822 | 17.1027 | 17.045 | 16.9975 | 19.8261 | 19.7168 | 19.6358 | 19.3129 | 19.2028 | 19.0622 | 18.015 | 17.9474 | 17.8708 | 18.6462 | 18.638 | 18.6115 | 18.6008 | 18.601 | 18.5866 | 18.5635 | 18.5834 | 18.5627 | 18.4728 | 18.4249 | 18.4058 | 18.5879 | 18.5617 | 18.5726 | 17.9043 | 17.8052 | 17.7106 | 17.1186 | 17.0154 | 16.8996 | 21.1258 | 21.0824 | 21.0178 | 20.8657 | 20.7791 | 20.615 | 19.804 | 19.7397 | 19.6642 | 19.5748 | 19.4892 | 19.4362 | 19.2312 | 19.1669 | 19.1296 | 18.9947 | 18.9028 | 18.8255 | 18.5698 | 18.4644 | 18.372 | 16.6161 | 16.5755 | 16.5427 | 16.4501 | 16.391 | 16.3402
143 | Econ flow meter Pressure | BarA | 8.4122 | 8.3863 | 8.3756 | 8.2964 | 8.2792 | 8.2753 | 8.102 | 8.0947 | 8.0819 | 8.0613 | 8.0515 | 8.0407 | 8.0219 | 8.0117 | 8.0032 | 7.8814 | 7.8635 | 7.8615 | 7.7608 | 7.7299 | 7.7267 | 8.3739 | 8.3785 | 8.3743 | 8.3887 | 8.3909 | 8.3951 | 8.4105 | 8.4154 | 8.4131 | 8.4665 | 8.4716 | 8.4632 | 8.4403 | 8.4471 | 8.4529 | 8.4622 | 8.437 | 8.4356 | 8.4334 | 8.4098 | 8.4042 | 8.3926 | 8.3812 | 8.3533 | 8.088 | 8.0736 | 8.0436 | 7.8913 | 7.8766 | 7.8545 | 7.7996 | 7.7697 | 7.7737 | 8.4721 | 8.4522 | 8.4436 | 8.234 | 8.2236 | 8.2227 | 8.1699 | 8.1704 | 8.1603 | 7.9611 | 7.9505 | 7.9479 | 7.7678 | 7.7624 | 7.7525 | 7.7264 | 7.718 | 8.3037 | 8.295 | 8.2789 | 8.0887 | 8.0956 | 8.0862 | 8.0374 | 8.024 | 8.0136 | 8.0114 | 7.8993 | 7.8961 | 7.8928 | 7.7666 | 7.7533 | 7.752 | 7.757 | 8.9966 | 8.9857 | 8.9795 | 8.9769 | 8.8824 | 8.8671 | 8.8562 | 8.7487 | 8.7354 | 8.6794 | 8.8807 | 8.8701 | 8.8601 | 8.8601 | 8.8366 | 8.8188 | 8.803 | 8.7805 | 8.4585 | 8.4446 | 8.4312 | 8.3059 | 8.2927 | 8.2723 | 8.2481 | 8.2316 | 8.2163 | 8.1345 | 8.0984 | 8.0683 | 7.744 | 7.7269 | 7.7258 | 8.4467 | 8.4234 | 8.4077 | 8.3 | 8.284 | 8.2754 | 8.1488 | 8.1331 | 8.1158 | 8.0749 | 8.0532 | 8.0264 | 7.5594 | 7.5504 | 7.5345 | 7.8341 | 7.8246 | 7.8102 | 7.7531 | 7.742 | 7.7261 | 8.0665 | 8.0632 | 8.0628 | 8.0669 | 8.0618 | 8.0629 | 8.1815 | 8.1701 | 8.1636 | 8.0727 | 8.0678 | 8.0516 | 8.4408 | 8.3876 | 8.3531 | 8.2698 | 8.2522 | 8.2204 | 8.1659 | 8.1342 | 8.0997 | 8.2913 | 8.2775 | 8.2599 | 7.9204 | 7.9024 | 7.8954 | 8.4482 | 8.4278 | 8.4046 | 8.3458 | 8.3168 | 8.2942 | 8.1616 | 8.1495 | 8.1422 | 8.3379 | 8.3332 | 8.3318 | 8.3273 | 8.3296 | 8.3259 | 8.322 | 8.3177 | 8.3136 | 8.2927 | 8.2925 | 8.2839 | 8.3122 | 8.3091 | 8.303 | 8.1599 | 8.14 | 8.124 | 8.0093 | 7.9911 | 7.9708 | 8.9502 | 8.9378 | 8.9224 | 8.883 | 8.8729 | 8.8346 | 8.6436 | 8.6335 | 8.6221 | 8.6043 | 8.5857 | 8.5756 | 8.5334 | 8.5211 | 8.5079 | 8.4785 | 8.4719 | 8.4505 | 8.4015 | 8.3824 | 8.363 | 8.0539 | 8.0467 | 8.0402 | 8.0186 | 8.0073 | 8.0011
144 | Econ flow meter gauge | ºC | 33.1036 | 32.9939 | 32.9486 | 32.6113 | 32.5375 | 32.5212 | 31.773 | 31.7414 | 31.6856 | 31.5957 | 31.5529 | 31.5059 | 31.4236 | 31.3787 | 31.3413 | 30.8037 | 30.724 | 30.7152 | 30.2651 | 30.1259 | 30.1117 | 32.941 | 32.9605 | 32.943 | 33.0039 | 33.0134 | 33.0309 | 33.0964 | 33.1169 | 33.1072 | 33.3326 | 33.3538 | 33.3188 | 33.2222 | 33.2509 | 33.2754 | 33.3143 | 33.2082 | 33.2022 | 33.1929 | 33.0932 | 33.0697 | 33.0203 | 32.9723 | 32.8538 | 31.7125 | 31.6497 | 31.5184 | 30.8476 | 30.7822 | 30.6841 | 30.4392 | 30.3052 | 30.3232 | 33.3559 | 33.2723 | 33.2362 | 32.344 | 32.2993 | 32.2955 | 32.0675 | 32.0698 | 32.0259 | 31.1564 | 31.1095 | 31.0982 | 30.2964 | 30.2721 | 30.2276 | 30.1104 | 30.0725 | 32.6425 | 32.6054 | 32.5363 | 31.7152 | 31.7453 | 31.7046 | 31.4915 | 31.4329 | 31.387 | 31.3774 | 30.8831 | 30.8691 | 30.8544 | 30.2913 | 30.2314 | 30.2253 | 30.2481 | 35.5125 | 35.4688 | 35.4438 | 35.4332 | 35.0513 | 34.9891 | 34.9445 | 34.5054 | 34.4509 | 34.2201 | 35.0441 | 35.0012 | 34.9607 | 34.9607 | 34.8649 | 34.7922 | 34.7278 | 34.6358 | 33.2986 | 33.2404 | 33.1838 | 32.6518 | 32.5954 | 32.5083 | 32.4043 | 32.3334 | 32.2677 | 31.9142 | 31.7574 | 31.6262 | 30.1895 | 30.1124 | 30.1077 | 33.2493 | 33.1507 | 33.0846 | 32.6266 | 32.5584 | 32.5216 | 31.9763 | 31.9083 | 31.833 | 31.6552 | 31.5604 | 31.4431 | 29.3512 | 29.3101 | 29.237 | 30.5932 | 30.5508 | 30.4864 | 30.2306 | 30.1805 | 30.1087 | 31.6187 | 31.6043 | 31.6023 | 31.6202 | 31.598 | 31.6028 | 32.1179 | 32.0684 | 32.0402 | 31.6455 | 31.6244 | 31.5535 | 33.2244 | 32.9991 | 32.853 | 32.4976 | 32.4221 | 32.2856 | 32.0504 | 31.9129 | 31.7631 | 32.5895 | 32.5303 | 32.4551 | 30.9764 | 30.8971 | 30.8659 | 33.2555 | 33.1693 | 33.0714 | 32.8218 | 32.6984 | 32.6019 | 32.0315 | 31.9796 | 31.9478 | 32.7881 | 32.768 | 32.7623 | 32.7433 | 32.7529 | 32.7371 | 32.7204 | 32.7021 | 32.6849 | 32.5954 | 32.5946 | 32.5579 | 32.6789 | 32.6656 | 32.6396 | 32.0242 | 31.9382 | 31.8689 | 31.3684 | 31.2884 | 31.199 | 35.3256 | 35.2753 | 35.2134 | 35.0534 | 35.0124 | 34.8567 | 34.0717 | 34.0302 | 33.9828 | 33.9088 | 33.8316 | 33.7894 | 33.6131 | 33.5618 | 33.5065 | 33.3829 | 33.3553 | 33.2652 | 33.0582 | 32.9772 | 32.8951 | 31.5633 | 31.5323 | 31.5038 | 31.4092 | 31.3593 | 31.3323
145 | Econ flow meter enthalpy | KJ/kg | 227.7058 | 227.5292 | 227.402 | 226.8404 | 226.7467 | 226.6386 | 225.3344 | 225.3178 | 225.2362 | 225.0109 | 224.9678 | 224.8792 | 224.751 | 224.7028 | 224.6237 | 223.6038 | 223.5592 | 223.5218 | 222.7753 | 222.6118 | 222.4256 | 227.3147 | 227.2856 | 227.3553 | 227.4498 | 227.512 | 227.5161 | 227.6397 | 227.7219 | 227.7518 | 228.2044 | 228.2214 | 228.1869 | 228.1665 | 228.175 | 228.1301 | 228.3045 | 228.1797 | 228.1385 | 228.1258 | 227.9309 | 227.9301 | 227.8333 | 227.7258 | 227.5293 | 225.594 | 225.4814 | 225.2775 | 224.1667 | 224.0102 | 223.8497 | 223.4541 | 223.2219 | 223.0318 | 228.087 | 227.9658 | 227.9006 | 226.3097 | 226.276 | 226.2166 | 225.8608 | 225.7956 | 225.7498 | 224.1866 | 224.1521 | 224.0948 | 222.5343 | 222.4857 | 222.4547 | 222.2489 | 222.183 | 226.6022 | 226.5344 | 226.4687 | 225.0991 | 225.0542 | 225.0337 | 224.6927 | 224.5352 | 224.5399 | 224.5058 | 223.7021 | 223.6621 | 223.6204 | 222.4756 | 222.4025 | 222.406 | 222.3897 | 231.3662 | 231.275 | 231.2503 | 231.2389 | 230.6711 | 230.5058 | 230.4556 | 229.7283 | 229.5969 | 229.1994 | 230.6319 | 230.5608 | 230.5025 | 230.4105 | 230.3128 | 230.1803 | 230.1165 | 229.987 | 228.0061 | 227.905 | 227.79 | 226.9708 | 226.87 | 226.7391 | 226.5871 | 226.4317 | 226.3628 | 225.6838 | 225.4461 | 225.2454 | 222.6262 | 222.5596 | 222.498 | 227.594 | 227.4368 | 227.3129 | 226.6352 | 226.5374 | 226.4243 | 225.6164 | 225.482 | 225.4238 | 225.1347 | 224.957 | 224.7559 | 220.9689 | 220.9004 | 220.7874 | 223.2763 | 223.2132 | 223.0783 | 222.3865 | 222.2934 | 222.2135 | 224.5565 | 224.5571 | 224.5549 | 224.5216 | 224.4841 | 224.4519 | 225.6863 | 225.5758 | 225.5363 | 224.8571 | 224.7805 | 224.7083 | 227.3453 | 226.9852 | 226.7557 | 226.2053 | 226.0909 | 225.9096 | 225.4887 | 225.3019 | 225.0465 | 226.2767 | 226.2303 | 226.0638 | 223.4381 | 223.3577 | 223.2916 | 227.247 | 227.0936 | 226.98 | 226.5273 | 226.373 | 226.1761 | 224.7119 | 224.6175 | 224.5107 | 225.595 | 225.5835 | 225.5465 | 225.5315 | 225.5317 | 225.5116 | 225.4793 | 225.5071 | 225.478 | 225.3522 | 225.2854 | 225.2587 | 225.5133 | 225.4767 | 225.4918 | 224.5576 | 224.4192 | 224.2871 | 223.4613 | 223.3175 | 223.1562 | 229.0757 | 229.0146 | 228.9236 | 228.7095 | 228.5878 | 228.357 | 227.2178 | 227.1276 | 227.0217 | 226.8965 | 226.7763 | 226.702 | 226.4148 | 226.3247 | 226.2724 | 226.0834 | 225.9549 | 225.8467 | 225.4889 | 225.3414 | 225.2122 | 222.7629 | 222.7064 | 222.6608 | 222.5318 | 222.4496 | 222.3789
146 | Econ flow meter specific Vol | m3/kg | 0.0008155 | 0.0008152 | 0.00081498 | 0.00081401 | 0.00081386 | 0.00081367 | 0.00081145 | 0.00081142 | 0.00081128 | 0.0008109 | 0.00081083 | 0.00081068 | 0.00081046 | 0.00081038 | 0.00081025 | 0.00080853 | 0.00080846 | 0.00080839 | 0.00080715 | 0.00080688 | 0.00080656 | 0.00081482 | 0.00081477 | 0.00081489 | 0.00081506 | 0.00081516 | 0.00081517 | 0.00081538 | 0.00081553 | 0.00081558 | 0.00081636 | 0.00081639 | 0.00081633 | 0.00081631 | 0.00081632 | 0.00081624 | 0.00081654 | 0.00081633 | 0.00081626 | 0.00081624 | 0.0008159 | 0.0008159 | 0.00081573 | 0.00081555 | 0.00081521 | 0.00081191 | 0.00081171 | 0.00081137 | 0.0008095 | 0.00080923 | 0.00080896 | 0.0008083 | 0.00080791 | 0.00080758 | 0.00081615 | 0.00081595 | 0.00081583 | 0.0008131 | 0.00081305 | 0.00081295 | 0.00081234 | 0.00081223 | 0.00081215 | 0.00080951 | 0.00080945 | 0.00080935 | 0.00080673 | 0.00080665 | 0.0008066 | 0.00080626 | 0.00080615 | 0.00081359 | 0.00081348 | 0.00081337 | 0.00081104 | 0.00081096 | 0.00081093 | 0.00081035 | 0.00081009 | 0.0008101 | 0.00081004 | 0.00080869 | 0.00080862 | 0.00080855 | 0.00080663 | 0.00080651 | 0.00080652 | 0.00080649 | 0.00082185 | 0.00082169 | 0.00082164 | 0.00082162 | 0.00082063 | 0.00082034 | 0.00082025 | 0.00081898 | 0.00081875 | 0.00081806 | 0.00082056 | 0.00082044 | 0.00082034 | 0.00082017 | 0.00082 | 0.00081977 | 0.00081966 | 0.00081944 | 0.00081602 | 0.00081584 | 0.00081564 | 0.00081424 | 0.00081407 | 0.00081384 | 0.00081359 | 0.00081332 | 0.0008132 | 0.00081204 | 0.00081164 | 0.0008113 | 0.0008069 | 0.00080679 | 0.00080669 | 0.00081529 | 0.00081502 | 0.00081481 | 0.00081365 | 0.00081349 | 0.00081329 | 0.00081192 | 0.00081169 | 0.0008116 | 0.00081111 | 0.00081081 | 0.00081047 | 0.00080415 | 0.00080403 | 0.00080385 | 0.00080798 | 0.00080788 | 0.00080765 | 0.00080649 | 0.00080633 | 0.0008062 | 0.00081011 | 0.00081011 | 0.00081011 | 0.00081005 | 0.00080998 | 0.00080993 | 0.00081203 | 0.00081184 | 0.00081178 | 0.00081063 | 0.0008105 | 0.00081038 | 0.00081485 | 0.00081424 | 0.00081384 | 0.00081291 | 0.00081271 | 0.00081241 | 0.00081169 | 0.00081138 | 0.00081095 | 0.00081302 | 0.00081295 | 0.00081266 | 0.00080823 | 0.0008081 | 0.00080799 | 0.00081467 | 0.00081441 | 0.00081422 | 0.00081344 | 0.00081318 | 0.00081285 | 0.00081034 | 0.00081018 | 0.00081 | 0.00081181 | 0.0008118 | 0.00081173 | 0.00081171 | 0.00081171 | 0.00081167 | 0.00081162 | 0.00081167 | 0.00081162 | 0.00081141 | 0.00081129 | 0.00081125 | 0.00081168 | 0.00081162 | 0.00081165 | 0.00081008 | 0.00080984 | 0.00080962 | 0.00080824 | 0.000808 | 0.00080773 | 0.00081773 | 0.00081763 | 0.00081747 | 0.00081711 | 0.00081689 | 0.0008165 | 0.00081455 | 0.00081439 | 0.00081421 | 0.000814 | 0.00081379 | 0.00081367 | 0.00081318 | 0.00081302 | 0.00081294 | 0.00081262 | 0.00081239 | 0.00081221 | 0.00081161 | 0.00081136 | 0.00081114 | 0.00080702 | 0.00080693 | 0.00080685 | 0.00080664 | 0.00080651 | 0.00080639
147 | Econ flow meter vol Flow | m^3/hr | -0.025937 | -0.043148 | -0.031002 | -0.022691 | -0.036411 | -0.028543 | -0.029477 | -0.030018 | -0.008136 | -0.025593 | -0.025298 | -0.016643 | -0.028887 | -0.012808 | -0.012021 | -0.012168 | -0.040689 | -0.005235 | -0.012611 | -0.022937 | -0.003956 | -0.04541 | -0.021216 | -0.030412 | -0.047475 | -0.027412 | -0.035132 | -0.026035 | -0.033411 | -0.033805 | -0.033067 | -0.020429 | -0.043 | -0.031936 | -0.060654 | -0.03351 | -0.027166 | 30.7931 | 32.1068 | 29.751 | 41.5055 | 55.2093 | 43.9462 | 41.5772 | 39.9145 | -0.025396 | -0.027461 | -0.019594 | -0.021167 | -0.027068 | -0.012021 | -0.016496 | 0.008927 | -0.009169 | -0.024314 | -0.040247 | -0.038034 | -0.042902 | -0.01861 | -0.02633 | -0.035723 | -0.025347 | -0.016987 | -0.014627 | -0.006464 | -0.005874 | -0.002973 | 0.002338 | -0.005923 | -0.004497 | 0.003518 | -0.020479 | -0.025199 | -0.03705 | -0.004448 | -0.016545 | -0.022052 | -0.015955 | -0.028002 | -0.013496 | -0.018659 | -0.022888 | -0.021659 | -0.004596 | -0.004104 | -0.011529 | -0.009267 | -0.00848 | 35.002 | 29.0561 | 34.1746 | 30.6214 | -0.045016 | -0.039656 | -0.041427 | -0.031199 | -0.028789 | -0.038329 | -0.040148 | -0.047524 | -0.053769 | -0.035723 | -0.027855 | -0.059621 | -0.042509 | -0.023429 | -0.022691 | -0.033952 | -0.045016 | -0.010742 | -0.050868 | -0.024118 | -0.02515 | -0.036411 | -0.031641 | 29.5967 | 25.9915 | 29.7857 | 0.002043 | -0.012168 | -0.004104 | -0.043246 | -0.027215 | -0.03469 | -0.015512 | -0.017922 | 0.25583 | -0.023773 | -0.011234 | -0.027363 | 41.3327 | 41.3405 | 41.3113 | 0.006419 | -0.000612 | -0.008726 | -0.006267 | -0.00971 | -0.020577 | 0.008386 | 0.001404 | 0.004059 | -0.013889 | -0.00789 | -0.017135 | -0.027068 | -0.020036 | -0.004497 | -0.021413 | -0.02156 | -0.013791 | -0.009906 | -0.015414 | -0.027511 | -0.038919 | -0.013348 | -0.028543 | 1.1736 | 2.0966 | 1.7481 | -0.021511 | -0.005923 | -0.002924 | 38.8679 | 27.6776 | 27.6752 | -0.01802 | 0.004698 | -0.016004 | -0.029232 | -0.012562 | -0.021856 | -0.025347 | -0.02815 | -0.020184 | -0.014725 | 0.000617 | -0.012217 | -0.025642 | -0.021069 | -0.021167 | -0.005677 | -0.008579 | -0.015807 | -0.020479 | -0.016889 | -0.020872 | -0.02933 | -0.029822 | -0.014529 | -0.010939 | -0.014676 | -0.012808 | -0.01625 | -0.008136 | -0.018708 | 0.001797 | -0.008923 | -0.008284 | 3.3197 | 1.4097 | 1.7126 | -0.0192 | -0.024363 | -0.040689 | -0.01861 | -0.024413 | -0.023724 | -0.034985 | -0.029576 | -0.014775 | -0.033264 | -0.016102 | -0.023331 | -0.013152 | -0.026478 | -0.013398 | 41.3053 | 41.3224 | 41.3332 | 0.000666 | -0.00076 | -0.005579 | 0.002486 | -0.001793 | 0.009862
148 | Econ flow meter mass Flow | kg/s | -0.0088347 | -0.014703 | -0.010567 | -0.0077432 | -0.012427 | -0.0097443 | -0.010091 | -0.010276 | -0.0027857 | -0.008767 | -0.0086667 | -0.0057027 | -0.0099007 | -0.0043902 | -0.0041212 | -0.0041804 | -0.01398 | -0.0017988 | -0.00434 | -0.0078963 | -0.0013624 | -0.015481 | -0.0072331 | -0.010367 | -0.01618 | -0.009341 | -0.011972 | -0.0088694 | -0.01138 | -0.011514 | -0.011251 | -0.006951 | -0.014632 | -0.010867 | -0.020639 | -0.011404 | -0.0092415 | 10.4781 | 10.9261 | 10.1247 | 14.1308 | 18.7963 | 14.9648 | 14.1613 | 13.6006 | -0.0086888 | -0.0093975 | -0.0067081 | -0.0072634 | -0.0092914 | -0.0041277 | -0.005669 | 0.0030693 | -0.0031538 | -0.0082753 | -0.013702 | -0.01295 | -0.014656 | -0.0063581 | -0.0089968 | -0.012215 | -0.0086686 | -0.00581 | -0.0050192 | -0.0022182 | -0.002016 | -0.0010237 | 0.00080511 | -0.0020398 | -0.0015493 | 0.0012122 | -0.006992 | -0.0086047 | -0.012653 | -0.0015234 | -0.0056671 | -0.0075537 | -0.0054691 | -0.0096019 | -0.0046277 | -0.0063985 | -0.0078618 | -0.0074403 | -0.001579 | -0.0014133 | -0.0039708 | -0.0031917 | -0.0029207 | 11.8304 | 9.8226 | 11.5536 | 10.3526 | -0.015238 | -0.013428 | -0.014029 | -0.010582 | -0.0097672 | -0.013015 | -0.013591 | -0.01609 | -0.018207 | -0.012099 | -0.009436 | -0.020202 | -0.014406 | -0.0079421 | -0.0077242 | -0.01156 | -0.015331 | -0.0036646 | -0.017357 | -0.0082318 | -0.0085868 | -0.012436 | -0.010808 | 10.1242 | 8.8954 | 10.1982 | 0.00070331 | -0.0041894 | -0.0014132 | -0.014734 | -0.0092755 | -0.011826 | -0.0052957 | -0.0061198 | 0.087378 | -0.0081333 | -0.0038445 | -0.0093653 | 14.1551 | 14.163 | 14.1589 | 0.0022173 | -0.00021143 | -0.0030154 | -0.0021545 | -0.0033387 | -0.0070771 | 0.0028884 | 0.00048367 | 0.0013985 | -0.0047624 | -0.0027054 | -0.0058754 | -0.009282 | -0.0068712 | -0.0015423 | -0.0073249 | -0.0073769 | -0.0047191 | -0.0033945 | -0.0052828 | -0.0094301 | -0.013267 | -0.0045537 | -0.0097422 | 0.40102 | 0.7166 | 0.59769 | -0.0073615 | -0.0020278 | -0.0010016 | 13.2796 | 9.4572 | 9.4597 | -0.0061932 | 0.0016149 | -0.005502 | -0.0099672 | -0.0042846 | -0.0074564 | -0.0086556 | -0.0096158 | -0.0068976 | -0.0050476 | 0.00021154 | -0.0041896 | -0.0087739 | -0.0072093 | -0.0072434 | -0.0019427 | -0.0029359 | -0.0054096 | -0.007009 | -0.0057799 | -0.0071435 | -0.010041 | -0.010211 | -0.0049748 | -0.0037436 | -0.0050229 | -0.0043834 | -0.0055722 | -0.0027907 | -0.0064186 | 0.0006176 | -0.0030676 | -0.0028489 | 1.1277 | 0.47892 | 0.58194 | -0.0065271 | -0.0082844 | -0.013843 | -0.0063464 | -0.0083269 | -0.0080937 | -0.011939 | -0.010095 | -0.005044 | -0.011363 | -0.0055014 | -0.0079721 | -0.0044958 | -0.0090535 | -0.0045821 | 14.137 | 14.1472 | 14.1547 | 0.00022924 | -0.00026162 | -0.0019207 | 0.00085609 | -0.00061755 | 0.0033972
149 | Econ @ comp temp | ºC | 20.1535 | 20.0278 | 19.9371 | 19.5368 | 19.47 | 19.3929 | 18.4614 | 18.4495 | 18.3912 | 18.23 | 18.1992 | 18.1358 | 18.0441 | 18.0096 | 17.9529 | 17.222 | 17.1901 | 17.1633 | 16.6275 | 16.5101 | 16.3762 | 19.8748 | 19.8541 | 19.9038 | 19.9711 | 20.0154 | 20.0184 | 20.1064 | 20.165 | 20.1863 | 20.5085 | 20.5206 | 20.496 | 20.4816 | 20.4876 | 20.4556 | 20.5798 | 20.4911 | 20.4617 | 20.4527 | 20.314 | 20.3134 | 20.2445 | 20.1679 | 20.0281 | 18.6473 | 18.5668 | 18.421 | 17.626 | 17.5138 | 17.3988 | 17.1151 | 16.9485 | 16.8119 | 20.4248 | 20.3386 | 20.2922 | 19.1581 | 19.1341 | 19.0917 | 18.8376 | 18.791 | 18.7583 | 17.6398 | 17.6151 | 17.574 | 16.454 | 16.4191 | 16.3969 | 16.249 | 16.2016 | 19.3667 | 19.3183 | 19.2715 | 18.293 | 18.2607 | 18.2461 | 18.0021 | 17.8893 | 17.8928 | 17.8683 | 17.2925 | 17.2638 | 17.2338 | 16.4118 | 16.3593 | 16.3619 | 16.3501 | 22.7509 | 22.6864 | 22.669 | 22.6609 | 22.259 | 22.1419 | 22.1063 | 21.5907 | 21.4975 | 21.2153 | 22.2312 | 22.1809 | 22.1396 | 22.0743 | 22.0051 | 21.9113 | 21.866 | 21.7742 | 20.3673 | 20.2953 | 20.2134 | 19.6299 | 19.558 | 19.4647 | 19.3563 | 19.2454 | 19.1962 | 18.7113 | 18.5413 | 18.3979 | 16.5204 | 16.4726 | 16.4283 | 20.0736 | 19.9616 | 19.8733 | 19.3902 | 19.3205 | 19.2398 | 18.6629 | 18.5668 | 18.5253 | 18.3186 | 18.1914 | 18.0475 | 15.3278 | 15.2785 | 15.1971 | 16.9871 | 16.9418 | 16.845 | 16.3478 | 16.2808 | 16.2235 | 17.9042 | 17.9047 | 17.9032 | 17.8792 | 17.8524 | 17.8293 | 18.7127 | 18.6337 | 18.6054 | 18.1197 | 18.0648 | 18.0132 | 19.8962 | 19.6397 | 19.476 | 19.0832 | 19.0016 | 18.8722 | 18.5714 | 18.4379 | 18.2552 | 19.1342 | 19.1011 | 18.9822 | 17.1027 | 17.045 | 16.9975 | 19.8261 | 19.7168 | 19.6358 | 19.3129 | 19.2028 | 19.0622 | 18.015 | 17.9474 | 17.8708 | 18.6462 | 18.638 | 18.6115 | 18.6008 | 18.601 | 18.5866 | 18.5635 | 18.5834 | 18.5627 | 18.4728 | 18.4249 | 18.4058 | 18.5879 | 18.5617 | 18.5726 | 17.9043 | 17.8052 | 17.7106 | 17.1186 | 17.0154 | 16.8996 | 21.1258 | 21.0824 | 21.0178 | 20.8657 | 20.7791 | 20.615 | 19.804 | 19.7397 | 19.6642 | 19.5748 | 19.4892 | 19.4362 | 19.2312 | 19.1669 | 19.1296 | 18.9947 | 18.9028 | 18.8255 | 18.5698 | 18.4644 | 18.372 | 16.6161 | 16.5755 | 16.5427 | 16.4501 | 16.391 | 16.3402
150 | Econ @ comp Pressure | BarA | 8.4122 | 8.3863 | 8.3756 | 8.2964 | 8.2792 | 8.2753 | 8.102 | 8.0947 | 8.0819 | 8.0613 | 8.0515 | 8.0407 | 8.0219 | 8.0117 | 8.0032 | 7.8814 | 7.8635 | 7.8615 | 7.7608 | 7.7299 | 7.7267 | 8.3739 | 8.3785 | 8.3743 | 8.3887 | 8.3909 | 8.3951 | 8.4105 | 8.4154 | 8.4131 | 8.4665 | 8.4716 | 8.4632 | 8.4403 | 8.4471 | 8.4529 | 8.4622 | 8.437 | 8.4356 | 8.4334 | 8.4098 | 8.4042 | 8.3926 | 8.3812 | 8.3533 | 8.088 | 8.0736 | 8.0436 | 7.8913 | 7.8766 | 7.8545 | 7.7996 | 7.7697 | 7.7737 | 8.4721 | 8.4522 | 8.4436 | 8.234 | 8.2236 | 8.2227 | 8.1699 | 8.1704 | 8.1603 | 7.9611 | 7.9505 | 7.9479 | 7.7678 | 7.7624 | 7.7525 | 7.7264 | 7.718 | 8.3037 | 8.295 | 8.2789 | 8.0887 | 8.0956 | 8.0862 | 8.0374 | 8.024 | 8.0136 | 8.0114 | 7.8993 | 7.8961 | 7.8928 | 7.7666 | 7.7533 | 7.752 | 7.757 | 8.9966 | 8.9857 | 8.9795 | 8.9769 | 8.8824 | 8.8671 | 8.8562 | 8.7487 | 8.7354 | 8.6794 | 8.8807 | 8.8701 | 8.8601 | 8.8601 | 8.8366 | 8.8188 | 8.803 | 8.7805 | 8.4585 | 8.4446 | 8.4312 | 8.3059 | 8.2927 | 8.2723 | 8.2481 | 8.2316 | 8.2163 | 8.1345 | 8.0984 | 8.0683 | 7.744 | 7.7269 | 7.7258 | 8.4467 | 8.4234 | 8.4077 | 8.3 | 8.284 | 8.2754 | 8.1488 | 8.1331 | 8.1158 | 8.0749 | 8.0532 | 8.0264 | 7.5594 | 7.5504 | 7.5345 | 7.8341 | 7.8246 | 7.8102 | 7.7531 | 7.742 | 7.7261 | 8.0665 | 8.0632 | 8.0628 | 8.0669 | 8.0618 | 8.0629 | 8.1815 | 8.1701 | 8.1636 | 8.0727 | 8.0678 | 8.0516 | 8.4408 | 8.3876 | 8.3531 | 8.2698 | 8.2522 | 8.2204 | 8.1659 | 8.1342 | 8.0997 | 8.2913 | 8.2775 | 8.2599 | 7.9204 | 7.9024 | 7.8954 | 8.4482 | 8.4278 | 8.4046 | 8.3458 | 8.3168 | 8.2942 | 8.1616 | 8.1495 | 8.1422 | 8.3379 | 8.3332 | 8.3318 | 8.3273 | 8.3296 | 8.3259 | 8.322 | 8.3177 | 8.3136 | 8.2927 | 8.2925 | 8.2839 | 8.3122 | 8.3091 | 8.303 | 8.1599 | 8.14 | 8.124 | 8.0093 | 7.9911 | 7.9708 | 8.9502 | 8.9378 | 8.9224 | 8.883 | 8.8729 | 8.8346 | 8.6436 | 8.6335 | 8.6221 | 8.6043 | 8.5857 | 8.5756 | 8.5334 | 8.5211 | 8.5079 | 8.4785 | 8.4719 | 8.4505 | 8.4015 | 8.3824 | 8.363 | 8.0539 | 8.0467 | 8.0402 | 8.0186 | 8.0073 | 8.0011
151 | Econ @ comp SH | ºC | -12.9501 | -12.9662 | -13.0115 | -13.0745 | -13.0674 | -13.1283 | -13.3117 | -13.2919 | -13.2944 | -13.3657 | -13.3538 | -13.3701 | -13.3796 | -13.3691 | -13.3884 | -13.5817 | -13.5339 | -13.5519 | -13.6376 | -13.6158 | -13.7355 | -13.0662 | -13.1064 | -13.0392 | -13.0328 | -12.9979 | -13.0125 | -12.9901 | -12.9519 | -12.9209 | -12.8241 | -12.8332 | -12.8227 | -12.7406 | -12.7633 | -12.8198 | -12.7345 | -12.7171 | -12.7405 | -12.7402 | -12.7793 | -12.7563 | -12.7758 | -12.8044 | -12.8258 | -13.0652 | -13.0829 | -13.0974 | -13.2217 | -13.2684 | -13.2853 | -13.3241 | -13.3567 | -13.5113 | -12.9311 | -12.9337 | -12.944 | -13.1859 | -13.1652 | -13.2038 | -13.2299 | -13.2788 | -13.2676 | -13.5166 | -13.4944 | -13.5242 | -13.8423 | -13.8529 | -13.8307 | -13.8614 | -13.871 | -13.2758 | -13.2872 | -13.2648 | -13.4222 | -13.4846 | -13.4585 | -13.4894 | -13.5436 | -13.4942 | -13.5091 | -13.5907 | -13.6053 | -13.6205 | -13.8795 | -13.8721 | -13.8635 | -13.8981 | -12.7616 | -12.7823 | -12.7749 | -12.7722 | -12.7923 | -12.8472 | -12.8382 | -12.9147 | -12.9534 | -13.0048 | -12.8129 | -12.8204 | -12.8211 | -12.8864 | -12.8598 | -12.881 | -12.8617 | -12.8616 | -12.9313 | -12.9451 | -12.9704 | -13.0219 | -13.0374 | -13.0437 | -13.0481 | -13.088 | -13.0715 | -13.203 | -13.2161 | -13.2283 | -13.6691 | -13.6399 | -13.6795 | -13.1757 | -13.189 | -13.2112 | -13.2364 | -13.2379 | -13.2818 | -13.3135 | -13.3415 | -13.3077 | -13.3367 | -13.369 | -13.3956 | -14.0234 | -14.0316 | -14.04 | -13.6061 | -13.6089 | -13.6414 | -13.8828 | -13.8996 | -13.8852 | -13.7144 | -13.6996 | -13.6991 | -13.741 | -13.7457 | -13.7735 | -13.4053 | -13.4347 | -13.4347 | -13.5257 | -13.5595 | -13.5403 | -13.3281 | -13.3595 | -13.377 | -13.4144 | -13.4206 | -13.4134 | -13.479 | -13.475 | -13.5079 | -13.4553 | -13.4292 | -13.4729 | -13.8737 | -13.8521 | -13.8684 | -13.4294 | -13.4525 | -13.4356 | -13.5089 | -13.4956 | -13.5396 | -14.0166 | -14.0322 | -14.077 | -14.1419 | -14.13 | -14.1507 | -14.1424 | -14.152 | -14.1505 | -14.1569 | -14.1187 | -14.1222 | -14.1226 | -14.1697 | -14.1521 | -14.0909 | -14.1038 | -14.067 | -14.1199 | -14.1329 | -14.1583 | -14.2498 | -14.2729 | -14.2993 | -14.1998 | -14.1929 | -14.1956 | -14.1878 | -14.2333 | -14.2416 | -14.2678 | -14.2905 | -14.3187 | -14.334 | -14.3424 | -14.3533 | -14.3819 | -14.3949 | -14.3769 | -14.3882 | -14.4526 | -14.4396 | -14.4884 | -14.5129 | -14.5231 | -14.9473 | -14.9568 | -14.9611 | -14.9591 | -14.9683 | -14.9921
152 | Econ @ comp gauge | ºC | 33.1036 | 32.9939 | 32.9486 | 32.6113 | 32.5375 | 32.5212 | 31.773 | 31.7414 | 31.6856 | 31.5957 | 31.5529 | 31.5059 | 31.4236 | 31.3787 | 31.3413 | 30.8037 | 30.724 | 30.7152 | 30.2651 | 30.1259 | 30.1117 | 32.941 | 32.9605 | 32.943 | 33.0039 | 33.0134 | 33.0309 | 33.0964 | 33.1169 | 33.1072 | 33.3326 | 33.3538 | 33.3188 | 33.2222 | 33.2509 | 33.2754 | 33.3143 | 33.2082 | 33.2022 | 33.1929 | 33.0932 | 33.0697 | 33.0203 | 32.9723 | 32.8538 | 31.7125 | 31.6497 | 31.5184 | 30.8476 | 30.7822 | 30.6841 | 30.4392 | 30.3052 | 30.3232 | 33.3559 | 33.2723 | 33.2362 | 32.344 | 32.2993 | 32.2955 | 32.0675 | 32.0698 | 32.0259 | 31.1564 | 31.1095 | 31.0982 | 30.2964 | 30.2721 | 30.2276 | 30.1104 | 30.0725 | 32.6425 | 32.6054 | 32.5363 | 31.7152 | 31.7453 | 31.7046 | 31.4915 | 31.4329 | 31.387 | 31.3774 | 30.8831 | 30.8691 | 30.8544 | 30.2913 | 30.2314 | 30.2253 | 30.2481 | 35.5125 | 35.4688 | 35.4438 | 35.4332 | 35.0513 | 34.9891 | 34.9445 | 34.5054 | 34.4509 | 34.2201 | 35.0441 | 35.0012 | 34.9607 | 34.9607 | 34.8649 | 34.7922 | 34.7278 | 34.6358 | 33.2986 | 33.2404 | 33.1838 | 32.6518 | 32.5954 | 32.5083 | 32.4043 | 32.3334 | 32.2677 | 31.9142 | 31.7574 | 31.6262 | 30.1895 | 30.1124 | 30.1077 | 33.2493 | 33.1507 | 33.0846 | 32.6266 | 32.5584 | 32.5216 | 31.9763 | 31.9083 | 31.833 | 31.6552 | 31.5604 | 31.4431 | 29.3512 | 29.3101 | 29.237 | 30.5932 | 30.5508 | 30.4864 | 30.2306 | 30.1805 | 30.1087 | 31.6187 | 31.6043 | 31.6023 | 31.6202 | 31.598 | 31.6028 | 32.1179 | 32.0684 | 32.0402 | 31.6455 | 31.6244 | 31.5535 | 33.2244 | 32.9991 | 32.853 | 32.4976 | 32.4221 | 32.2856 | 32.0504 | 31.9129 | 31.7631 | 32.5895 | 32.5303 | 32.4551 | 30.9764 | 30.8971 | 30.8659 | 33.2555 | 33.1693 | 33.0714 | 32.8218 | 32.6984 | 32.6019 | 32.0315 | 31.9796 | 31.9478 | 32.7881 | 32.768 | 32.7623 | 32.7433 | 32.7529 | 32.7371 | 32.7204 | 32.7021 | 32.6849 | 32.5954 | 32.5946 | 32.5579 | 32.6789 | 32.6656 | 32.6396 | 32.0242 | 31.9382 | 31.8689 | 31.3684 | 31.2884 | 31.199 | 35.3256 | 35.2753 | 35.2134 | 35.0534 | 35.0124 | 34.8567 | 34.0717 | 34.0302 | 33.9828 | 33.9088 | 33.8316 | 33.7894 | 33.6131 | 33.5618 | 33.5065 | 33.3829 | 33.3553 | 33.2652 | 33.0582 | 32.9772 | 32.8951 | 31.5633 | 31.5323 | 31.5038 | 31.4092 | 31.3593 | 31.3323
153 | Econ @ comp enthalpy | KJ/kg | 227.7058 | 227.5292 | 227.402 | 226.8404 | 226.7467 | 226.6386 | 225.3344 | 225.3178 | 225.2362 | 225.0109 | 224.9678 | 224.8792 | 224.751 | 224.7028 | 224.6237 | 223.6038 | 223.5592 | 223.5218 | 222.7753 | 222.6118 | 222.4256 | 227.3147 | 227.2856 | 227.3553 | 227.4498 | 227.512 | 227.5161 | 227.6397 | 227.7219 | 227.7518 | 228.2044 | 228.2214 | 228.1869 | 228.1665 | 228.175 | 228.1301 | 228.3045 | 228.1797 | 228.1385 | 228.1258 | 227.9309 | 227.9301 | 227.8333 | 227.7258 | 227.5293 | 225.594 | 225.4814 | 225.2775 | 224.1667 | 224.0102 | 223.8497 | 223.4541 | 223.2219 | 223.0318 | 228.087 | 227.9658 | 227.9006 | 226.3097 | 226.276 | 226.2166 | 225.8608 | 225.7956 | 225.7498 | 224.1866 | 224.1521 | 224.0948 | 222.5343 | 222.4857 | 222.4547 | 222.2489 | 222.183 | 226.6022 | 226.5344 | 226.4687 | 225.0991 | 225.0542 | 225.0337 | 224.6927 | 224.5352 | 224.5399 | 224.5058 | 223.7021 | 223.6621 | 223.6204 | 222.4756 | 222.4025 | 222.406 | 222.3897 | 231.3662 | 231.275 | 231.2503 | 231.2389 | 230.6711 | 230.5058 | 230.4556 | 229.7283 | 229.5969 | 229.1994 | 230.6319 | 230.5608 | 230.5025 | 230.4105 | 230.3128 | 230.1803 | 230.1165 | 229.987 | 228.0061 | 227.905 | 227.79 | 226.9708 | 226.87 | 226.7391 | 226.5871 | 226.4317 | 226.3628 | 225.6838 | 225.4461 | 225.2454 | 222.6262 | 222.5596 | 222.498 | 227.594 | 227.4368 | 227.3129 | 226.6352 | 226.5374 | 226.4243 | 225.6164 | 225.482 | 225.4238 | 225.1347 | 224.957 | 224.7559 | 220.9689 | 220.9004 | 220.7874 | 223.2763 | 223.2132 | 223.0783 | 222.3865 | 222.2934 | 222.2135 | 224.5565 | 224.5571 | 224.5549 | 224.5216 | 224.4841 | 224.4519 | 225.6863 | 225.5758 | 225.5363 | 224.8571 | 224.7805 | 224.7083 | 227.3453 | 226.9852 | 226.7557 | 226.2053 | 226.0909 | 225.9096 | 225.4887 | 225.3019 | 225.0465 | 226.2767 | 226.2303 | 226.0638 | 223.4381 | 223.3577 | 223.2916 | 227.247 | 227.0936 | 226.98 | 226.5273 | 226.373 | 226.1761 | 224.7119 | 224.6175 | 224.5107 | 225.595 | 225.5835 | 225.5465 | 225.5315 | 225.5317 | 225.5116 | 225.4793 | 225.5071 | 225.478 | 225.3522 | 225.2854 | 225.2587 | 225.5133 | 225.4767 | 225.4918 | 224.5576 | 224.4192 | 224.2871 | 223.4613 | 223.3175 | 223.1562 | 229.0757 | 229.0146 | 228.9236 | 228.7095 | 228.5878 | 228.357 | 227.2178 | 227.1276 | 227.0217 | 226.8965 | 226.7763 | 226.702 | 226.4148 | 226.3247 | 226.2724 | 226.0834 | 225.9549 | 225.8467 | 225.4889 | 225.3414 | 225.2122 | 222.7629 | 222.7064 | 222.6608 | 222.5318 | 222.4496 | 222.3789
154 | Econ @ comp specific Vol | m3/kg | 0.0008155 | 0.0008152 | 0.00081498 | 0.00081401 | 0.00081386 | 0.00081367 | 0.00081145 | 0.00081142 | 0.00081128 | 0.0008109 | 0.00081083 | 0.00081068 | 0.00081046 | 0.00081038 | 0.00081025 | 0.00080853 | 0.00080846 | 0.00080839 | 0.00080715 | 0.00080688 | 0.00080656 | 0.00081482 | 0.00081477 | 0.00081489 | 0.00081506 | 0.00081516 | 0.00081517 | 0.00081538 | 0.00081553 | 0.00081558 | 0.00081636 | 0.00081639 | 0.00081633 | 0.00081631 | 0.00081632 | 0.00081624 | 0.00081654 | 0.00081633 | 0.00081626 | 0.00081624 | 0.0008159 | 0.0008159 | 0.00081573 | 0.00081555 | 0.00081521 | 0.00081191 | 0.00081171 | 0.00081137 | 0.0008095 | 0.00080923 | 0.00080896 | 0.0008083 | 0.00080791 | 0.00080758 | 0.00081615 | 0.00081595 | 0.00081583 | 0.0008131 | 0.00081305 | 0.00081295 | 0.00081234 | 0.00081223 | 0.00081215 | 0.00080951 | 0.00080945 | 0.00080935 | 0.00080673 | 0.00080665 | 0.0008066 | 0.00080626 | 0.00080615 | 0.00081359 | 0.00081348 | 0.00081337 | 0.00081104 | 0.00081096 | 0.00081093 | 0.00081035 | 0.00081009 | 0.0008101 | 0.00081004 | 0.00080869 | 0.00080862 | 0.00080855 | 0.00080663 | 0.00080651 | 0.00080652 | 0.00080649 | 0.00082185 | 0.00082169 | 0.00082164 | 0.00082162 | 0.00082063 | 0.00082034 | 0.00082025 | 0.00081898 | 0.00081875 | 0.00081806 | 0.00082056 | 0.00082044 | 0.00082034 | 0.00082017 | 0.00082 | 0.00081977 | 0.00081966 | 0.00081944 | 0.00081602 | 0.00081584 | 0.00081564 | 0.00081424 | 0.00081407 | 0.00081384 | 0.00081359 | 0.00081332 | 0.0008132 | 0.00081204 | 0.00081164 | 0.0008113 | 0.0008069 | 0.00080679 | 0.00080669 | 0.00081529 | 0.00081502 | 0.00081481 | 0.00081365 | 0.00081349 | 0.00081329 | 0.00081192 | 0.00081169 | 0.0008116 | 0.00081111 | 0.00081081 | 0.00081047 | 0.00080415 | 0.00080403 | 0.00080385 | 0.00080798 | 0.00080788 | 0.00080765 | 0.00080649 | 0.00080633 | 0.0008062 | 0.00081011 | 0.00081011 | 0.00081011 | 0.00081005 | 0.00080998 | 0.00080993 | 0.00081203 | 0.00081184 | 0.00081178 | 0.00081063 | 0.0008105 | 0.00081038 | 0.00081485 | 0.00081424 | 0.00081384 | 0.00081291 | 0.00081271 | 0.00081241 | 0.00081169 | 0.00081138 | 0.00081095 | 0.00081302 | 0.00081295 | 0.00081266 | 0.00080823 | 0.0008081 | 0.00080799 | 0.00081467 | 0.00081441 | 0.00081422 | 0.00081344 | 0.00081318 | 0.00081285 | 0.00081034 | 0.00081018 | 0.00081 | 0.00081181 | 0.0008118 | 0.00081173 | 0.00081171 | 0.00081171 | 0.00081167 | 0.00081162 | 0.00081167 | 0.00081162 | 0.00081141 | 0.00081129 | 0.00081125 | 0.00081168 | 0.00081162 | 0.00081165 | 0.00081008 | 0.00080984 | 0.00080962 | 0.00080824 | 0.000808 | 0.00080773 | 0.00081773 | 0.00081763 | 0.00081747 | 0.00081711 | 0.00081689 | 0.0008165 | 0.00081455 | 0.00081439 | 0.00081421 | 0.000814 | 0.00081379 | 0.00081367 | 0.00081318 | 0.00081302 | 0.00081294 | 0.00081262 | 0.00081239 | 0.00081221 | 0.00081161 | 0.00081136 | 0.00081114 | 0.00080702 | 0.00080693 | 0.00080685 | 0.00080664 | 0.00080651 | 0.00080639
155 | Econ @ comp vol Flow | m^3/hr | -0.025937 | -0.043148 | -0.031002 | -0.022691 | -0.036411 | -0.028543 | -0.029477 | -0.030018 | -0.008136 | -0.025593 | -0.025298 | -0.016643 | -0.028887 | -0.012808 | -0.012021 | -0.012168 | -0.040689 | -0.005235 | -0.012611 | -0.022937 | -0.003956 | -0.04541 | -0.021216 | -0.030412 | -0.047475 | -0.027412 | -0.035132 | -0.026035 | -0.033411 | -0.033805 | -0.033067 | -0.020429 | -0.043 | -0.031936 | -0.060654 | -0.03351 | -0.027166 | 30.7931 | 32.1068 | 29.751 | 41.5055 | 55.2093 | 43.9462 | 41.5772 | 39.9145 | -0.025396 | -0.027461 | -0.019594 | -0.021167 | -0.027068 | -0.012021 | -0.016496 | 0.008927 | -0.009169 | -0.024314 | -0.040247 | -0.038034 | -0.042902 | -0.01861 | -0.02633 | -0.035723 | -0.025347 | -0.016987 | -0.014627 | -0.006464 | -0.005874 | -0.002973 | 0.002338 | -0.005923 | -0.004497 | 0.003518 | -0.020479 | -0.025199 | -0.03705 | -0.004448 | -0.016545 | -0.022052 | -0.015955 | -0.028002 | -0.013496 | -0.018659 | -0.022888 | -0.021659 | -0.004596 | -0.004104 | -0.011529 | -0.009267 | -0.00848 | 35.002 | 29.0561 | 34.1746 | 30.6214 | -0.045016 | -0.039656 | -0.041427 | -0.031199 | -0.028789 | -0.038329 | -0.040148 | -0.047524 | -0.053769 | -0.035723 | -0.027855 | -0.059621 | -0.042509 | -0.023429 | -0.022691 | -0.033952 | -0.045016 | -0.010742 | -0.050868 | -0.024118 | -0.02515 | -0.036411 | -0.031641 | 29.5967 | 25.9915 | 29.7857 | 0.002043 | -0.012168 | -0.004104 | -0.043246 | -0.027215 | -0.03469 | -0.015512 | -0.017922 | 0.25583 | -0.023773 | -0.011234 | -0.027363 | 41.3327 | 41.3405 | 41.3113 | 0.006419 | -0.000612 | -0.008726 | -0.006267 | -0.00971 | -0.020577 | 0.008386 | 0.001404 | 0.004059 | -0.013889 | -0.00789 | -0.017135 | -0.027068 | -0.020036 | -0.004497 | -0.021413 | -0.02156 | -0.013791 | -0.009906 | -0.015414 | -0.027511 | -0.038919 | -0.013348 | -0.028543 | 1.1736 | 2.0966 | 1.7481 | -0.021511 | -0.005923 | -0.002924 | 38.8679 | 27.6776 | 27.6752 | -0.01802 | 0.004698 | -0.016004 | -0.029232 | -0.012562 | -0.021856 | -0.025347 | -0.02815 | -0.020184 | -0.014725 | 0.000617 | -0.012217 | -0.025642 | -0.021069 | -0.021167 | -0.005677 | -0.008579 | -0.015807 | -0.020479 | -0.016889 | -0.020872 | -0.02933 | -0.029822 | -0.014529 | -0.010939 | -0.014676 | -0.012808 | -0.01625 | -0.008136 | -0.018708 | 0.001797 | -0.008923 | -0.008284 | 3.3197 | 1.4097 | 1.7126 | -0.0192 | -0.024363 | -0.040689 | -0.01861 | -0.024413 | -0.023724 | -0.034985 | -0.029576 | -0.014775 | -0.033264 | -0.016102 | -0.023331 | -0.013152 | -0.026478 | -0.013398 | 41.3053 | 41.3224 | 41.3332 | 0.000666 | -0.00076 | -0.005579 | 0.002486 | -0.001793 | 0.009862
156 | assumed approach of econ liquid to econ gauge | ºC | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
157 | target superheat economiser port | ºC | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
158 | Liquid injection
159 | LI flow meter Temp | ºC | 19.548 | 19.4774 | 19.3849 | 19.1152 | 19.0285 | 19.0063 | 18.2818 | 18.3 | 18.2472 | 18.1184 | 18.0892 | 18.0361 | 17.9758 | 17.9264 | 17.8939 | 17.3273 | 17.3199 | 17.2655 | 16.8168 | 16.7405 | 16.5886 | 19.3445 | 19.3337 | 19.3353 | 19.3593 | 19.3535 | 19.3783 | 19.4165 | 19.4233 | 19.4224 | 19.5129 | 19.5116 | 19.5024 | 19.4119 | 19.3997 | 19.4176 | 19.3965 | 19.2768 | 19.2536 | 19.2455 | 19.1201 | 19.1091 | 19.0841 | 19.0339 | 18.8962 | 17.8546 | 17.7969 | 17.7177 | 17.1293 | 17.0588 | 16.9646 | 16.7477 | 16.5877 | 16.519 | 19.4298 | 19.3557 | 19.3329 | 18.4754 | 18.4856 | 18.4406 | 18.2724 | 18.2217 | 18.2061 | 17.4242 | 17.3995 | 17.376 | 16.5334 | 16.5028 | 16.4883 | 16.3958 | 16.367 | 18.8189 | 18.7613 | 18.7005 | 17.9405 | 17.9163 | 17.9122 | 17.7416 | 17.6518 | 17.6321 | 17.5962 | 17.1716 | 17.1395 | 17.1223 | 16.4162 | 16.3613 | 16.3399 | 16.3208 | 21.7071 | 21.6477 | 21.6439 | 21.6178 | 21.2944 | 21.238 | 21.2058 | 20.8601 | 20.7562 | 20.5337 | 21.2526 | 21.2336 | 21.1573 | 21.1121 | 21.0328 | 20.9965 | 20.91 | 20.8537 | 19.2982 | 19.2382 | 19.1841 | 18.6755 | 18.6427 | 18.5464 | 18.4656 | 18.4145 | 18.3534 | 17.9906 | 17.8531 | 17.7346 | 16.3038 | 16.2771 | 16.256 | 18.9888 | 18.927 | 18.8385 | 18.47 | 18.3757 | 18.3022 | 17.6191 | 17.5737 | 17.4959 | 17.3445 | 17.2379 | 17.1583 | 15.1456 | 15.1224 | 15.0586 | 16.6793 | 16.6592 | 16.5676 | 16.2276 | 16.1804 | 16.1308 | 17.6817 | 17.667 | 17.6517 | 17.666 | 17.6471 | 17.6128 | 17.8378 | 17.8023 | 17.7745 | 17.4083 | 17.3497 | 17.2824 | 18.8091 | 18.6361 | 18.5005 | 18.2075 | 18.1209 | 18.0216 | 17.7946 | 17.6877 | 17.5445 | 18.3109 | 18.2849 | 18.2005 | 16.8673 | 16.8071 | 16.7826 | 18.641 | 18.577 | 18.5099 | 18.2821 | 18.1983 | 18.0989 | 17.8291 | 17.8039 | 17.7723 | 18.3026 | 18.2905 | 18.2761 | 18.2478 | 18.2318 | 18.2368 | 18.2385 | 18.2057 | 18.1899 | 18.0175 | 18.0208 | 17.9786 | 17.8771 | 17.8654 | 17.8386 | 17.1986 | 17.146 | 17.0623 | 16.6281 | 16.5301 | 16.4443 | 19.8269 | 19.7715 | 19.728 | 19.6083 | 19.5591 | 19.4079 | 18.4032 | 18.3363 | 18.2876 | 18.2237 | 18.1448 | 18.0764 | 17.956 | 17.9115 | 17.9098 | 17.7976 | 17.7432 | 17.7079 | 17.5549 | 17.5007 | 17.4381 | 16.3049 | 16.2943 | 16.2742 | 16.2031 | 16.1427 | 16.1053
160 | LI flow meter pressure - Not working correctly. | BarA | 1.6789 | 1.6802 | 1.6729 | 1.6678 | 1.6664 | 1.6649 | 1.6581 | 1.6544 | 1.6579 | 1.6592 | 1.6562 | 1.6536 | 1.6579 | 1.6561 | 1.6506 | 1.6425 | 1.6402 | 1.6418 | 1.6357 | 1.6347 | 1.6307 | 1.694 | 1.6889 | 1.6899 | 1.6927 | 1.696 | 1.6922 | 1.6973 | 1.6954 | 1.6946 | 1.6921 | 1.6983 | 1.6977 | 1.6997 | 1.6912 | 1.6948 | 1.6922 | 1.6877 | 1.6931 | 1.6869 | 1.6794 | 1.6812 | 1.6848 | 1.681 | 1.6769 | 1.6521 | 1.6499 | 1.6468 | 1.6389 | 1.6326 | 1.6371 | 1.6325 | 1.6278 | 1.6233 | 1.7331 | 1.7269 | 1.7301 | 1.7234 | 1.7215 | 1.7137 | 1.7126 | 1.7116 | 1.7137 | 1.6964 | 1.6938 | 1.6963 | 1.6834 | 1.6805 | 1.6803 | 1.6859 | 1.6796 | 1.7336 | 1.726 | 1.7303 | 1.7136 | 1.717 | 1.7248 | 1.7116 | 1.7125 | 1.7111 | 1.7122 | 1.703 | 1.696 | 1.7028 | 1.6913 | 1.6924 | 1.6905 | 1.6904 | 1.7809 | 1.7825 | 1.7794 | 1.7771 | 1.7711 | 1.7741 | 1.7715 | 1.7635 | 1.7618 | 1.759 | 1.788 | 1.7862 | 1.7842 | 1.7834 | 1.7846 | 1.7837 | 1.7808 | 1.7773 | 1.7478 | 1.7488 | 1.7472 | 1.7381 | 1.7338 | 1.7334 | 1.7305 | 1.7293 | 1.7304 | 1.7225 | 1.72 | 1.7174 | 1.6974 | 1.6932 | 1.6948 | 1.7633 | 1.7619 | 1.7621 | 1.7501 | 1.7498 | 1.7505 | 1.7325 | 1.7341 | 1.7328 | 1.7266 | 1.7283 | 1.7201 | 1.6859 | 1.6854 | 1.6849 | 1.7314 | 1.7322 | 1.728 | 1.7227 | 1.7185 | 1.719 | 1.7588 | 1.7576 | 1.7603 | 1.7633 | 1.7629 | 1.7586 | 1.7626 | 1.7589 | 1.756 | 1.7516 | 1.7471 | 1.746 | 1.7735 | 1.7669 | 1.7649 | 1.7583 | 1.7565 | 1.7568 | 1.7478 | 1.745 | 1.7452 | 1.7611 | 1.7591 | 1.7617 | 1.7302 | 1.7359 | 1.7374 | 1.8106 | 1.8055 | 1.8029 | 1.8007 | 1.7953 | 1.8005 | 1.7962 | 1.7918 | 1.7926 | 1.8135 | 1.8149 | 1.8146 | 1.8148 | 1.8164 | 1.8157 | 1.8188 | 1.8154 | 1.816 | 1.8107 | 1.8143 | 1.8117 | 1.812 | 1.8119 | 1.8104 | 1.7879 | 1.7894 | 1.7844 | 1.7812 | 1.7789 | 1.7788 | 1.8607 | 1.8616 | 1.8604 | 1.8563 | 1.8555 | 1.8541 | 1.8364 | 1.8369 | 1.8358 | 1.835 | 1.8324 | 1.8334 | 1.825 | 1.828 | 1.8268 | 1.8243 | 1.82 | 1.8214 | 1.8197 | 1.8183 | 1.8178 | 1.7963 | 1.7916 | 1.7926 | 1.7884 | 1.79 | 1.7918
161 | LI flow meter gauge | ºC | -14.4216 | -14.4034 | -14.509 | -14.5826 | -14.6038 | -14.6257 | -14.7242 | -14.7784 | -14.7278 | -14.7084 | -14.7525 | -14.7904 | -14.7277 | -14.7546 | -14.8346 | -14.9542 | -14.9884 | -14.9647 | -15.0554 | -15.0693 | -15.1292 | -14.2037 | -14.2771 | -14.2628 | -14.2217 | -14.1742 | -14.2298 | -14.1563 | -14.183 | -14.1944 | -14.2302 | -14.142 | -14.1507 | -14.122 | -14.2436 | -14.1921 | -14.2292 | -14.294 | -14.217 | -14.3062 | -14.4148 | -14.389 | -14.3365 | -14.3911 | -14.451 | -14.8127 | -14.8452 | -14.8905 | -15.008 | -15.1001 | -15.0338 | -15.1026 | -15.1715 | -15.2392 | -13.6446 | -13.7332 | -13.6884 | -13.7833 | -13.8101 | -13.9207 | -13.9363 | -13.951 | -13.9209 | -14.1684 | -14.2061 | -14.1697 | -14.357 | -14.3989 | -14.402 | -14.3207 | -14.412 | -13.6383 | -13.7455 | -13.6854 | -13.9228 | -13.8734 | -13.7635 | -13.9512 | -13.9382 | -13.9579 | -13.9426 | -14.0734 | -14.1742 | -14.0767 | -14.2424 | -14.2266 | -14.2535 | -14.2547 | -12.9759 | -12.9533 | -12.9963 | -13.0282 | -13.1123 | -13.07 | -13.107 | -13.2175 | -13.2412 | -13.2804 | -12.8781 | -12.9031 | -12.9298 | -12.9409 | -12.9254 | -12.9367 | -12.977 | -13.0253 | -13.4378 | -13.4232 | -13.4465 | -13.5749 | -13.6352 | -13.6409 | -13.6813 | -13.699 | -13.6828 | -13.7949 | -13.8316 | -13.8675 | -14.1548 | -14.215 | -14.1921 | -13.221 | -13.2405 | -13.237 | -13.405 | -13.4099 | -13.4001 | -13.6533 | -13.6305 | -13.6498 | -13.7374 | -13.7128 | -13.8298 | -14.3206 | -14.3275 | -14.3349 | -13.6688 | -13.6574 | -13.717 | -13.7921 | -13.8518 | -13.8458 | -13.2832 | -13.3 | -13.2621 | -13.2202 | -13.2264 | -13.2869 | -13.2309 | -13.2819 | -13.323 | -13.3849 | -13.4478 | -13.4627 | -13.0783 | -13.17 | -13.1982 | -13.2899 | -13.3164 | -13.3122 | -13.4374 | -13.4776 | -13.4739 | -13.2519 | -13.2788 | -13.2436 | -13.6869 | -13.6053 | -13.5837 | -12.5676 | -12.6369 | -12.6727 | -12.7034 | -12.7765 | -12.7049 | -12.7645 | -12.8259 | -12.8139 | -12.5273 | -12.5082 | -12.512 | -12.5095 | -12.4879 | -12.4972 | -12.4547 | -12.5014 | -12.4935 | -12.5656 | -12.5165 | -12.5515 | -12.5483 | -12.5491 | -12.5693 | -12.8791 | -12.8585 | -12.9268 | -12.9716 | -13.0041 | -13.0051 | -11.8896 | -11.8766 | -11.8932 | -11.9479 | -11.9595 | -11.9777 | -12.2166 | -12.2094 | -12.2242 | -12.2353 | -12.2702 | -12.2572 | -12.3707 | -12.3299 | -12.3457 | -12.3806 | -12.4393 | -12.4196 | -12.4425 | -12.4615 | -12.4685 | -12.7634 | -12.8279 | -12.8144 | -12.8729 | -12.8497 | -12.8253
162 | LI flow meter enthalpy | KJ/kg | 418.5895 | 418.5265 | 418.4618 | 418.241 | 418.1696 | 418.1536 | 417.5472 | 417.5703 | 417.5181 | 417.4053 | 417.3864 | 417.3463 | 417.286 | 417.2475 | 417.2308 | 416.7635 | 416.762 | 416.7122 | 416.3419 | 416.2788 | 416.1576 | 418.3847 | 418.3857 | 418.385 | 418.3998 | 418.3883 | 418.4173 | 418.4398 | 418.4493 | 418.4501 | 418.5328 | 418.5193 | 418.5126 | 418.431 | 418.4376 | 418.4457 | 418.4328 | 418.3392 | 418.3086 | 418.3141 | 418.2218 | 418.2088 | 418.18 | 418.1447 | 418.0351 | 417.1942 | 417.1495 | 417.0881 | 416.602 | 416.5547 | 416.465 | 416.2896 | 416.1628 | 416.1136 | 418.3788 | 418.3278 | 418.3019 | 417.58 | 417.5926 | 417.5699 | 417.4279 | 417.3867 | 417.369 | 416.7352 | 416.7195 | 416.6942 | 416.001 | 415.9809 | 415.9689 | 415.8783 | 415.8668 | 417.8537 | 417.8197 | 417.7589 | 417.1418 | 417.114 | 417.0946 | 416.9756 | 416.8968 | 416.8829 | 416.8499 | 416.5055 | 416.4926 | 416.4638 | 415.8844 | 415.8352 | 415.8209 | 415.8047 | 420.2427 | 420.1883 | 420.1911 | 420.1731 | 419.9065 | 419.8518 | 419.8294 | 419.5474 | 419.4613 | 419.2755 | 419.8369 | 419.8242 | 419.7622 | 419.7249 | 419.6543 | 419.6246 | 419.556 | 419.5144 | 418.2362 | 418.1826 | 418.1395 | 417.7216 | 417.7021 | 417.6204 | 417.5569 | 417.5157 | 417.4609 | 417.1663 | 417.0538 | 416.9576 | 415.7758 | 415.7616 | 415.7404 | 417.9392 | 417.8889 | 417.8124 | 417.5207 | 417.4405 | 417.3761 | 416.8276 | 416.7854 | 416.7216 | 416.6048 | 416.5099 | 416.4589 | 414.8117 | 414.7929 | 414.7396 | 416.0256 | 416.0067 | 415.9371 | 415.6576 | 415.626 | 415.5828 | 416.8269 | 416.8169 | 416.7982 | 416.8043 | 416.789 | 416.7685 | 416.9531 | 416.9301 | 416.9123 | 416.6077 | 416.5668 | 416.5113 | 417.764 | 417.6289 | 417.5166 | 417.2788 | 417.2084 | 417.1226 | 416.9464 | 416.8607 | 416.7375 | 417.3619 | 417.3435 | 417.266 | 416.189 | 416.1256 | 416.1014 | 417.544 | 417.4993 | 417.447 | 417.256 | 417.1949 | 417.0989 | 416.8762 | 416.8638 | 416.8349 | 417.2472 | 417.2339 | 417.2221 | 417.1974 | 417.1804 | 417.1861 | 417.1811 | 417.16 | 417.1453 | 417.0081 | 417.0035 | 416.9725 | 416.8849 | 416.875 | 416.855 | 416.3527 | 416.3045 | 416.2431 | 415.8779 | 415.7988 | 415.7255 | 418.4626 | 418.4129 | 418.3779 | 418.283 | 418.2424 | 418.1149 | 417.2867 | 417.2281 | 417.1884 | 417.1352 | 417.0727 | 417.0119 | 416.9258 | 416.8813 | 416.8823 | 416.7912 | 416.7534 | 416.7201 | 416.5923 | 416.5486 | 416.496 | 415.5694 | 415.5702 | 415.551 | 415.499 | 415.4438 | 415.408
163 | LI flow meter specific Vol | m3/kg | 0.13682 | 0.13668 | 0.13724 | 0.13753 | 0.13761 | 0.13773 | 0.13791 | 0.13825 | 0.13792 | 0.13773 | 0.13798 | 0.13817 | 0.13777 | 0.1379 | 0.13836 | 0.13876 | 0.13896 | 0.13879 | 0.13908 | 0.13912 | 0.1394 | 0.13545 | 0.13587 | 0.13578 | 0.13556 | 0.13528 | 0.13562 | 0.13521 | 0.13537 | 0.13544 | 0.13569 | 0.13518 | 0.13523 | 0.13501 | 0.13571 | 0.13542 | 0.13562 | 0.13593 | 0.13548 | 0.13599 | 0.13655 | 0.1364 | 0.13608 | 0.13637 | 0.13664 | 0.13821 | 0.13837 | 0.13859 | 0.13897 | 0.13948 | 0.13903 | 0.13932 | 0.13965 | 0.14002 | 0.13231 | 0.13277 | 0.1325 | 0.13259 | 0.13275 | 0.13335 | 0.13335 | 0.1334 | 0.13323 | 0.13422 | 0.13442 | 0.1342 | 0.13483 | 0.13505 | 0.13506 | 0.13455 | 0.13506 | 0.13195 | 0.13253 | 0.13216 | 0.1331 | 0.1328 | 0.13218 | 0.13315 | 0.13303 | 0.13313 | 0.13303 | 0.13354 | 0.1341 | 0.13354 | 0.13411 | 0.13399 | 0.13413 | 0.13413 | 0.12977 | 0.12962 | 0.12985 | 0.13001 | 0.13031 | 0.13005 | 0.13023 | 0.13067 | 0.13075 | 0.13085 | 0.12901 | 0.12913 | 0.12924 | 0.12928 | 0.12915 | 0.1292 | 0.12937 | 0.12961 | 0.13108 | 0.13097 | 0.13107 | 0.13152 | 0.13184 | 0.13183 | 0.13201 | 0.13208 | 0.13196 | 0.1324 | 0.13254 | 0.13268 | 0.13355 | 0.13388 | 0.13373 | 0.12973 | 0.1298 | 0.12974 | 0.13047 | 0.13045 | 0.13036 | 0.13141 | 0.13126 | 0.13133 | 0.13174 | 0.13154 | 0.13216 | 0.13387 | 0.1339 | 0.13391 | 0.13101 | 0.13093 | 0.13122 | 0.13146 | 0.13177 | 0.13171 | 0.1294 | 0.12948 | 0.12926 | 0.12904 | 0.12907 | 0.12938 | 0.12919 | 0.12945 | 0.12966 | 0.12981 | 0.13013 | 0.13018 | 0.12885 | 0.12927 | 0.12935 | 0.1297 | 0.1298 | 0.12973 | 0.1303 | 0.13047 | 0.13038 | 0.12955 | 0.12968 | 0.12945 | 0.13121 | 0.13072 | 0.13059 | 0.12602 | 0.12636 | 0.12651 | 0.12656 | 0.12691 | 0.12648 | 0.12666 | 0.12698 | 0.1269 | 0.12564 | 0.12553 | 0.12554 | 0.12552 | 0.12539 | 0.12545 | 0.12522 | 0.12545 | 0.1254 | 0.1257 | 0.12544 | 0.1256 | 0.12553 | 0.12553 | 0.12563 | 0.12696 | 0.12682 | 0.12714 | 0.12716 | 0.12729 | 0.12725 | 0.12306 | 0.12297 | 0.12303 | 0.12325 | 0.12329 | 0.12331 | 0.12405 | 0.12398 | 0.12404 | 0.12406 | 0.12421 | 0.1241 | 0.12464 | 0.1244 | 0.12448 | 0.12461 | 0.12489 | 0.12477 | 0.12482 | 0.12489 | 0.12489 | 0.12588 | 0.12622 | 0.12614 | 0.12642 | 0.12626 | 0.12611
164 | LI flow meter vol Flow | m^3/hr | 0.52097 | 0.52228 | 0.51856 | 0.52383 | 0.51913 | 0.5219 | 0.52213 | 0.51969 | 0.52445 | 0.52287 | 0.52214 | 0.51881 | 0.52234 | 0.5214 | 0.52309 | 0.51901 | 0.52345 | 0.52259 | 0.52245 | 0.52425 | 2.1308 | 0.52363 | 0.52213 | 0.52231 | 0.51894 | 0.52252 | 0.52322 | 0.52084 | 0.52169 | 0.52331 | 0.52161 | 0.51954 | 0.52028 | 0.52225 | 0.51986 | 0.52168 | 0.52169 | 0.52185 | 0.51922 | 0.51902 | 0.52214 | 0.52263 | 0.52283 | 0.5233 | 0.52062 | 0.52139 | 0.52232 | 0.52261 | 0.52145 | 0.52158 | 0.52163 | 0.52302 | 0.52431 | 0.52138 | 0.52242 | 0.52038 | 0.5213 | 0.5199 | 0.52089 | 0.52049 | 0.52335 | 0.52231 | 0.52328 | 0.52227 | 0.5238 | 0.52209 | 0.52245 | 0.52199 | 0.52256 | 0.52208 | 0.51901 | 0.51943 | 0.52385 | 0.52362 | 0.52067 | 0.52138 | 0.52129 | 0.52197 | 0.52215 | 0.51988 | 0.52255 | 0.52247 | 0.52298 | 0.52265 | 0.5209 | 0.52151 | 0.52401 | 0.51914 | 0.5229 | 0.52214 | 0.5195 | 0.5228 | 0.5209 | 0.52272 | 0.5207 | 0.5215 | 0.52287 | 0.52322 | 0.52429 | 0.52376 | 0.52382 | 0.52088 | 0.52394 | 0.52282 | 0.52108 | 0.52184 | 0.52135 | 0.52159 | 0.51999 | 0.5222 | 0.52415 | 0.52191 | 0.52189 | 0.52089 | 0.5219 | 0.5234 | 0.52135 | 0.52375 | 0.5242 | 0.52244 | 0.52114 | 0.52244 | 0.51929 | 0.52193 | 0.52172 | 0.5215 | 0.52307 | 0.51997 | 0.52144 | 0.52251 | 0.52156 | 0.52188 | 0.52084 | 0.52181 | 0.52297 | 0.52365 | 0.52049 | 0.5225 | 0.52299 | 0.52258 | 0.52229 | 0.52073 | 0.52067 | 0.51994 | 0.52312 | 0.52106 | 0.52084 | 0.52164 | 0.5203 | 0.52059 | 0.52417 | 0.52014 | 0.52067 | 0.52106 | 0.52118 | 0.52294 | 0.52445 | 0.52109 | 0.52138 | 0.52066 | 0.52039 | 0.52342 | 0.52174 | 0.52093 | 0.52204 | 0.52173 | 0.52371 | 0.52104 | 0.52378 | 0.52293 | 0.5208 | 0.52315 | 0.52233 | 0.52189 | 0.52176 | 0.52182 | 0.52377 | 0.52039 | 1.9166 | 6.4393 | 6.4391 | 0.52208 | 0.52176 | 0.52326 | 6.4407 | 6.4416 | 6.4388 | 0.52054 | 0.51979 | 0.52168 | 0.5216 | 0.52299 | 0.52413 | 0.52087 | 0.52231 | 0.52196 | 0.52359 | 0.5225 | 0.52323 | 0.51941 | 0.52353 | 0.52047 | 0.52314 | 0.52314 | 0.52164 | 0.52298 | 0.52145 | 0.5209 | 0.52364 | 0.52272 | 0.52165 | 0.52056 | 0.52194 | 0.52029 | 0.5232 | 0.52376 | 0.51911 | 0.51975 | 0.52158 | 0.52164 | 0.52187 | 0.52159 | 0.51906 | 0.52146 | 0.52118 | 0.51986
165 | LI flow meter mass Flow | kg/s | 0.0010577 | 0.0010615 | 0.0010495 | 0.001058 | 0.0010479 | 0.0010526 | 0.0010516 | 0.0010442 | 0.0010563 | 0.0010545 | 0.0010512 | 0.001043 | 0.0010532 | 0.0010503 | 0.0010502 | 0.001039 | 0.0010464 | 0.001046 | 0.0010435 | 0.0010467 | 0.0042462 | 0.0010739 | 0.0010675 | 0.0010685 | 0.0010634 | 0.0010729 | 0.0010717 | 0.00107 | 0.0010705 | 0.0010733 | 0.0010678 | 0.0010676 | 0.0010688 | 0.0010745 | 0.0010641 | 0.0010701 | 0.0010685 | 0.0010664 | 0.0010646 | 0.0010602 | 0.0010622 | 0.0010644 | 0.0010673 | 0.0010659 | 0.0010584 | 0.0010479 | 0.0010486 | 0.0010474 | 0.0010423 | 0.0010387 | 0.0010422 | 0.0010428 | 0.0010429 | 0.0010343 | 0.0010968 | 0.0010887 | 0.0010928 | 0.0010892 | 0.00109 | 0.0010842 | 0.0010902 | 0.0010876 | 0.001091 | 0.0010809 | 0.0010824 | 0.0010806 | 0.0010764 | 0.0010736 | 0.0010747 | 0.0010779 | 0.0010675 | 0.0010934 | 0.001098 | 0.0011006 | 0.0010867 | 0.0010905 | 0.0010955 | 0.0010889 | 0.0010903 | 0.0010847 | 0.0010912 | 0.0010868 | 0.0010833 | 0.0010872 | 0.0010789 | 0.0010812 | 0.0010852 | 0.0010751 | 0.0011193 | 0.001119 | 0.0011113 | 0.001117 | 0.0011104 | 0.0011165 | 0.0011106 | 0.0011086 | 0.0011109 | 0.0011107 | 0.0011289 | 0.0011267 | 0.0011259 | 0.0011192 | 0.0011269 | 0.0011241 | 0.0011188 | 0.0011184 | 0.0011048 | 0.0011062 | 0.001102 | 0.0011029 | 0.0011043 | 0.0010997 | 0.0010982 | 0.0010955 | 0.0010986 | 0.0010981 | 0.0010927 | 0.0010966 | 0.0010903 | 0.001084 | 0.0010825 | 0.0011187 | 0.0011113 | 0.0011175 | 0.0011107 | 0.0011105 | 0.0011146 | 0.0010991 | 0.0011035 | 0.0011052 | 0.0010997 | 0.001102 | 0.0010947 | 0.0010827 | 0.0010849 | 0.0010862 | 0.0011036 | 0.0011085 | 0.0011071 | 0.0011042 | 0.001101 | 0.0010982 | 0.0011177 | 0.0011154 | 0.0011241 | 0.0011216 | 0.001121 | 0.00112 | 0.0011187 | 0.0011171 | 0.001123 | 0.001113 | 0.0011114 | 0.0011119 | 0.0011235 | 0.0011237 | 0.0011262 | 0.001116 | 0.0011157 | 0.0011148 | 0.0011094 | 0.0011144 | 0.0011116 | 0.001117 | 0.0011182 | 0.0011196 | 0.0011088 | 0.0011072 | 0.0011142 | 0.0011527 | 0.0011449 | 0.0011486 | 0.0011464 | 0.0011423 | 0.0011459 | 0.0011444 | 0.0011458 | 0.0011391 | 0.0042375 | 0.014249 | 0.014247 | 0.0011554 | 0.0011558 | 0.0011587 | 0.014287 | 0.014263 | 0.014263 | 0.0011503 | 0.001151 | 0.0011537 | 0.0011542 | 0.0011573 | 0.0011589 | 0.0011397 | 0.001144 | 0.0011404 | 0.0011438 | 0.0011403 | 0.0011422 | 0.0011724 | 0.0011826 | 0.0011751 | 0.001179 | 0.0011787 | 0.0011751 | 0.001171 | 0.0011683 | 0.0011665 | 0.0011724 | 0.001169 | 0.0011676 | 0.0011601 | 0.0011654 | 0.001161 | 0.0011663 | 0.0011649 | 0.0011557 | 0.0011567 | 0.0011601 | 0.0011602 | 0.0011516 | 0.0011479 | 0.001143 | 0.0011458 | 0.0011466 | 0.0011451
166 | LI on/off | - | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI
167
168
169 | Electrical Data
170 | Power input |  | 119.4992 | 118.79 | 119.4309 | 127.5683 | 128.006 | 127.5888 | 59.1581 | 59.7945 | 59.2685 | 54.1841 | 53.9606 | 54.4708 | 54.5679 | 54.1843 | 54.205 | 19.3043 | 19.9726 | 19.6288 | 20.6619 | 20.0945 | 21.2378 | 52.6734 | 52.8096 | 52.7737 | 57.2978 | 56.5406 | 57.2907 | 59.5372 | 59.1441 | 59.3426 | 122.3535 | 121.1635 | 121.5595 | 128.6453 | 128.3336 | 128.7511 | 126.3583 | 229.86 | 229.8192 | 229.788 | 229.7588 | 230.2063 | 230.3415 | 228.8473 | 230.1678 | 255.5948 | 256.0513 | 254.6313 | 252.0243 | 254.8569 | 257.0034 | 251.7677 | 252.3911 | 249.7002 | 248.1303 | 253.0356 | 250.7873 | 116.0362 | 116.253 | 116.5996 | 117.7818 | 117.9755 | 117.775 | 52.2129 | 51.8846 | 51.9135 | 19.3076 | 18.9079 | 19.4552 | 20.8503 | 19.9527 | 126.2066 | 126.4329 | 126.5345 | 55.8506 | 56.3042 | 57.0558 | 56.9312 | 59.386 | 59.4363 | 59.0296 | 59.8121 | 60.4708 | 60.3824 | 20.7578 | 20.9116 | 20.5648 | 20.537 | 226.7017 | 227.1654 | 226.3685 | 225.8979 | 250.1444 | 250.5474 | 251.8222 | 247.958 | 248.6345 | 248.3697 | 253.0415 | 251.1063 | 250.9324 | 251.6663 | 249.521 | 250.653 | 248.8685 | 248.8877 | 249.8527 | 250.2379 | 250.1678 | 250.0491 | 252.4685 | 253.5992 | 250.4028 | 249.5629 | 249.7189 | 227.605 | 226.5059 | 227.0164 | 59.1048 | 58.9568 | 58.5944 | 251.6153 | 252.1751 | 250.4415 | 250.3699 | 250.0738 | 249.3838 | 252.2843 | 252.7251 | 250.7308 | 226.7294 | 225.7125 | 226.1696 | 58.7229 | 58.9279 | 58.1343 | 56.0385 | 55.5897 | 56.3449 | 51.8491 | 52.0769 | 51.9873 | 19.7068 | 19.8131 | 19.7217 | 20.5707 | 21.0419 | 20.5815 | 117.4799 | 118.1851 | 117.2627 | 127.4955 | 126.3336 | 126.6961 | 249.9693 | 246.878 | 248.761 | 251.2586 | 249.6893 | 248.3999 | 248.9689 | 247.7815 | 249.3591 | 225.4875 | 225.4563 | 223.8227 | 58.3426 | 59.0402 | 58.3082 | 250.4776 | 253.801 | 249.7197 | 254.0856 | 254.7866 | 252.6337 | 58.8955 | 58.5624 | 58.1529 | 20.9593 | 21.0495 | 20.6696 | 19.3961 | 19.6168 | 19.3655 | 20.7379 | 20.5422 | 20.5998 | 55.9822 | 55.5058 | 55.5622 | 52.4554 | 52.7361 | 52.1904 | 117.6301 | 117.1262 | 114.9977 | 128.3149 | 127.7376 | 128.5979 | 251.7195 | 250.0775 | 249.4836 | 251.5394 | 250.8161 | 252.39 | 249.0566 | 249.3972 | 250.1434 | 252.0137 | 249.9096 | 250.0278 | 251.8127 | 251.4453 | 251.3258 | 250.6854 | 255.1167 | 253.356 | 227.1958 | 226.7404 | 226.0356 | 58.4112 | 58.8934 | 58.5261 | 58.7867 | 58.6631 | 58.7514
171 | Amps phase 1 |  | 197.2947 | 195.4498 | 197.3222 | 211.1828 | 208.877 | 210.4298 | 107.5964 | 106.9401 | 105.8934 | 100.6003 | 100.9459 | 101.1183 | 100.8844 | 101.1716 | 100.58 | 41.196 | 41.9138 | 40.9422 | 44.0314 | 43.6532 | 44.268 | 100.0473 | 100.38 | 98.9103 | 104.9581 | 104.3297 | 104.139 | 106.6916 | 106.7099 | 105.8669 | 199.0384 | 201.7561 | 201.35 | 208.8348 | 210.6616 | 208.1948 | 208.9447 | 367.1387 | 366.6719 | 369.4891 | 366.4696 | 366.1901 | 369.475 | 367.8917 | 371.4444 | 410.3301 | 409.7719 | 405.7678 | 403.7374 | 406.6094 | 411.0409 | 401.9374 | 404.1312 | 401.8522 | 402.7253 | 404.2369 | 399.5616 | 193.9173 | 195.5197 | 193.944 | 194.6697 | 197.6336 | 194.3211 | 98.5969 | 98.2443 | 97.7495 | 42.4155 | 41.7892 | 42.6723 | 44.2199 | 43.9915 | 208.5746 | 204.8336 | 208.2424 | 104.0913 | 105.5597 | 105.3829 | 104.5507 | 107.3508 | 107.072 | 106.3972 | 106.4333 | 108.8735 | 107.9682 | 44.8417 | 44.1796 | 43.6032 | 44.4289 | 359.6462 | 360.3393 | 359.8021 | 360.1237 | 399.3037 | 401.4624 | 403.23 | 397.5884 | 398.5031 | 398.1938 | 403.9355 | 401.7544 | 400.4796 | 401.166 | 395.7559 | 398.2029 | 397.6313 | 393.9594 | 399.9829 | 400.6167 | 402.3714 | 403.8621 | 407.6304 | 410.6779 | 402.6581 | 403.8256 | 405.5116 | 364.8774 | 367.6853 | 365.4373 | 104.3809 | 104.141 | 102.6989 | 405.2731 | 405.2249 | 406.6244 | 398.846 | 400.5182 | 398.1597 | 403.2951 | 406.8945 | 403.5141 | 363.4616 | 361.5596 | 364.7188 | 106.2106 | 105.6429 | 103.9087 | 105.7443 | 105.7645 | 106.3692 | 100.2501 | 100.0857 | 99.2755 | 41.9809 | 42.1843 | 41.7606 | 44.2636 | 44.2237 | 43.6761 | 196.7158 | 198.2908 | 197.806 | 208.0993 | 208.3936 | 209.2083 | 401.1018 | 395.487 | 399.3512 | 402.4721 | 400.7401 | 398.0508 | 402.9233 | 399.3172 | 403.7615 | 359.0219 | 355.6795 | 354.856 | 106.6884 | 106.7749 | 106.9056 | 401.6338 | 405.6702 | 401.1818 | 405.4443 | 407.9586 | 403.714 | 107.3967 | 107.2267 | 106.3671 | 44.8991 | 45.2321 | 44.9381 | 41.996 | 42.841 | 43.2237 | 43.9768 | 44.5702 | 44.6677 | 103.4281 | 104.0729 | 103.2904 | 100.4015 | 101.0392 | 99.6232 | 196.1969 | 195.4483 | 193.7607 | 209.1946 | 212.0086 | 208.8158 | 402.6211 | 400.4607 | 399.2563 | 402.3312 | 400.3928 | 403.6392 | 402.5703 | 403.0808 | 404.0941 | 407.3103 | 404.4139 | 403.8514 | 409.7925 | 408.1666 | 407.7058 | 404.8136 | 413.9249 | 410.1725 | 368.0884 | 367.9907 | 365.9418 | 106.9666 | 105.6953 | 108.5539 | 108.4911 | 107.4811 | 107.7953
172 | Amps phase 2 |  | 198.6702 | 199.0956 | 198.8477 | 213.0151 | 212.7122 | 212.6876 | 106.8506 | 108.5871 | 108.1186 | 100.6098 | 100.3306 | 101.1104 | 100.4599 | 101.196 | 100.4843 | 40.4575 | 41.5605 | 41.8341 | 43.2225 | 42.1086 | 44.0294 | 96.7844 | 97.7352 | 97.8312 | 103.5112 | 103.1312 | 104.5794 | 106.6256 | 107.0409 | 106.6489 | 203.3994 | 200.8406 | 203.0793 | 218.5591 | 212.8844 | 218.5082 | 213.8986 | 376.0741 | 374.7724 | 374.1692 | 374.5448 | 375.9294 | 378.0917 | 373.1916 | 373.0183 | 417.7165 | 418.0971 | 415.3696 | 408.9479 | 414.5864 | 415.5608 | 407.6325 | 408.5392 | 404.5109 | 402.5404 | 407.6571 | 398.3239 | 193.5027 | 194.1531 | 193.5975 | 195.0374 | 194.955 | 196.6561 | 95.6895 | 94.2544 | 95.2375 | 40.6576 | 40.0611 | 40.6095 | 42.6161 | 42.5085 | 212.0752 | 214.1322 | 211.9313 | 102.4169 | 103.498 | 104.5391 | 103.5562 | 106.6613 | 106.6509 | 106.4423 | 108.6787 | 109.6532 | 109.6073 | 42.2657 | 42.6891 | 42.9878 | 42.0057 | 360.675 | 362.6841 | 361.0677 | 361.5934 | 401.3242 | 401.2519 | 404.2058 | 400.6199 | 403.5039 | 406.406 | 405.4187 | 402.1727 | 400.6845 | 405.5304 | 399.7079 | 400.6594 | 397.746 | 397.3638 | 409.7689 | 408.4648 | 408.2861 | 408.4448 | 412.7133 | 411.8164 | 408.4937 | 407.3052 | 406.1302 | 373.5324 | 373.2789 | 373.7141 | 109.3896 | 110.8564 | 110.6567 | 408.3448 | 407.8336 | 408.4459 | 403.2173 | 404.5591 | 402.7563 | 409.642 | 410.0972 | 405.764 | 368.2458 | 366.5143 | 367.0172 | 107.0224 | 107.3984 | 107.3946 | 104.5636 | 103.2648 | 103.713 | 97.6098 | 97.4012 | 97.9645 | 41.9747 | 41.1678 | 41.5665 | 43.634 | 44.1199 | 43.9461 | 196.3658 | 201.0224 | 198.5457 | 216.4825 | 214.8778 | 212.9872 | 408.5803 | 401.9716 | 405.7374 | 409.0298 | 404.5637 | 407.0818 | 408.4728 | 406.1868 | 407.5453 | 362.8136 | 364.6181 | 360.7411 | 109.0842 | 108.8817 | 107.3377 | 408.0427 | 413.5165 | 406.282 | 414.4395 | 413.8753 | 411.3238 | 106.4594 | 107.2851 | 105.1669 | 44.0703 | 44.5547 | 44.0162 | 41.8858 | 42.0277 | 41.5881 | 44.053 | 43.376 | 43.7578 | 105.4862 | 105.2516 | 104.8382 | 97.9059 | 98.8856 | 98.6131 | 199.1936 | 199.2811 | 193.5825 | 216.7012 | 215.9021 | 215.7022 | 405.6433 | 404.2145 | 403.5219 | 405.4472 | 404.9515 | 408.5098 | 406.8893 | 408.263 | 407.0509 | 411.3346 | 407.2196 | 409.9289 | 409.1643 | 412.7852 | 410.9548 | 411.3275 | 417.8131 | 412.5074 | 369.6771 | 371.0632 | 369.9217 | 107.513 | 108.6321 | 105.969 | 107.5645 | 108.5956 | 107.0371
173 | Amps phase 3 |  | 198.6858 | 196.5078 | 198.3565 | 208.2475 | 207.9318 | 205.3157 | 114.8394 | 115.4956 | 115.3265 | 105.4149 | 105.8118 | 105.7619 | 106.5637 | 105.523 | 106.4277 | 43.0202 | 43.9333 | 43.7925 | 46.3432 | 45.8141 | 46.4298 | 103.444 | 103.2821 | 103.8839 | 112.8296 | 109.581 | 111.4662 | 115.7532 | 115.2437 | 115.8268 | 202.926 | 197.9886 | 197.1766 | 210.2579 | 211.3018 | 210.9482 | 207.2708 | 382.1381 | 382.3322 | 382.2426 | 380.3893 | 381.0325 | 379.596 | 377.4726 | 382.7531 | 419.7683 | 419.9897 | 419.3864 | 415.2794 | 419.1771 | 421.2502 | 412.9662 | 415.6606 | 411.067 | 409.0878 | 413.2569 | 409.0923 | 194.5562 | 194.0718 | 192.1757 | 193.1728 | 194.2406 | 193.6759 | 101.5948 | 101.4753 | 101.95 | 45.1977 | 44.2658 | 44.9619 | 47.2288 | 45.6918 | 206.4048 | 208.3821 | 207.6377 | 109.7312 | 108.5938 | 111.418 | 111.6057 | 117.0289 | 117.0718 | 117.5792 | 118.2015 | 117.4265 | 118.7652 | 46.6779 | 46.9874 | 46.6503 | 45.8407 | 370.4674 | 371.1904 | 369.545 | 367.5979 | 409.0742 | 411.7742 | 413.4091 | 410.0592 | 409.8034 | 408.9916 | 412.9295 | 410.6845 | 411.023 | 411.1498 | 410.317 | 412.18 | 409.9423 | 411.1288 | 411.7937 | 409.6749 | 413.5101 | 412.5161 | 417.0324 | 417.5754 | 414.3751 | 408.7112 | 410.6759 | 376.8148 | 375.249 | 375.9045 | 114.9691 | 113.116 | 112.1962 | 411.8212 | 412.9598 | 410.2328 | 407.0776 | 405.5102 | 408.1494 | 414.9767 | 414.1667 | 412.1024 | 373.7148 | 373.1971 | 371.5716 | 112.1357 | 113.7607 | 112.0673 | 109.5875 | 108.6506 | 109.4506 | 102.3868 | 102.0043 | 102.3327 | 45.3689 | 44.4895 | 44.5868 | 46.2517 | 46.259 | 46.4724 | 194.1053 | 198.2338 | 197.0615 | 211.5869 | 208.4117 | 209.7799 | 411.5932 | 404.3425 | 409.9918 | 415.2467 | 409.9733 | 407.3631 | 413.3945 | 412.0783 | 412.8414 | 368.4577 | 369.1425 | 368.5876 | 115.024 | 115.579 | 114.4309 | 413.1285 | 416.0854 | 408.6791 | 417.7939 | 419.5932 | 416.514 | 114.5974 | 113.6657 | 113.554 | 46.7452 | 46.6715 | 46.7744 | 45.3876 | 44.5095 | 43.4463 | 45.6315 | 45.2585 | 47.2402 | 108.8572 | 107.09 | 107.446 | 101.5661 | 103.7026 | 102.3476 | 195.0478 | 194.9329 | 192.0004 | 213.5894 | 209.5786 | 215.3414 | 412.3854 | 410.9706 | 410.3677 | 415.0627 | 411.7228 | 415.3098 | 414.8839 | 413.8953 | 415.3515 | 416.2498 | 412.5535 | 414.8082 | 416.1111 | 413.2616 | 416.4615 | 413.0898 | 419.6893 | 421.1912 | 375.5553 | 374.1532 | 372.9978 | 114.2899 | 114.9609 | 111.2436 | 112.6181 | 112.612 | 113.094
174 | Voltage Phase 1 |  | 385.735 | 385.1328 | 384.3926 | 383.1533 | 386.387 | 386.29 | 393.3895 | 393.2566 | 392.8126 | 392.4107 | 392.1945 | 392.5252 | 392.59 | 391.3191 | 391.7668 | 392.815 | 393.0038 | 392.2923 | 391.7883 | 392.8479 | 393.6353 | 391.1621 | 391.4827 | 391.6231 | 394.8878 | 395.919 | 395.5744 | 395.6564 | 395.4878 | 395.7836 | 386.4995 | 387.2161 | 386.209 | 383.9177 | 383.451 | 383.5436 | 380.266 | 387.0678 | 387.1141 | 386.715 | 388.3051 | 388.6003 | 386.9339 | 388.0573 | 386.8793 | 386.1083 | 387.2325 | 387.2848 | 387.661 | 387.3199 | 389.1295 | 389.3866 | 388.0535 | 387.9746 | 386.0808 | 390.3037 | 393.3854 | 384.4915 | 382.6445 | 387.1941 | 388.041 | 386.3311 | 385.9894 | 392.2217 | 392.497 | 393.0242 | 393.0669 | 392.8805 | 392.1883 | 392.9397 | 392.9462 | 385.4534 | 385.9318 | 385.4666 | 391.3109 | 392.0096 | 392.3896 | 391.8893 | 391.1028 | 391.6318 | 391.0598 | 389.1586 | 388.2585 | 388.0193 | 391.5457 | 391.7004 | 391.6513 | 391.6281 | 394.1862 | 394.0377 | 394.0753 | 393.7108 | 390.3849 | 390.0565 | 390.0321 | 387.9602 | 387.6589 | 386.748 | 391.1575 | 391.2625 | 391.8539 | 391.0021 | 390.918 | 390.7022 | 390.0443 | 390.6852 | 386.2664 | 387.7201 | 386.4187 | 385.6258 | 386.2263 | 386.3082 | 385.8322 | 386.313 | 386.077 | 387.1243 | 384.8367 | 385.8713 | 389.9212 | 390.6934 | 390.4132 | 388.0284 | 387.7968 | 385.5854 | 391.2403 | 390.3618 | 390.6406 | 388.0632 | 387.6086 | 388.1396 | 388.5059 | 389.1731 | 388.4681 | 392.7734 | 392.2895 | 392.4039 | 389.1583 | 388.4236 | 388.9763 | 386.8425 | 387.427 | 388.3141 | 394.2373 | 392.8414 | 394.1276 | 394.1279 | 393.7126 | 393.8521 | 384.4383 | 382.4084 | 382.4591 | 380.6678 | 380.8088 | 380.7841 | 385.9788 | 388.4112 | 386.6851 | 387.3548 | 388.1031 | 385.9949 | 383.6124 | 383.9015 | 383.8327 | 393.0576 | 393.307 | 392.1948 | 393.6078 | 394.125 | 393.3839 | 387.068 | 387.3742 | 387.6238 | 387.2894 | 387.2281 | 387.8787 | 394.4284 | 394.9185 | 394.3318 | 391.5428 | 392.2126 | 392.3051 | 392.1862 | 392.4463 | 393.1044 | 392.0617 | 392.7169 | 391.9505 | 393.0471 | 392.4918 | 393.485 | 391.1986 | 389.6418 | 390.5072 | 384.7327 | 384.0511 | 383.9133 | 382.5064 | 382.5863 | 383.3703 | 390.3917 | 389.8806 | 389.5439 | 389.6052 | 390.4742 | 389.9022 | 384.466 | 385.0862 | 385.1826 | 384.8484 | 385.9821 | 385.1639 | 385.4979 | 384.6889 | 384.8355 | 384.3029 | 384.8881 | 384.7271 | 386.7691 | 387.0174 | 386.7713 | 389.764 | 389.2766 | 389.8944 | 389.5468 | 390.1634 | 389.7628
175 | Voltage Phase 2 |  | 393.9749 | 393.4142 | 392.2578 | 390.9904 | 394.8124 | 394.7076 | 392.6014 | 392.91 | 392.6588 | 391.0334 | 390.9886 | 390.7425 | 391.3545 | 389.3866 | 390.6586 | 394.0321 | 394.265 | 393.2913 | 392.836 | 394.2957 | 394.9097 | 389.1173 | 388.9279 | 389.3839 | 393.8973 | 394.2282 | 394.0718 | 394.6437 | 394.13 | 394.9829 | 394.5494 | 394.8925 | 393.8838 | 392.0005 | 392.5687 | 392.052 | 388.3751 | 381.3617 | 382.4113 | 380.4896 | 383.0838 | 382.5013 | 382.6371 | 382.0497 | 381.9776 | 382.4868 | 383.7468 | 384.1285 | 383.8503 | 385.13 | 385.1713 | 385.1044 | 383.2865 | 383.0254 | 381.8683 | 386.4217 | 387.2332 | 392.6136 | 391.3571 | 394.3681 | 395.2393 | 393.9332 | 393.6915 | 390.1962 | 390.1006 | 390.6992 | 393.2138 | 392.9273 | 392.4963 | 393.7762 | 393.3405 | 393.7981 | 393.7752 | 393.8197 | 389.7375 | 389.7364 | 390.5642 | 389.8905 | 390.2445 | 390.8649 | 390.3955 | 388.7134 | 387.4984 | 387.3201 | 392.7039 | 393.0231 | 392.7546 | 392.6679 | 389.1196 | 386.8175 | 386.186 | 386.4724 | 386.8192 | 384.3913 | 384.1288 | 383.4532 | 381.8725 | 383.0827 | 387.6346 | 385.6198 | 386.3508 | 385.4752 | 384.74 | 385.4522 | 384.3005 | 384.2383 | 384.4596 | 384.53 | 382.136 | 382.6006 | 380.7853 | 382.1909 | 381.5777 | 382.6405 | 382.0448 | 382.3062 | 379.0173 | 380.6895 | 389.8078 | 390.872 | 390.9857 | 385.1261 | 386.0327 | 383.0533 | 387.1915 | 386.4386 | 385.0125 | 385.0146 | 384.1147 | 383.7226 | 384.1563 | 382.2769 | 383.7354 | 392.2608 | 391.4256 | 392.2731 | 386.9452 | 386.1435 | 386.5744 | 384.1817 | 385.0788 | 386.017 | 394.5173 | 393.1307 | 394.3738 | 394.4861 | 393.8972 | 394.4909 | 392.2379 | 389.9401 | 390.2834 | 388.3575 | 388.4059 | 388.4544 | 383.8016 | 384.6028 | 384.0892 | 383.3555 | 384.4915 | 384.8742 | 380.9635 | 380.8886 | 381.7089 | 386.5121 | 386.6692 | 386.2132 | 392.8599 | 393.3441 | 392.0817 | 383.3045 | 384.9562 | 384.4667 | 385.0195 | 384.72 | 386.0963 | 393.5642 | 394.1342 | 393.4664 | 391.6559 | 392.2469 | 392.5896 | 392.1597 | 392.0434 | 392.6248 | 392.5512 | 393.2515 | 392.6169 | 391.3721 | 390.5262 | 392.1206 | 388.3649 | 387.1652 | 387.8743 | 392.0636 | 391.4456 | 391.5766 | 389.878 | 390.4479 | 391.4321 | 384.7912 | 384.8364 | 384.1166 | 383.666 | 384.3897 | 383.7888 | 380.3766 | 379.2928 | 382.8506 | 382.7148 | 382.0615 | 379.8943 | 379.9744 | 381.5645 | 380.7676 | 383.5368 | 382.2668 | 381.3159 | 381.255 | 381.2449 | 381.4081 | 388.6539 | 388.3981 | 388.2902 | 387.9699 | 388.9746 | 388.2922
176 | Voltage Phase 3 |  | 391.2808 | 391.6155 | 390.5056 | 391.4287 | 393.5194 | 393.2478 | 389.2656 | 388.8925 | 388.3023 | 388.5757 | 388.3694 | 388.6977 | 388.6993 | 387.3777 | 388.3758 | 392.0933 | 392.26 | 391.281 | 391.1024 | 392.7999 | 392.9307 | 389.6655 | 389.4943 | 389.5616 | 392.2081 | 392.6364 | 392.5833 | 391.8213 | 391.5823 | 391.8355 | 390.504 | 389.7223 | 390.6406 | 390.1956 | 391.4757 | 389.4873 | 388.5945 | 378.2448 | 378.4693 | 378.7195 | 380.1138 | 379.8886 | 378.0668 | 379.1275 | 377.8041 | 377.9981 | 378.4664 | 378.1517 | 378.7359 | 378.3372 | 379.3531 | 380.1629 | 379.5038 | 378.6259 | 376.8959 | 380.4741 | 383.6371 | 389.4464 | 388.6583 | 390.8068 | 391.7011 | 390.6139 | 392.7518 | 390.3921 | 391.5788 | 391.7321 | 392.6519 | 391.7614 | 391.829 | 392.9538 | 392.1305 | 392.1866 | 391.8255 | 391.5054 | 388.5952 | 389.0021 | 389.4646 | 388.8311 | 387.4098 | 388.0265 | 387.5187 | 385.4316 | 384.5835 | 384.5211 | 392.9779 | 392.6905 | 392.4282 | 392.4696 | 384.3642 | 385.4394 | 385.7145 | 384.8034 | 381.5387 | 381.4186 | 380.8696 | 379.7609 | 380.144 | 378.1388 | 381.3724 | 382.0777 | 382.6908 | 382.0544 | 383.4097 | 383.0437 | 382.4328 | 383.8591 | 376.816 | 378.1704 | 377.0081 | 376.334 | 376.3874 | 376.6089 | 377.3972 | 376.5607 | 376.067 | 377.8738 | 375.5023 | 377.1144 | 385.2007 | 385.8763 | 385.6395 | 377.9299 | 378.2784 | 375.522 | 381.5492 | 380.4007 | 380.6953 | 378.4195 | 378.381 | 377.9886 | 379.1902 | 380.4515 | 379.6748 | 388.3934 | 387.6425 | 387.5642 | 386.1824 | 385.7353 | 386.064 | 385.3956 | 386.3858 | 387.1795 | 393.0236 | 391.7246 | 393.1274 | 392.8652 | 391.8794 | 392.5566 | 388.8506 | 386.3064 | 387.4751 | 388.7902 | 387.4941 | 388.4305 | 377.1754 | 378.5501 | 377.6105 | 377.6129 | 378.8078 | 377.4156 | 375.1075 | 375.1915 | 375.0409 | 385.1267 | 385.8653 | 384.0839 | 389.409 | 390.002 | 390.1587 | 377.7938 | 378.6241 | 378.7119 | 378.1399 | 378.0881 | 378.6528 | 390.7939 | 390.9431 | 390.6616 | 390.236 | 390.7692 | 391.3252 | 391.122 | 390.728 | 391.4075 | 390.6681 | 391.7038 | 391.3223 | 388.8563 | 388.5456 | 389.3978 | 389.0002 | 388.4378 | 387.9814 | 388.5136 | 388.1125 | 387.9954 | 390.33 | 390.051 | 390.4805 | 381.1677 | 380.4558 | 380.4967 | 380.3591 | 380.7927 | 380.0731 | 375.4501 | 376.389 | 376.0446 | 375.6615 | 376.2504 | 376.1259 | 376.1691 | 376.0052 | 375.3262 | 375.6626 | 375.8416 | 375.6775 | 378.3147 | 377.8954 | 377.5746 | 386.0108 | 384.6071 | 385.6502 | 385.3656 | 385.7824 | 385.398
177 | Power Factor |  | 0.98755 | 0.98744 | 0.98699 | 0.98699 | 0.98712 | 0.9867 | 0.98768 | 0.98686 | 0.98799 | 0.9873 | 0.98733 | 0.98751 | 0.98775 | 0.98724 | 0.98721 | 1 | 1 | 1 | 1 | 1 | 1 | 0.98655 | 0.98532 | 0.98654 | 0.98696 | 0.98601 | 0.98688 | 0.98784 | 0.98756 | 0.98743 | 0.98783 | 0.98774 | 0.98748 | 0.98748 | 0.98699 | 0.98715 | 0.98667 | 0.9852 | 0.98551 | 0.98462 | 0.98521 | 0.98478 | 0.98558 | 0.9848 | 0.98503 | 0.98369 | 0.9837 | 0.98407 | 0.98406 | 0.98416 | 0.98374 | 0.98414 | 0.98354 | 0.98404 | 0.98406 | 0.98393 | 0.98405 | 0.98781 | 0.98767 | 0.98838 | 0.98855 | 0.988 | 0.98771 | 0.98723 | 0.98696 | 0.98691 | 1 | 1 | 1 | 1 | 1 | 0.98669 | 0.98647 | 0.98684 | 0.98596 | 0.98538 | 0.98673 | 0.98612 | 0.9877 | 0.98836 | 0.98796 | 0.98857 | 0.98722 | 0.98763 | 1 | 1 | 1 | 1 | 0.98532 | 0.98452 | 0.98438 | 0.9845 | 0.98478 | 0.98406 | 0.98362 | 0.98435 | 0.9836 | 0.9844 | 0.9847 | 0.98371 | 0.98447 | 0.98447 | 0.98427 | 0.98479 | 0.98453 | 0.98432 | 0.98513 | 0.9844 | 0.9839 | 0.98476 | 0.98332 | 0.98379 | 0.98405 | 0.98415 | 0.98395 | 0.98548 | 0.9845 | 0.98535 | 0.98847 | 0.98794 | 0.98797 | 0.98367 | 0.98392 | 0.98383 | 0.98403 | 0.98392 | 0.98361 | 0.9841 | 0.98392 | 0.98396 | 0.9854 | 0.98473 | 0.9853 | 0.98804 | 0.98816 | 0.98677 | 0.98627 | 0.98617 | 0.98708 | 0.9861 | 0.98722 | 0.98701 | 1 | 1 | 1 | 1 | 1 | 1 | 0.98802 | 0.98709 | 0.98666 | 0.98743 | 0.98732 | 0.9872 | 0.98471 | 0.98482 | 0.98516 | 0.9845 | 0.98471 | 0.98494 | 0.98423 | 0.98456 | 0.98481 | 0.98538 | 0.98537 | 0.98586 | 0.98748 | 0.98732 | 0.98697 | 0.9841 | 0.98392 | 0.98415 | 0.98467 | 0.98444 | 0.98485 | 0.98686 | 0.98691 | 0.98711 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.98646 | 0.98574 | 0.98648 | 0.98709 | 0.98694 | 0.98769 | 0.98658 | 0.98698 | 0.98727 | 0.98676 | 0.98606 | 0.98656 | 0.98383 | 0.98408 | 0.98409 | 0.98386 | 0.98359 | 0.98377 | 0.98436 | 0.98376 | 0.98432 | 0.98458 | 0.98406 | 0.98349 | 0.98361 | 0.98404 | 0.98399 | 0.98468 | 0.98406 | 0.98419 | 0.98508 | 0.98484 | 0.98492 | 0.98668 | 0.98822 | 0.98694 | 0.98746 | 0.9867 | 0.98703
178 | KvA |  | 121.0052 | 120.3011 | 121.0052 | 129.2498 | 129.6764 | 129.3082 | 59.896 | 60.5904 | 59.9891 | 54.8808 | 54.6528 | 55.1598 | 55.2447 | 54.8844 | 54.9074 | 19.3043 | 19.9726 | 19.6288 | 20.6619 | 20.0945 | 21.2378 | 53.3917 | 53.5965 | 53.4939 | 58.0551 | 57.343 | 58.0521 | 60.2698 | 59.5153 | 60.0978 | 123.8604 | 122.6675 | 123.1013 | 130.2757 | 130.0259 | 130.4278 | 128.0659 | 233.3126 | 233.1979 | 233.3763 | 233.2087 | 233.7648 | 233.7109 | 232.3788 | 233.665 | 259.8334 | 260.2949 | 258.7534 | 256.1062 | 258.9574 | 261.2513 | 255.8256 | 256.6155 | 253.7489 | 252.1496 | 257.1688 | 254.8527 | 117.4686 | 117.7043 | 117.9701 | 119.1463 | 119.4082 | 119.2404 | 52.8883 | 52.5699 | 52.6022 | 19.3076 | 18.9079 | 19.4552 | 20.8503 | 19.9527 | 127.9084 | 128.1674 | 128.222 | 56.6457 | 57.1396 | 57.8228 | 57.7325 | 60.1257 | 60.1361 | 59.7488 | 60.5038 | 61.2534 | 61.1388 | 20.7578 | 20.9116 | 20.5648 | 20.537 | 230.0805 | 230.7365 | 229.9608 | 229.4551 | 254.0111 | 254.6045 | 256.0167 | 251.9009 | 252.7801 | 252.3068 | 256.9721 | 255.2648 | 254.8903 | 255.6355 | 253.5096 | 254.5253 | 252.7785 | 252.8513 | 253.6246 | 254.2038 | 254.2623 | 253.9183 | 256.7501 | 257.7773 | 254.4604 | 253.5835 | 253.7932 | 230.9585 | 230.0722 | 230.391 | 59.794 | 59.6766 | 59.3078 | 255.791 | 256.2965 | 254.5574 | 254.4336 | 254.1602 | 253.5396 | 256.361 | 256.8544 | 254.819 | 230.0892 | 229.2124 | 229.5441 | 59.4338 | 59.6337 | 58.9141 | 56.8184 | 56.3691 | 57.0827 | 52.5802 | 52.7512 | 52.6716 | 19.7068 | 19.8131 | 19.7217 | 20.5707 | 21.0419 | 20.5815 | 118.9043 | 119.7305 | 118.8477 | 129.1187 | 127.9567 | 128.3392 | 253.8509 | 250.6833 | 252.5093 | 255.214 | 253.5668 | 252.1986 | 252.9578 | 251.668 | 253.2047 | 228.8341 | 228.8026 | 227.0325 | 59.0824 | 59.7982 | 59.0778 | 254.5256 | 257.9491 | 253.7417 | 258.0413 | 258.8129 | 256.5197 | 59.6794 | 59.3391 | 58.9123 | 20.9593 | 21.0495 | 20.6696 | 19.3961 | 19.6168 | 19.3655 | 20.7379 | 20.5422 | 20.5998 | 56.7506 | 56.3085 | 56.3237 | 53.1414 | 53.4341 | 52.8411 | 119.2301 | 118.6714 | 116.4805 | 130.037 | 129.5437 | 130.3497 | 255.8562 | 254.1225 | 253.5172 | 255.6666 | 254.9997 | 256.5547 | 253.0146 | 253.5153 | 254.1274 | 255.9599 | 253.9582 | 254.225 | 256.0091 | 255.5231 | 255.4144 | 254.5846 | 259.2486 | 257.4258 | 230.6366 | 230.2307 | 229.4967 | 59.1999 | 59.5955 | 59.3007 | 59.5332 | 59.4537 | 59.5235
179 | Avg Amps |  | 198.2169 | 197.0177 | 198.1755 | 210.8151 | 209.8403 | 209.4777 | 109.7621 | 110.3409 | 109.7795 | 102.2083 | 102.3627 | 102.6635 | 102.636 | 102.6302 | 102.4973 | 41.5579 | 42.4692 | 42.1896 | 44.5324 | 43.8586 | 44.9091 | 100.0919 | 100.4658 | 100.2085 | 107.0996 | 105.6806 | 106.7282 | 109.6902 | 109.6648 | 109.4475 | 201.7879 | 200.1951 | 200.5353 | 212.5506 | 211.6159 | 212.5504 | 210.0381 | 375.117 | 374.5921 | 375.3003 | 373.8012 | 374.384 | 375.7209 | 372.852 | 375.7386 | 415.9383 | 415.9529 | 413.5079 | 409.3216 | 413.4576 | 415.9506 | 407.512 | 409.4437 | 405.81 | 404.7845 | 408.3836 | 402.3259 | 193.9921 | 194.5816 | 193.239 | 194.2933 | 195.6097 | 194.8844 | 98.627 | 97.9913 | 98.3123 | 42.757 | 42.0387 | 42.7479 | 44.6883 | 44.064 | 209.0182 | 209.116 | 209.2705 | 105.4131 | 105.8838 | 107.1133 | 106.5708 | 110.347 | 110.2649 | 110.1396 | 111.1045 | 111.9844 | 112.1136 | 44.5951 | 44.6187 | 44.4138 | 44.0918 | 363.5962 | 364.7379 | 363.4716 | 363.105 | 403.234 | 404.8295 | 406.9483 | 402.7558 | 403.9368 | 404.5305 | 407.4279 | 404.8705 | 404.0624 | 405.9487 | 401.927 | 403.6808 | 401.7732 | 400.8173 | 407.1818 | 406.2521 | 408.0559 | 408.2743 | 412.4587 | 413.3566 | 408.509 | 406.614 | 407.4392 | 371.7415 | 372.0711 | 371.6853 | 109.5799 | 109.3711 | 108.5172 | 408.4797 | 408.6728 | 408.4344 | 403.047 | 403.5292 | 403.0218 | 409.3046 | 410.3861 | 407.1268 | 368.4741 | 367.0903 | 367.7692 | 108.4562 | 108.934 | 107.7902 | 106.6318 | 105.8933 | 106.5109 | 100.0822 | 99.8304 | 99.8575 | 43.1081 | 42.6139 | 42.6379 | 44.7164 | 44.8675 | 44.6982 | 195.729 | 199.1823 | 197.8044 | 212.0562 | 210.561 | 210.6585 | 407.0918 | 400.6004 | 405.0268 | 408.9162 | 405.0924 | 404.1652 | 408.2635 | 405.8608 | 408.0494 | 363.4311 | 363.1467 | 361.3949 | 110.2655 | 110.4119 | 109.5581 | 407.6017 | 411.7574 | 405.381 | 412.5592 | 413.809 | 410.5173 | 109.4845 | 109.3925 | 108.3627 | 45.2382 | 45.4861 | 45.2429 | 43.0898 | 43.1261 | 42.7527 | 44.5537 | 44.4016 | 45.2219 | 105.9238 | 105.4715 | 105.1915 | 99.9578 | 101.2091 | 100.1946 | 196.8127 | 196.5541 | 193.1145 | 213.1617 | 212.4964 | 213.2865 | 406.8833 | 405.2153 | 404.3819 | 407.6137 | 405.689 | 409.1529 | 408.1145 | 408.413 | 408.8321 | 411.6316 | 408.0623 | 409.5295 | 411.6893 | 411.4045 | 411.7074 | 409.7437 | 417.1424 | 414.6237 | 371.1069 | 371.0691 | 369.6204 | 109.5898 | 109.7627 | 108.5888 | 109.5579 | 109.5629 | 109.3088
180 | Avg Volts |  | 390.3302 | 390.0542 | 389.052 | 388.5241 | 391.5729 | 391.4151 | 391.7522 | 391.6864 | 391.2579 | 390.6733 | 390.5175 | 390.6552 | 390.8813 | 389.3611 | 390.2671 | 392.9801 | 393.1762 | 392.2882 | 391.9089 | 393.3145 | 393.8253 | 389.9816 | 389.9683 | 390.1896 | 393.6644 | 394.2612 | 394.0765 | 394.0405 | 393.7334 | 394.2007 | 390.5176 | 390.6103 | 390.2445 | 388.7046 | 389.1651 | 388.361 | 385.7452 | 382.2248 | 382.6649 | 381.9747 | 383.8342 | 383.6634 | 382.5459 | 383.0782 | 382.2204 | 382.1977 | 383.1486 | 383.1883 | 383.4158 | 383.5957 | 384.5513 | 384.8846 | 383.6146 | 383.2086 | 381.615 | 385.7331 | 388.0852 | 388.8505 | 387.5533 | 390.7897 | 391.6604 | 390.2927 | 390.8109 | 390.9367 | 391.3921 | 391.8185 | 392.9775 | 392.5231 | 392.1712 | 393.2232 | 392.8057 | 390.4794 | 390.5108 | 390.2639 | 389.8812 | 390.2494 | 390.8061 | 390.2036 | 389.5857 | 390.1744 | 389.658 | 387.7679 | 386.7801 | 386.6201 | 392.4092 | 392.4713 | 392.278 | 392.2552 | 389.2233 | 388.7649 | 388.6586 | 388.3289 | 386.2476 | 385.2888 | 385.0102 | 383.7248 | 383.2251 | 382.6565 | 386.7215 | 386.32 | 386.9652 | 386.1772 | 386.3559 | 386.3994 | 385.5925 | 386.2609 | 382.514 | 383.4735 | 381.8543 | 381.5201 | 381.133 | 381.7026 | 381.6024 | 381.8381 | 381.3962 | 382.4348 | 379.7855 | 381.225 | 388.3099 | 389.1472 | 389.0128 | 383.6948 | 384.036 | 381.3869 | 386.6603 | 385.7337 | 385.4495 | 383.8324 | 383.3681 | 383.2836 | 383.9508 | 383.9672 | 383.9595 | 391.1425 | 390.4525 | 390.747 | 387.4286 | 386.7675 | 387.2049 | 385.4733 | 386.2972 | 387.1702 | 393.9261 | 392.5656 | 393.8763 | 393.8264 | 393.1631 | 393.6332 | 388.5089 | 386.2183 | 386.7392 | 385.9385 | 385.5696 | 385.8897 | 382.3186 | 383.8547 | 382.7949 | 382.7744 | 383.8008 | 382.7616 | 379.8945 | 379.9939 | 380.1941 | 388.2321 | 388.6138 | 387.4973 | 391.9589 | 392.4904 | 391.8748 | 382.7221 | 383.6515 | 383.6008 | 383.4829 | 383.3454 | 384.2093 | 392.9288 | 393.332 | 392.82 | 391.1449 | 391.7429 | 392.0733 | 391.8226 | 391.7393 | 392.3789 | 391.7603 | 392.5574 | 391.9632 | 391.0918 | 390.5212 | 391.6678 | 389.5213 | 388.4149 | 388.7876 | 388.4366 | 387.8697 | 387.8284 | 387.5715 | 387.6951 | 388.4276 | 385.4502 | 385.0576 | 384.7191 | 384.5434 | 385.2189 | 384.588 | 380.0976 | 380.256 | 381.3593 | 381.0749 | 381.4313 | 380.3947 | 380.5471 | 380.7529 | 380.3098 | 381.1674 | 380.9988 | 380.5735 | 382.1129 | 382.0526 | 381.918 | 388.1429 | 387.4273 | 387.945 | 387.6275 | 388.3068 | 387.8177
181 | Hz |  | 49.945 | 49.9392 | 49.9397 | 49.9102 | 50.0631 | 50.0327 | 50.0306 | 49.9723 | 49.9556 | 50.0876 | 49.9798 | 50.1305 | 50.0809 | 50.0327 | 49.9785 | 49.9705 | 49.9765 | 49.955 | 49.9433 | 49.9928 | 50.0868 | 49.926 | 49.9431 | 49.9604 | 49.8776 | 49.9252 | 49.9871 | 50.0405 | 50.0211 | 50.0631 | 50.0717 | 50.0511 | 50.0466 | 49.9605 | 49.9962 | 49.9993 | 50.0326 | 50.125 | 50.1317 | 50.0952 | 50.0735 | 50.0325 | 50.029 | 49.9764 | 50.0032 | 50.0087 | 50.0111 | 50.0476 | 49.9611 | 50.0178 | 50.0507 | 50.0536 | 49.9935 | 50.004 | 49.9297 | 50.0601 | 50.024 | 50.0575 | 50.0123 | 50.1775 | 50.108 | 50.0719 | 50.073 | 49.9657 | 49.961 | 50.0151 | 49.9395 | 49.9556 | 49.9676 | 49.948 | 49.8984 | 49.8999 | 49.8783 | 49.8943 | 50.0758 | 50.0657 | 50.0702 | 49.9924 | 50.0805 | 50.0579 | 50.0693 | 49.9713 | 49.9505 | 49.915 | 49.9437 | 49.9621 | 49.98 | 49.9866 | 50.112 | 50.1316 | 50.1773 | 50.1568 | 50.1493 | 50.1049 | 49.9818 | 49.9969 | 49.998 | 50.0716 | 49.9889 | 49.9143 | 49.9113 | 49.9202 | 49.942 | 49.9816 | 49.9231 | 50.0247 | 49.9589 | 50.0579 | 49.9014 | 50.1222 | 50.0678 | 50.1 | 50.087 | 50.0778 | 50.1147 | 49.9431 | 49.9257 | 49.9474 | 50.0748 | 50.0952 | 50.0442 | 49.9403 | 49.9936 | 49.981 | 50.0087 | 49.9202 | 49.926 | 50.0725 | 50.0518 | 50.0421 | 50.041 | 50.0088 | 50.0214 | 50.1845 | 50.1506 | 50.0839 | 50.0539 | 50.0693 | 50.0828 | 50.0186 | 50.1223 | 49.985 | 50.0648 | 50.0385 | 50.0368 | 49.9596 | 49.9304 | 49.9603 | 49.9857 | 49.9625 | 49.9219 | 49.9219 | 49.9521 | 49.8836 | 49.9773 | 50.0042 | 50.0267 | 49.9339 | 50.0298 | 49.9564 | 49.9121 | 49.9334 | 50.0116 | 49.9703 | 49.982 | 49.9802 | 49.948 | 50.0155 | 49.9794 | 50.0346 | 50.0662 | 50.0362 | 49.9878 | 50.0324 | 50.0491 | 50.1113 | 50.1294 | 50.1185 | 49.9954 | 50.0314 | 50.0429 | 49.9882 | 50.0369 | 50.0485 | 50.03 | 50.0481 | 50.0839 | 49.9332 | 49.9226 | 49.9453 | 50.0773 | 50.051 | 50.0067 | 50.0476 | 50.0158 | 50.0189 | 49.9512 | 50.0132 | 50.0495 | 50.0109 | 49.9134 | 49.858 | 49.9596 | 49.9528 | 49.8659 | 50.0627 | 50.0535 | 50.0911 | 50.0692 | 50.084 | 49.9586 | 49.9795 | 49.9591 | 49.9431 | 50.0596 | 49.9825 | 49.9975 | 49.9474 | 49.9906 | 49.9671 | 49.9524 | 49.9908 | 49.955 | 49.9652 | 49.99 | 49.9985
182
183 | Motor Temperatures
184 | T1 (terminal post) |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
185 | T2 (ambient terminal box) |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
186 | T3 (ambient rig enclosure) |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
187 | T4 |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
188 | T5 |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
189 | T6 |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
190 | T7 |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
191 | T8 |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
192 | T9 |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
193 | T10 |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
194 | T11 |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
195 | T12 |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
196 | T13 |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
197 | T14 |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
198 | T15 |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
199 | T16 |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
200 | T17 |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
201 | T18 |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
202 | T19 |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
203 | T20 |  | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1
204 | T21 |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
205 | T22 |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
206 | T23 |  | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2
207 | T24 |  | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2
208 | T25 |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
209 | T26 |  | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1
210 | T27 |  | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2
211 | T28 |  | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2
212 | T29 |  | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2
213 | T30 |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
214 | T spare 1
215 | T spare 2
216
217 | Max Temp |  | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2
218 | Min Temp |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
219 | Avg Temp |  | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13
220
221
222 | Calculated Data
223 | Suction Flow at FM conditions | m^3/hr | 708.5533 | 708.239 | 708.9824 | 753.3499 | 754.6669 | 753.9793 | 459.6092 | 459.1117 | 458.4765 | 402.5823 | 402.5339 | 405.1102 | 404.9291 | 403.8661 | 404.6599 | 179.8175 | 180.006 | 180.6444 | 192.8903 | 193.2239 | 196.0088 | 402.7638 | 402.2725 | 402.9232 | 432.2026 | 432.5648 | 432.9053 | 431.5543 | 433.2524 | 432.0915 | 717.0727 | 716.8703 | 717.2743 | 752.582 | 752.1472 | 750.0536 | 744.4851 | 1058.93 | 1061.3358 | 1060.2397 | 1059.7164 | 1057.6105 | 1057.1208 | 1059.3345 | 1060.6859 | 1120.7046 | 1122.7851 | 1125.4913 | 1126.2432 | 1125.8052 | 1122.9724 | 1128.7409 | 1127.6508 | 1125.5224 | 1094.5429 | 1094.4888 | 1094.2393 | 682.6334 | 679.5682 | 680.3845 | 695.7665 | 697.6081 | 696.4332 | 389.4074 | 389.6914 | 388.8562 | 163.5925 | 166.9995 | 155.5166 | 179.5908 | 180.9583 | 735.1244 | 734.6323 | 734.4339 | 421.724 | 421.0643 | 422.7079 | 422.476 | 444.7665 | 446.4117 | 445.5893 | 444.5517 | 445.6618 | 445.5565 | 175.3381 | 180.2559 | 176.42 | 182.0249 | 1032.9634 | 1033.6461 | 1034.0407 | 1036.3232 | 1100.9827 | 1103.1869 | 1101.1818 | 1107.5314 | 1112.7848 | 1109.5549 | 1106.4373 | 1107.5957 | 1107.953 | 1106.9884 | 1107.5945 | 1107.8572 | 1108.7734 | 1107.5527 | 1138.231 | 1138.4527 | 1142.0461 | 1141.9203 | 1141.2077 | 1141.1278 | 1145.9468 | 1145.4018 | 1146.4713 | 1066.1123 | 1071.2948 | 1069.3823 | 457.3374 | 457.0021 | 458.2307 | 1135.4609 | 1134.0225 | 1134.7348 | 1144.781 | 1140.8975 | 1140.9929 | 1147.2442 | 1141.9289 | 1147.5331 | 1068.0927 | 1069.1057 | 1069.6966 | 458.1127 | 459.1281 | 460.5906 | 432.0657 | 432.1927 | 432.6537 | 402.8876 | 402.368 | 402.4024 | 165.5452 | 166.7393 | 175.6701 | 189.3809 | 185.1499 | 186.6649 | 721.4893 | 722.4118 | 722.2458 | 763.2945 | 764.0845 | 765.0877 | 1133.5116 | 1132.8965 | 1126.0625 | 1134.0115 | 1136.7857 | 1137.393 | 1134.7679 | 1137.4385 | 1134.6126 | 1063.7015 | 1072.4233 | 1068.1636 | 455.8056 | 454.8754 | 455.8404 | 1141.5298 | 1139.8152 | 1139.1977 | 1141.3384 | 1142.9751 | 1143.4111 | 456.1142 | 453.9677 | 458.4884 | 186.2945 | 187.6422 | 189.594 | 174.9865 | 174.8234 | 175.5865 | 186.106 | 188.1258 | 189.2072 | 431.7579 | 431.3527 | 431.2683 | 400.6899 | 400.7723 | 400.0052 | 715.6684 | 710.2543 | 701.2182 | 765.1471 | 764.9557 | 764.682 | 1131.1487 | 1130.6586 | 1131.5999 | 1131.7888 | 1131.9556 | 1130.0768 | 1134.7434 | 1136.2509 | 1136.3222 | 1135.5056 | 1134.2828 | 1134.8401 | 1137.0787 | 1136.5509 | 1135.5334 | 1136.037 | 1137.9212 | 1135.7186 | 1063.9666 | 1063.7318 | 1064.1486 | 456.6768 | 458.1315 | 459.0695 | 456.3715 | 458.1036 | 457.2845
224 | Suction Flow at suction conditions (from Flowmeters) | m^3/hr | 731.8961 | 731.6168 | 731.7942 | 780.5865 | 782.1289 | 781.4163 | 465.9316 | 465.4707 | 465.061 | 407.198 | 407.0781 | 409.7502 | 409.4813 | 408.6627 | 409.1473 | 180.8857 | 180.8563 | 181.5073 | 193.9535 | 194.328 | 197.2309 | 407.2085 | 406.9548 | 408.074 | 437.8414 | 438.4573 | 438.477 | 437.2093 | 438.9258 | 437.6932 | 740.1854 | 739.7968 | 740.1364 | 779.2445 | 777.5309 | 776.7166 | 770.6592 | 1139.634 | 1141.4914 | 1142.1496 | 1141.2389 | 1139.0023 | 1138.3073 | 1141.7443 | 1140.959 | 1220.5253 | 1222.6087 | 1224.0078 | 1229.1848 | 1229.9968 | 1227.4021 | 1232.9103 | 1232.0966 | 1230.3022 | 1200.3594 | 1201.217 | 1201.2489 | 704.3695 | 702.4048 | 703.1388 | 718.9594 | 721.8457 | 719.985 | 394.8397 | 395.1843 | 394.316 | 164.3678 | 167.7678 | 156.0763 | 180.3324 | 181.8162 | 764.8714 | 763.9256 | 765.452 | 427.8803 | 427.0823 | 428.5392 | 428.09 | 451.9369 | 453.7461 | 452.6066 | 451.5341 | 452.9695 | 452.8054 | 176.9893 | 181.6006 | 177.4138 | 182.9027 | 1117.3446 | 1117.5182 | 1118.7084 | 1118.6845 | 1211.8179 | 1211.2473 | 1209.0505 | 1212.2486 | 1215.2424 | 1215.0122 | 1249.0351 | 1250.7126 | 1253.1355 | 1253.2126 | 1252.0274 | 1251.963 | 1252.9447 | 1254.3633 | 1256.8805 | 1255.3162 | 1258.7729 | 1262.2168 | 1261.3269 | 1261.9601 | 1265.7133 | 1266.0111 | 1266.2992 | 1162.7893 | 1163.9088 | 1165.2976 | 462.7573 | 463.0279 | 464.2643 | 1252.3665 | 1250.9616 | 1251.5064 | 1263.03 | 1258.0375 | 1259.3944 | 1265.5632 | 1261.9628 | 1269.3495 | 1164.6671 | 1164.425 | 1165.44 | 464.4651 | 464.9623 | 466.8919 | 437.5039 | 437.814 | 437.8271 | 406.7138 | 405.7478 | 406.3865 | 166.0037 | 167.2912 | 176.1108 | 189.6091 | 185.4768 | 187.0722 | 746.2678 | 747.1896 | 747.602 | 792.4345 | 793.596 | 793.3262 | 1243.2446 | 1245.3293 | 1242.2904 | 1247.5352 | 1250.4209 | 1251.6936 | 1250.9299 | 1250.6975 | 1250.6288 | 1158.9234 | 1165.8114 | 1159.4545 | 461.1849 | 459.5543 | 461.1948 | 1256.2799 | 1257.0348 | 1256.4184 | 1257.9322 | 1258.709 | 1259.3412 | 462.5132 | 460.4154 | 464.537 | 186.44 | 187.9147 | 189.8132 | 175.3701 | 175.2318 | 175.9166 | 186.3748 | 188.6482 | 189.6793 | 436.9537 | 436.4958 | 436.3067 | 404.4496 | 404.2033 | 403.862 | 738.3737 | 733.4054 | 724.6351 | 794.4629 | 793.8774 | 794.6621 | 1243.3019 | 1242.4812 | 1243.5577 | 1245.3325 | 1245.4595 | 1241.7175 | 1247.5853 | 1251.3143 | 1248.6389 | 1249.559 | 1247.7942 | 1250.7645 | 1250.8751 | 1250.0629 | 1250.0384 | 1250.5325 | 1251.2034 | 1250.1394 | 1154.3388 | 1152.2686 | 1153.5369 | 463.7783 | 465.2845 | 466.0843 | 463.2867 | 465.4362 | 463.937
225 | Suction Flow at suction Conditions (from orifice Plate) | m^3/hr | 588.6431 | 587.4978 | 589.1919 | 626.3167 | 625.8564 | 625.6469 | 360.7214 | 357.4955 | 359.6043 | 309.3802 | 307.6276 | 308.8888 | 309.5396 | 308.8799 | 306.5254 | 83.1324 | 83.0887 | 85.7477 | 105.4488 | 103.3781 | 106.0117 | 310.7532 | 310.4954 | 310.4337 | 337.9718 | 337.6932 | 340.8582 | 340.0975 | 338.3671 | 338.3853 | 597.9771 | 599.3268 | 598.9668 | 632.4455 | 625.8082 | 626.5509 | 616.3912 | 912.7136 | 913.4674 | 915.0752 | 917.9553 | 913.0858 | 914.0106 | 913.2268 | 917.1187 | 982.4414 | 983.649 | 982.0972 | 989.5958 | 989.9525 | 992.9106 | 993.8674 | 992.8752 | 994.7658 | 963.8959 | 967.397 | 965.5232 | 570.29 | 571.6501 | 571.1958 | 576.2208 | 577.0197 | 579.2492 | 298.8347 | 297.5686 | 296.6989 | 70.9901 | 76.6304 | 75.7204 | 84.3887 | 92.4647 | 613.7579 | 610.5059 | 610.2641 | 327.2339 | 329.7415 | 329.6843 | 329.1593 | 350.768 | 350.1487 | 349.6766 | 345.6774 | 345.1779 | 346.7998 | 88.7528 | 88.1888 | 87.4609 | 87.0573 | 894.1563 | 897.4812 | 895.0107 | 897.7461 | 972.4105 | 975.1973 | 972.9486 | 979.9477 | 982.7264 | 980.4297 | 985.4754 | 986.4837 | 984.7731 | 985.9678 | 982.5348 | 986.1016 | 984.3795 | 985.9521 | 989.0984 | 988.2249 | 989.9247 | 1000.3143 | 996.2335 | 998.3187 | 998.5415 | 1001.3467 | 998.5198 | 913.8565 | 914.8163 | 919.7901 | 355.0406 | 354.4568 | 357.5956 | 991.9321 | 992.947 | 992.1709 | 1001.9422 | 998.8599 | 1001.378 | 1004.7608 | 1001.2675 | 1003.1321 | 921.8535 | 919.4395 | 920.5623 | 359.1456 | 357.1086 | 360.9452 | 341.6169 | 338.4678 | 338.6444 | 312.6246 | 308.1911 | 310.3888 | 71.8737 | 72.4298 | 79.4564 | 87.4731 | 92.388 | 93.7882 | 600.4855 | 597.4921 | 595.7325 | 633.1538 | 634.499 | 632.9529 | 994.4701 | 994.8971 | 994.8722 | 1000.5321 | 1003.5772 | 1000.3827 | 1000.2454 | 1001.554 | 1000.2746 | 920.4018 | 921.8313 | 924.1481 | 360.7183 | 357.9093 | 360.1539 | 1002.0917 | 1002.4822 | 999.9429 | 1002.0052 | 1000.967 | 1000.501 | 364.29 | 362.7464 | 362.9379 | 91.7744 | 88.6238 | 90.2832 | 75.193 | 71.4059 | 75.1379 | 90.2387 | 90.9917 | 90.8519 | 340.721 | 337.8976 | 339.5422 | 309.8672 | 310.5946 | 308.8829 | 595.4898 | 595.1123 | 587.5875 | 639.2919 | 638.7495 | 638.8348 | 1000.3437 | 997.8456 | 1000.4075 | 1000.782 | 1004.2599 | 1000.7665 | 1012.0703 | 1008.1887 | 1007.0367 | 1006.8095 | 1006.9985 | 1005.8167 | 1008.7199 | 1006.2551 | 1004.9013 | 1006.8729 | 1007.4786 | 1005.4438 | 927.2236 | 928.9986 | 929.4538 | 362.6215 | 364.0331 | 365.1436 | 363.8555 | 363.6709 | 363.7908
226 | ratio suction orifice / FM (suction conds) | % | 80.4272 | 80.3013 | 80.5133 | 80.2367 | 80.0196 | 80.0658 | 77.4194 | 76.803 | 77.3241 | 75.9778 | 75.5697 | 75.3847 | 75.5931 | 75.5831 | 74.9181 | 45.9585 | 45.9418 | 47.242 | 54.3681 | 53.1977 | 53.75 | 76.3131 | 76.2973 | 76.0729 | 77.1905 | 77.0185 | 77.7368 | 77.7883 | 77.0898 | 77.3111 | 80.7875 | 81.0124 | 80.9265 | 81.1614 | 80.4866 | 80.6666 | 79.9823 | 80.0883 | 80.024 | 80.1187 | 80.435 | 80.1654 | 80.2956 | 79.9852 | 80.3814 | 80.4933 | 80.4549 | 80.2362 | 80.5083 | 80.4841 | 80.8953 | 80.6115 | 80.5842 | 80.8554 | 80.3006 | 80.5347 | 80.3766 | 80.9646 | 81.3847 | 81.2351 | 80.1465 | 79.9367 | 80.453 | 75.6851 | 75.2987 | 75.244 | 43.1898 | 45.6765 | 48.515 | 46.7962 | 50.8562 | 80.2433 | 79.9169 | 79.726 | 76.4779 | 77.208 | 76.9321 | 76.8902 | 77.6144 | 77.1684 | 77.2584 | 76.5562 | 76.2034 | 76.5892 | 50.1458 | 48.5619 | 49.2977 | 47.5976 | 80.0251 | 80.3102 | 80.0039 | 80.2502 | 80.2439 | 80.5118 | 80.4721 | 80.8372 | 80.8667 | 80.693 | 78.8989 | 78.8737 | 78.5847 | 78.6752 | 78.4755 | 78.7644 | 78.5653 | 78.6018 | 78.6947 | 78.7232 | 78.642 | 79.2506 | 78.983 | 79.1086 | 78.8916 | 79.0946 | 78.8534 | 78.5918 | 78.5986 | 78.9318 | 76.7229 | 76.5519 | 77.0242 | 79.2046 | 79.3747 | 79.2781 | 79.3285 | 79.3983 | 79.5127 | 79.3924 | 79.3421 | 79.0273 | 79.1517 | 78.9608 | 78.9884 | 77.3246 | 76.8038 | 77.3081 | 78.0832 | 77.3086 | 77.3466 | 76.866 | 75.9563 | 76.3777 | 43.2964 | 43.2956 | 45.1173 | 46.1334 | 49.8111 | 50.1348 | 80.4652 | 79.9653 | 79.6858 | 79.8998 | 79.9524 | 79.7847 | 79.9899 | 79.8903 | 80.0837 | 80.2007 | 80.2592 | 79.9223 | 79.9601 | 80.0796 | 79.9817 | 79.4187 | 79.0721 | 79.7054 | 78.2155 | 77.8818 | 78.0915 | 79.7666 | 79.7498 | 79.5868 | 79.6549 | 79.5233 | 79.4464 | 78.7632 | 78.7868 | 78.1289 | 49.2246 | 47.1617 | 47.5642 | 42.8767 | 40.7494 | 42.7122 | 48.4178 | 48.2335 | 47.8976 | 77.9765 | 77.4114 | 77.8219 | 76.6145 | 76.8412 | 76.4823 | 80.6488 | 81.1437 | 81.0874 | 80.4684 | 80.4595 | 80.3907 | 80.4586 | 80.3107 | 80.4472 | 80.3626 | 80.6337 | 80.5953 | 81.1223 | 80.5704 | 80.6508 | 80.5732 | 80.7023 | 80.4161 | 80.6411 | 80.4964 | 80.3896 | 80.5155 | 80.5208 | 80.4265 | 80.3251 | 80.6234 | 80.5743 | 78.1885 | 78.2388 | 78.3428 | 78.5379 | 78.1355 | 78.4138
227 | Error message if orifice plate ≠ Suction FM | - | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
228
229
230 | isentropic compression DH | KJ/kg | 23.9068 | 23.9539 | 23.9926 | 24.0765 | 24.1659 | 24.137 | 17.8387 | 17.8348 | 17.7901 | 17.6621 | 17.6186 | 17.614 | 17.5831 | 17.6185 | 17.5547 | 13.8622 | 13.8754 | 13.8078 | 13.9171 | 13.93 | 13.8908 | 17.4814 | 17.4468 | 17.4123 | 17.3978 | 17.375 | 17.3405 | 17.3764 | 17.395 | 17.3615 | 24.1403 | 24.1532 | 24.1358 | 24.0721 | 24.0465 | 24.0353 | 24.0953 | 30.2522 | 30.2357 | 30.2757 | 30.2619 | 30.2427 | 30.2401 | 30.2288 | 30.2689 | 32.609 | 32.6896 | 32.5797 | 30.3316 | 30.2454 | 30.2446 | 30.1078 | 30.0184 | 29.9212 | 32.439 | 32.4924 | 32.4928 | 24.0778 | 24.0881 | 24.1833 | 24.1077 | 24.1173 | 24.1207 | 17.5006 | 17.5874 | 17.6112 | 13.935 | 13.9609 | 13.9461 | 13.9902 | 13.9002 | 23.879 | 23.8399 | 23.7801 | 17.4269 | 17.4004 | 17.416 | 17.3904 | 17.4404 | 17.3976 | 17.4039 | 18.6916 | 18.7543 | 18.6953 | 14.1866 | 14.1012 | 14.0413 | 13.9593 | 30.208 | 30.2837 | 30.3079 | 30.3579 | 30.231 | 30.2697 | 30.2537 | 30.6917 | 30.7726 | 30.5735 | 31.3299 | 31.3071 | 31.341 | 31.3432 | 31.0641 | 31.0878 | 31.0817 | 30.9129 | 32.6359 | 32.6445 | 32.7194 | 30.114 | 30.1259 | 30.2468 | 30.1461 | 30.1542 | 30.1818 | 30.0959 | 30.1725 | 30.0839 | 17.5783 | 17.5597 | 17.5226 | 32.5761 | 32.5417 | 32.4514 | 29.8141 | 29.7844 | 29.7366 | 30.3579 | 30.244 | 30.2517 | 30.0586 | 30.0869 | 30.1001 | 17.5526 | 17.5265 | 17.4218 | 17.6481 | 17.5801 | 17.7451 | 17.6013 | 17.5287 | 17.5399 | 13.8767 | 13.8889 | 13.7977 | 13.9763 | 13.9278 | 13.9065 | 23.992 | 23.8494 | 23.8626 | 23.9467 | 23.9479 | 23.8322 | 32.7875 | 32.5887 | 32.4273 | 30.1161 | 30.1182 | 30.1198 | 29.8366 | 29.6955 | 29.7901 | 30.378 | 30.5663 | 30.3549 | 17.6012 | 17.728 | 17.5448 | 30.1199 | 30.1564 | 30.2136 | 30.5246 | 30.5469 | 30.4696 | 17.4789 | 17.4934 | 17.5077 | 14.0779 | 14.0549 | 13.9952 | 13.784 | 14.2853 | 14.3089 | 14.1811 | 14.1269 | 14.1304 | 17.5108 | 17.4854 | 17.4952 | 17.4976 | 17.5056 | 17.5176 | 24.0307 | 24.0023 | 23.9025 | 24.0323 | 24.0158 | 24.0098 | 32.692 | 32.5362 | 32.4998 | 32.4892 | 32.477 | 32.4108 | 29.817 | 29.7505 | 29.8422 | 29.7966 | 29.7836 | 29.7828 | 30.1477 | 30.1542 | 30.118 | 30.2745 | 30.2805 | 30.2879 | 30.2148 | 30.3579 | 30.1985 | 17.5079 | 17.5396 | 17.5294 | 17.512 | 17.5476 | 17.5018
231 | Actual Compression DH | KJ/kg | 34.8457 | 35.2214 | 35.5067 | 35.6881 | 35.6516 | 35.7802 | 25.7591 | 25.739 | 25.7935 | 26.5352 | 26.5074 | 26.49 | 26.4371 | 26.3523 | 26.155 | 20.1506 | 20.0153 | 20.249 | 19.2704 | 19.2154 | 18.93 | 25.5325 | 25.634 | 25.9476 | 25.7745 | 25.7912 | 25.6935 | 26.6899 | 26.6261 | 26.476 | 35.2186 | 35.2117 | 35.3152 | 35.4365 | 35.4057 | 35.4075 | 35.8362 | 46.5036 | 46.5029 | 46.4929 | 46.5153 | 46.5205 | 46.499 | 46.512 | 46.3901 | 51.9923 | 51.7108 | 51.8367 | 47.6455 | 47.6482 | 47.8512 | 47.0593 | 46.924 | 46.9275 | 51.8128 | 51.7996 | 51.8008 | 35.3236 | 35.3989 | 35.3147 | 35.4694 | 35.4888 | 35.4953 | 27.235 | 27.2185 | 27.0461 | 20.0976 | 19.9399 | 19.7598 | 19.3859 | 19.1078 | 35.4754 | 35.6113 | 36.4908 | 25.9448 | 25.971 | 25.9806 | 25.9244 | 26.1643 | 26.1934 | 26.1391 | 28.3622 | 28.3691 | 28.3919 | 21.5238 | 21.0804 | 21.031 | 21.2711 | 46.7685 | 46.7192 | 46.6633 | 46.6986 | 48.0429 | 47.9085 | 47.9479 | 48.3366 | 48.1923 | 47.8732 | 42.0104 | 41.9357 | 41.6765 | 41.498 | 41.4626 | 41.4657 | 41.2956 | 40.7216 | 49.7546 | 49.6874 | 49.6218 | 45.9911 | 46.13 | 45.9907 | 45.7378 | 45.787 | 45.7643 | 45.0659 | 44.4795 | 44.5951 | 25.7857 | 25.8347 | 25.8029 | 49.7447 | 49.6415 | 49.831 | 45.2423 | 45.2625 | 45.2714 | 45.7678 | 45.7297 | 46.0641 | 44.3365 | 44.3682 | 44.2137 | 25.2789 | 25.0134 | 25.2903 | 25.7531 | 26.0404 | 25.3571 | 25.1747 | 24.9169 | 24.9393 | 20.3246 | 20.1418 | 19.9338 | 20.0115 | 19.4081 | 19.1015 | 34.0851 | 34.0102 | 34.1849 | 34.2411 | 34.0642 | 34.0852 | 50.0334 | 49.9675 | 50.2045 | 45.9426 | 45.954 | 45.9178 | 45.2366 | 45.5898 | 45.7377 | 44.8807 | 44.5586 | 44.6761 | 25.1947 | 25.0091 | 24.9567 | 46.1283 | 46.2454 | 46.2602 | 46.4363 | 46.2845 | 46.2961 | 25.2848 | 25.4377 | 25.9541 | 20.4331 | 20.5316 | 20.6936 | 20.4229 | 20.7563 | 20.5457 | 20.3641 | 20.2743 | 20.0379 | 25.5045 | 25.5435 | 25.45 | 25.9586 | 26.0277 | 26.4029 | 34.0956 | 33.8444 | 33.9916 | 34.4536 | 34.445 | 34.2982 | 50.2505 | 50.0562 | 50.0673 | 49.9665 | 49.9289 | 50.1164 | 45.6007 | 45.6726 | 45.5476 | 45.621 | 45.6608 | 45.6188 | 46.0574 | 46.0625 | 46.3542 | 46.3316 | 46.3305 | 46.3141 | 44.7267 | 44.6901 | 44.2605 | 25.1271 | 25.1006 | 25.0972 | 25.1276 | 25.0479 | 24.7375
232 | isentropic efficiency (enthalpy only) | % | 68.6076 | 68.0095 | 67.5722 | 67.4635 | 67.7837 | 67.459 | 69.252 | 69.2909 | 68.9715 | 66.5607 | 66.4665 | 66.4929 | 66.5092 | 66.8576 | 67.1177 | 68.7932 | 69.3242 | 68.1898 | 72.2199 | 72.4937 | 73.3798 | 68.4673 | 68.0611 | 67.1056 | 67.4999 | 67.368 | 67.4897 | 65.1046 | 65.3304 | 65.5744 | 68.5442 | 68.5944 | 68.344 | 67.9302 | 67.9171 | 67.8819 | 67.2374 | 65.0535 | 65.019 | 65.119 | 65.0581 | 65.0094 | 65.0338 | 64.9914 | 65.2486 | 62.7189 | 63.2162 | 62.8506 | 63.6609 | 63.4765 | 63.2056 | 63.9785 | 63.9724 | 63.7605 | 62.608 | 62.7271 | 62.7264 | 68.1637 | 68.0475 | 68.4793 | 67.9677 | 67.9573 | 67.9546 | 64.2576 | 64.6157 | 65.1156 | 69.3366 | 70.0149 | 70.5783 | 72.1668 | 72.7465 | 67.3116 | 66.9447 | 65.1675 | 67.1691 | 66.9992 | 67.0344 | 67.081 | 66.6571 | 66.4198 | 66.582 | 65.903 | 66.1081 | 65.8473 | 65.911 | 66.8923 | 66.765 | 65.6256 | 64.5905 | 64.8207 | 64.9502 | 65.0082 | 62.9249 | 63.1822 | 63.097 | 63.4959 | 63.8539 | 63.8636 | 74.5765 | 74.655 | 75.2007 | 75.5294 | 74.9208 | 74.9724 | 75.2665 | 75.9128 | 65.5937 | 65.6998 | 65.9375 | 65.4779 | 65.3064 | 65.7671 | 65.9108 | 65.8575 | 65.9504 | 66.7821 | 67.8346 | 67.4602 | 68.1708 | 67.9695 | 67.9094 | 65.4866 | 65.5533 | 65.1228 | 65.8989 | 65.8038 | 65.6853 | 66.3303 | 66.1365 | 65.6731 | 67.7966 | 67.8119 | 68.0786 | 69.4358 | 70.0685 | 68.8872 | 68.5282 | 67.511 | 69.9808 | 69.9168 | 70.3487 | 70.3306 | 68.2757 | 68.9556 | 69.2177 | 69.8412 | 71.7627 | 72.8032 | 70.3884 | 70.1243 | 69.8043 | 69.9356 | 70.3024 | 69.9195 | 65.5312 | 65.2198 | 64.5904 | 65.5516 | 65.54 | 65.5949 | 65.9567 | 65.1363 | 65.1325 | 67.6861 | 68.598 | 67.9442 | 69.8608 | 70.8862 | 70.3009 | 65.2959 | 65.2096 | 65.3125 | 65.7345 | 65.9981 | 65.8147 | 69.128 | 68.7696 | 67.4565 | 68.8974 | 68.4551 | 67.6308 | 67.4928 | 68.8238 | 69.6444 | 69.6378 | 69.6788 | 70.5184 | 68.6576 | 68.4534 | 68.7434 | 67.4057 | 67.2576 | 66.347 | 70.4804 | 70.9196 | 70.3188 | 69.7526 | 69.7222 | 70.003 | 65.058 | 64.9992 | 64.9123 | 65.0219 | 65.0463 | 64.6711 | 65.3871 | 65.1387 | 65.5186 | 65.3133 | 65.228 | 65.2862 | 65.4568 | 65.4636 | 64.9736 | 65.3431 | 65.3576 | 65.3967 | 67.5543 | 67.9297 | 68.229 | 69.6773 | 69.8772 | 69.8461 | 69.6924 | 70.0561 | 70.7503
233
234 | Isentropic Efficiency (Power) | % | 68.2455 | 68.4819 | 68.28 | 68.0052 | 68.0163 | 68.0179 | 67.6978 | 67.1296 | 67.4337 | 64.2769 | 64.79 | 64.6389 | 64.5148 | 64.7819 | 64.5816 | 64.8289 | 62.6912 | 63.5481 | 64.4854 | 66.766 | 63.8323 | 66.2262 | 66.2018 | 66.2495 | 65.353 | 66.2768 | 65.4549 | 62.8789 | 63.5807 | 63.2646 | 67.5393 | 68.0816 | 67.7689 | 67.3796 | 67.4805 | 67.0905 | 67.8877 | 65.5454 | 65.6868 | 65.7324 | 65.6752 | 65.4273 | 65.3605 | 65.9763 | 65.5698 | 63.0184 | 62.9114 | 63.2627 | 64.5972 | 63.8014 | 63.0934 | 64.18 | 63.8159 | 64.3265 | 63.6938 | 62.5972 | 63.0685 | 67.5684 | 67.2343 | 67.2793 | 67.9423 | 68.0478 | 67.9385 | 64.6327 | 65.3214 | 65.0851 | 58.5565 | 61.1541 | 55.4787 | 60.2144 | 62.8106 | 67.3398 | 67.0743 | 67.2591 | 65.5189 | 64.8862 | 64.3094 | 64.5707 | 65.2187 | 65.3206 | 65.5777 | 65.3362 | 64.8598 | 64.9609 | 59.6856 | 60.6842 | 59.9669 | 61.6422 | 64.8064 | 64.9479 | 65.3483 | 65.3651 | 63.9927 | 63.9187 | 63.4652 | 64.0541 | 64.0755 | 64.2258 | 65.4268 | 66.1323 | 66.109 | 65.9225 | 66.0245 | 65.8749 | 66.249 | 66.069 | 66.3036 | 66.136 | 66.3422 | 66.7645 | 65.8163 | 65.6752 | 66.1068 | 66.1963 | 66.2645 | 67.6535 | 67.7196 | 67.7889 | 67.4433 | 67.658 | 67.7433 | 65.7037 | 65.4983 | 65.9415 | 66.124 | 65.7743 | 65.958 | 66.2172 | 65.9749 | 66.9186 | 67.7711 | 67.9601 | 67.8282 | 68.0769 | 68.0322 | 68.6973 | 67.2685 | 67.5002 | 66.8904 | 67.1856 | 66.4949 | 66.8674 | 58.0335 | 58.1753 | 61.328 | 63.8076 | 60.8821 | 62.6554 | 70.7206 | 70.1362 | 70.6948 | 69.0803 | 69.8664 | 69.4416 | 65.7471 | 66.4728 | 65.8451 | 65.7453 | 66.2876 | 66.5094 | 65.821 | 65.8619 | 65.5362 | 68.2642 | 68.4597 | 68.4399 | 67.5886 | 67.1082 | 67.6746 | 65.6951 | 64.8661 | 65.8374 | 65.5404 | 65.5978 | 66.1869 | 67.3358 | 67.2324 | 68.4608 | 61.9143 | 62.0647 | 63.6438 | 62.1286 | 62.3274 | 63.3887 | 62.4916 | 63.4688 | 63.412 | 67.0412 | 67.4225 | 67.0498 | 66.2413 | 65.6447 | 66.2896 | 70.0531 | 69.7918 | 69.821 | 68.9125 | 69.0421 | 68.5551 | 65.1302 | 65.3592 | 65.6289 | 65.2526 | 65.4007 | 64.6287 | 65.4917 | 65.4163 | 65.2829 | 64.7132 | 65.0181 | 65.2536 | 65.4916 | 65.4479 | 65.527 | 65.957 | 64.8963 | 65.2812 | 67.105 | 67.1578 | 67.3569 | 67.9604 | 67.4878 | 68.1075 | 67.5919 | 67.9953 | 67.5086
235 | Table Isentropic | % | 71.9638 | 71.9693 | 71.9987 | 71.8898 | 71.9467 | 71.9322 | 65.0915 | 65.1068 | 65.0525 | 64.9833 | 64.9496 | 64.9667 | 64.9547 | 65.0095 | 64.9093 | 58.2609 | 58.3039 | 58.1843 | 58.086 | 58.1937 | 58.115 | 64.9483 | 64.9666 | 64.9287 | 64.9762 | 64.9446 | 64.8979 | 64.937 | 64.9777 | 64.9399 | 71.9632 | 71.978 | 71.979 | 71.9594 | 71.9608 | 71.9698 | 71.9498 | 73.939 | 73.9388 | 73.9393 | 73.939 | 73.9387 | 73.9386 | 73.938 | 73.9377 | 73.7365 | 73.7354 | 73.7299 | 73.9396 | 73.9386 | 73.9386 | 73.9317 | 73.9293 | 73.9265 | 73.7366 | 73.7299 | 73.7342 | 71.9358 | 71.9533 | 72.01 | 71.9339 | 71.937 | 71.9374 | 64.8541 | 64.9342 | 64.9126 | 58.2078 | 58.2588 | 58.2378 | 58.4207 | 58.2262 | 71.9407 | 71.9267 | 71.9308 | 64.9229 | 64.897 | 64.9369 | 64.9589 | 64.9605 | 64.8925 | 64.8883 | 66.6005 | 66.6751 | 66.5992 | 58.8587 | 58.5627 | 58.4215 | 58.2832 | 73.9393 | 73.9397 | 73.9395 | 73.9397 | 73.9398 | 73.9384 | 73.9373 | 73.9316 | 73.9319 | 73.9276 | 73.9379 | 73.9377 | 73.9381 | 73.9382 | 73.9312 | 73.9326 | 73.9323 | 73.9258 | 73.7344 | 73.7409 | 73.7282 | 73.9387 | 73.9382 | 73.9382 | 73.9311 | 73.9298 | 73.9296 | 73.9393 | 73.9387 | 73.9389 | 65.0692 | 65.0633 | 64.9702 | 73.7226 | 73.723 | 73.7316 | 73.9304 | 73.9306 | 73.9311 | 73.9393 | 73.9386 | 73.9384 | 73.9384 | 73.9383 | 73.9384 | 65.1428 | 65.1104 | 64.9787 | 65.0812 | 64.9436 | 65.0846 | 64.8963 | 64.8415 | 64.9104 | 58.169 | 58.1689 | 57.9603 | 58.3446 | 58.2853 | 58.2501 | 71.992 | 71.9054 | 71.9163 | 71.9031 | 71.9196 | 71.8795 | 73.7202 | 73.7219 | 73.7087 | 73.9394 | 73.9397 | 73.9396 | 73.9333 | 73.9294 | 73.9326 | 73.9395 | 73.9393 | 73.9382 | 64.9362 | 65.1571 | 64.9056 | 73.9316 | 73.933 | 73.9337 | 73.9397 | 73.9399 | 73.94 | 64.9573 | 64.9624 | 64.9995 | 58.5822 | 58.5617 | 58.4432 | 58.007 | 59.0133 | 59.0369 | 58.7786 | 58.6407 | 58.6059 | 64.9828 | 64.9426 | 64.9111 | 65.0411 | 65.0206 | 65.0363 | 71.9697 | 71.9552 | 71.8723 | 71.9293 | 71.9339 | 71.9368 | 73.7158 | 73.7427 | 73.745 | 73.7428 | 73.7373 | 73.7394 | 73.9276 | 73.9252 | 73.9278 | 73.9277 | 73.9265 | 73.9256 | 73.9381 | 73.9383 | 73.9384 | 73.9398 | 73.9398 | 73.9399 | 73.9384 | 73.9399 | 73.9388 | 64.95 | 64.9745 | 64.9645 | 64.9561 | 64.9874 | 64.8921
236 | % of table isentropic | % | 94.8331 | 95.1543 | 94.8349 | 94.5965 | 94.5371 | 94.5584 | 104.004 | 103.1069 | 103.6605 | 98.9129 | 99.7542 | 99.4953 | 99.3227 | 99.6498 | 99.4951 | 111.2733 | 107.5249 | 109.2186 | 111.0172 | 114.7307 | 109.8381 | 101.9676 | 101.9013 | 102.0343 | 100.5799 | 102.0513 | 100.8583 | 96.8306 | 97.8501 | 97.4203 | 93.8525 | 94.5866 | 94.151 | 93.6356 | 93.7739 | 93.2204 | 94.3542 | 88.6479 | 88.8393 | 88.9005 | 88.8234 | 88.4885 | 88.3984 | 89.2319 | 88.6824 | 85.4644 | 85.3205 | 85.8034 | 87.3648 | 86.2898 | 85.3321 | 86.8099 | 86.3201 | 87.0141 | 86.3802 | 84.9006 | 85.5349 | 93.9288 | 93.4417 | 93.4304 | 94.4511 | 94.5935 | 94.4411 | 99.6586 | 100.5963 | 100.2659 | 100.5991 | 104.9696 | 95.2623 | 103.0702 | 107.8735 | 93.6047 | 93.2537 | 93.5053 | 100.9181 | 99.9834 | 99.0336 | 99.4024 | 100.3975 | 100.6596 | 101.0625 | 98.1016 | 97.2773 | 97.5402 | 101.4048 | 103.6226 | 102.6454 | 105.7633 | 87.6481 | 87.8391 | 88.3808 | 88.4032 | 86.547 | 86.4485 | 85.8366 | 86.6397 | 86.6682 | 86.8766 | 88.4889 | 89.4433 | 89.4113 | 89.1589 | 89.3053 | 89.1013 | 89.6077 | 89.3721 | 89.9222 | 89.687 | 89.9821 | 90.2971 | 89.0153 | 88.8244 | 89.4168 | 89.5394 | 89.632 | 91.4987 | 91.5889 | 91.6822 | 103.6487 | 103.988 | 104.2683 | 89.1229 | 88.8438 | 89.4345 | 89.4409 | 88.9676 | 89.2154 | 89.5562 | 89.2293 | 90.5059 | 91.6588 | 91.9146 | 91.736 | 104.5041 | 104.4873 | 105.7227 | 103.3609 | 103.9366 | 102.7745 | 103.5276 | 102.5499 | 103.0151 | 99.7671 | 100.011 | 105.8104 | 109.3634 | 104.4553 | 107.5626 | 98.2339 | 97.5396 | 98.3015 | 96.0741 | 97.1452 | 96.6083 | 89.1847 | 90.1669 | 89.3316 | 88.9178 | 89.6509 | 89.951 | 89.0275 | 89.0875 | 88.6431 | 92.3243 | 92.589 | 92.5636 | 104.0846 | 102.9945 | 104.2663 | 88.8593 | 87.7363 | 89.0492 | 88.6404 | 88.7178 | 89.5144 | 103.6617 | 103.4944 | 105.3252 | 105.688 | 105.9817 | 108.8984 | 107.1053 | 105.6158 | 107.3714 | 106.3171 | 108.2333 | 108.2007 | 103.1676 | 103.8186 | 103.2949 | 101.8453 | 100.9599 | 101.9271 | 97.3369 | 96.9934 | 97.1458 | 95.8059 | 95.9799 | 95.2991 | 88.3531 | 88.6315 | 88.9943 | 88.4868 | 88.6942 | 87.6447 | 88.5889 | 88.4898 | 88.3063 | 87.5358 | 87.9497 | 88.2693 | 88.5763 | 88.517 | 88.6237 | 89.2036 | 87.7691 | 88.2896 | 90.758 | 90.8275 | 91.0981 | 104.6349 | 103.8682 | 104.8381 | 104.0577 | 104.6284 | 104.0321
237 | Corrected IE% from N4 Powermeter Kw | % | 0.072299 | 0.07224 | 0.072319 | 0.071308 | 0.071505 | 0.07145 | 0.073186 | 0.07317 | 0.073087 | 0.069843 | 0.069802 | 0.070258 | 0.070246 | 0.070216 | 0.07015 | 0.072495 | 0.07259 | 0.072793 | 0.073548 | 0.073534 | 0.074597 | 0.071999 | 0.071954 | 0.07216 | 0.071701 | 0.071756 | 0.071767 | 0.068397 | 0.068734 | 0.068471 | 0.071559 | 0.071575 | 0.071547 | 0.071003 | 0.07085 | 0.070786 | 0.071224 | 0.067768 | 0.067918 | 0.067934 | 0.067891 | 0.067702 | 0.06774 | 0.067898 | 0.067872 | 0.065103 | 0.065217 | 0.065294 | 0.065743 | 0.065802 | 0.065657 | 0.065918 | 0.065894 | 0.065827 | 0.064756 | 0.064801 | 0.064802 | 0.071231 | 0.071018 | 0.071122 | 0.071533 | 0.071768 | 0.071653 | 0.070629 | 0.070673 | 0.070655 | 0.066337 | 0.067699 | 0.062936 | 0.069006 | 0.069563 | 0.070541 | 0.070488 | 0.070627 | 0.070638 | 0.070449 | 0.070848 | 0.070708 | 0.070921 | 0.071182 | 0.070999 | 0.070354 | 0.070617 | 0.070611 | 0.067869 | 0.069695 | 0.068099 | 0.070198 | 0.067187 | 0.067225 | 0.067335 | 0.067298 | 0.065411 | 0.06547 | 0.06532 | 0.065707 | 0.065873 | 0.065897 | 0.067779 | 0.067866 | 0.067946 | 0.06798 | 0.067877 | 0.067924 | 0.067966 | 0.067955 | 0.067958 | 0.06781 | 0.068092 | 0.067894 | 0.067806 | 0.067905 | 0.068253 | 0.068223 | 0.068277 | 0.069653 | 0.069859 | 0.069951 | 0.072989 | 0.07303 | 0.073175 | 0.067655 | 0.067585 | 0.067624 | 0.068015 | 0.067714 | 0.067766 | 0.068376 | 0.0681 | 0.068515 | 0.070173 | 0.070162 | 0.070119 | 0.074234 | 0.074388 | 0.07468 | 0.072901 | 0.073041 | 0.073081 | 0.073231 | 0.073059 | 0.07314 | 0.066853 | 0.067362 | 0.070706 | 0.072064 | 0.070742 | 0.071391 | 0.074095 | 0.074168 | 0.074309 | 0.073164 | 0.07331 | 0.073268 | 0.067658 | 0.067701 | 0.067412 | 0.067673 | 0.06783 | 0.067884 | 0.067747 | 0.06771 | 0.067778 | 0.070331 | 0.07085 | 0.070342 | 0.073287 | 0.072941 | 0.073404 | 0.067522 | 0.067571 | 0.067527 | 0.067736 | 0.067784 | 0.067757 | 0.073379 | 0.07292 | 0.073614 | 0.070861 | 0.07144 | 0.072086 | 0.07038 | 0.070087 | 0.070399 | 0.070709 | 0.071597 | 0.071924 | 0.072487 | 0.072403 | 0.072354 | 0.072375 | 0.072203 | 0.072147 | 0.073931 | 0.073644 | 0.073663 | 0.072515 | 0.072467 | 0.072518 | 0.066938 | 0.066872 | 0.066947 | 0.067038 | 0.067035 | 0.066777 | 0.067047 | 0.067224 | 0.067111 | 0.067141 | 0.067019 | 0.06713 | 0.067296 | 0.067244 | 0.067244 | 0.067298 | 0.067318 | 0.067293 | 0.069432 | 0.069341 | 0.069394 | 0.073614 | 0.073809 | 0.073905 | 0.07348 | 0.073863 | 0.073696
238
239 | Table volumetric efficiency | % | 97.3843 | 97.3822 | 97.371 | 97.4118 | 97.3907 | 97.3961 | 98.7059 | 98.7042 | 98.7103 | 98.718 | 98.7217 | 98.7198 | 98.7211 | 98.7151 | 98.7261 | 99.2784 | 99.2756 | 99.2833 | 99.2895 | 99.2827 | 99.2877 | 98.7218 | 98.7198 | 98.724 | 98.7187 | 98.7222 | 98.7273 | 98.7231 | 98.7186 | 98.7227 | 97.3845 | 97.3789 | 97.3785 | 97.3859 | 97.3854 | 97.382 | 97.3895 | 95.5445 | 95.5485 | 95.5354 | 95.5442 | 95.551 | 95.5544 | 95.5665 | 95.5716 | 94.6607 | 94.6583 | 94.6462 | 95.5253 | 95.5545 | 95.5543 | 95.6436 | 95.6633 | 95.6841 | 94.661 | 94.6463 | 94.6557 | 97.3948 | 97.3882 | 97.3667 | 97.3955 | 97.3943 | 97.3942 | 98.7321 | 98.7234 | 98.7257 | 99.2818 | 99.2785 | 99.2799 | 99.2681 | 99.2806 | 97.393 | 97.3981 | 97.3966 | 98.7246 | 98.7274 | 98.7231 | 98.7206 | 98.7205 | 98.7279 | 98.7284 | 98.5229 | 98.513 | 98.5231 | 99.2394 | 99.2589 | 99.2681 | 99.277 | 95.5342 | 95.5222 | 95.53 | 95.5204 | 95.5144 | 95.5576 | 95.5784 | 95.6442 | 95.6412 | 95.6764 | 95.5686 | 95.5725 | 95.5641 | 95.5617 | 95.6474 | 95.6348 | 95.638 | 95.6893 | 94.6561 | 94.6705 | 94.6427 | 95.5513 | 95.5624 | 95.5618 | 95.6484 | 95.6593 | 95.6612 | 95.5341 | 95.5519 | 95.5466 | 98.7084 | 98.7091 | 98.7194 | 94.6304 | 94.6313 | 94.6501 | 95.6545 | 95.6526 | 95.6484 | 95.5366 | 95.554 | 95.5584 | 95.5578 | 95.5606 | 95.5575 | 98.7002 | 98.7038 | 98.7185 | 98.7071 | 98.7223 | 98.7067 | 98.7275 | 98.7335 | 98.726 | 99.2843 | 99.2843 | 99.2975 | 99.273 | 99.2768 | 99.2791 | 97.3736 | 97.4061 | 97.402 | 97.4069 | 97.4008 | 97.4155 | 94.6253 | 94.629 | 94.601 | 95.5309 | 95.5205 | 95.5246 | 95.628 | 95.6625 | 95.6349 | 95.5275 | 95.5346 | 95.5628 | 98.7231 | 98.6986 | 98.7265 | 95.6442 | 95.6308 | 95.6242 | 95.5217 | 95.5099 | 95.4912 | 98.7208 | 98.7203 | 98.7162 | 99.2576 | 99.259 | 99.2667 | 99.2945 | 99.229 | 99.2274 | 99.2447 | 99.2538 | 99.2561 | 98.718 | 98.7224 | 98.7259 | 98.7116 | 98.7138 | 98.7121 | 97.382 | 97.3875 | 97.4182 | 97.3972 | 97.3955 | 97.3944 | 94.6159 | 94.6745 | 94.6798 | 94.6749 | 94.6624 | 94.6672 | 95.6761 | 95.6929 | 95.6748 | 95.6756 | 95.6846 | 95.6906 | 95.5651 | 95.5609 | 95.5579 | 95.5134 | 95.5138 | 95.5103 | 95.5585 | 95.5027 | 95.5489 | 98.7216 | 98.7189 | 98.72 | 98.721 | 98.7175 | 98.728
240 | Actual Volume Flow rate | m^3/hr | 731.8961 | 731.6168 | 731.7942 | 780.5865 | 782.1289 | 781.4163 | 465.9316 | 465.4707 | 465.061 | 407.198 | 407.0781 | 409.7502 | 409.4813 | 408.6627 | 409.1473 | 180.8857 | 180.8563 | 181.5073 | 193.9535 | 194.328 | 197.2309 | 407.2085 | 406.9548 | 408.074 | 437.8414 | 438.4573 | 438.477 | 437.2093 | 438.9258 | 437.6932 | 740.1854 | 739.7968 | 740.1364 | 779.2445 | 777.5309 | 776.7166 | 770.6592 | 1139.634 | 1141.4914 | 1142.1496 | 1141.2389 | 1139.0023 | 1138.3073 | 1141.7443 | 1140.959 | 1220.5253 | 1222.6087 | 1224.0078 | 1229.1848 | 1229.9968 | 1227.4021 | 1232.9103 | 1232.0966 | 1230.3022 | 1200.3594 | 1201.217 | 1201.2489 | 704.3695 | 702.4048 | 703.1388 | 718.9594 | 721.8457 | 719.985 | 394.8397 | 395.1843 | 394.316 | 164.3678 | 167.7678 | 156.0763 | 180.3324 | 181.8162 | 764.8714 | 763.9256 | 765.452 | 427.8803 | 427.0823 | 428.5392 | 428.09 | 451.9369 | 453.7461 | 452.6066 | 451.5341 | 452.9695 | 452.8054 | 176.9893 | 181.6006 | 177.4138 | 182.9027 | 1117.3446 | 1117.5182 | 1118.7084 | 1118.6845 | 1211.8179 | 1211.2473 | 1209.0505 | 1212.2486 | 1215.2424 | 1215.0122 | 1249.0351 | 1250.7126 | 1253.1355 | 1253.2126 | 1252.0274 | 1251.963 | 1252.9447 | 1254.3633 | 1256.8805 | 1255.3162 | 1258.7729 | 1262.2168 | 1261.3269 | 1261.9601 | 1265.7133 | 1266.0111 | 1266.2992 | 1162.7893 | 1163.9088 | 1165.2976 | 462.7573 | 463.0279 | 464.2643 | 1252.3665 | 1250.9616 | 1251.5064 | 1263.03 | 1258.0375 | 1259.3944 | 1265.5632 | 1261.9628 | 1269.3495 | 1164.6671 | 1164.425 | 1165.44 | 464.4651 | 464.9623 | 466.8919 | 437.5039 | 437.814 | 437.8271 | 406.7138 | 405.7478 | 406.3865 | 166.0037 | 167.2912 | 176.1108 | 189.6091 | 185.4768 | 187.0722 | 746.2678 | 747.1896 | 747.602 | 792.4345 | 793.596 | 793.3262 | 1243.2446 | 1245.3293 | 1242.2904 | 1247.5352 | 1250.4209 | 1251.6936 | 1250.9299 | 1250.6975 | 1250.6288 | 1158.9234 | 1165.8114 | 1159.4545 | 461.1849 | 459.5543 | 461.1948 | 1256.2799 | 1257.0348 | 1256.4184 | 1257.9322 | 1258.709 | 1259.3412 | 462.5132 | 460.4154 | 464.537 | 186.44 | 187.9147 | 189.8132 | 175.3701 | 175.2318 | 175.9166 | 186.3748 | 188.6482 | 189.6793 | 436.9537 | 436.4958 | 436.3067 | 404.4496 | 404.2033 | 403.862 | 738.3737 | 733.4054 | 724.6351 | 794.4629 | 793.8774 | 794.6621 | 1243.3019 | 1242.4812 | 1243.5577 | 1245.3325 | 1245.4595 | 1241.7175 | 1247.5853 | 1251.3143 | 1248.6389 | 1249.559 | 1247.7942 | 1250.7645 | 1250.8751 | 1250.0629 | 1250.0384 | 1250.5325 | 1251.2034 | 1250.1394 | 1154.3388 | 1152.2686 | 1153.5369 | 463.7783 | 465.2845 | 466.0843 | 463.2867 | 465.4362 | 463.937
241 | Volumetric efficiency | % | 95.6138 | 95.5759 | 95.5841 | 95.1706 | 95.3599 | 95.2629 | 94.6687 | 94.5708 | 94.5086 | 93.0692 | 93.0628 | 93.6619 | 93.6028 | 93.404 | 93.5311 | 87.0653 | 87.0511 | 87.3277 | 88.7089 | 88.8757 | 90.1312 | 93.0763 | 93.0323 | 93.2858 | 93.1204 | 93.2297 | 93.2317 | 92.9557 | 93.3423 | 93.078 | 95.3279 | 95.2846 | 95.3216 | 95.0044 | 94.7955 | 94.6975 | 95.2262 | 94.7324 | 94.8868 | 94.9415 | 94.8658 | 94.6885 | 94.6221 | 94.9078 | 94.8339 | 93.0018 | 93.1605 | 93.2593 | 93.6538 | 93.7235 | 93.5102 | 93.9455 | 93.8835 | 93.7546 | 91.4575 | 91.5305 | 91.5329 | 93.3393 | 93.1032 | 93.1911 | 93.9157 | 94.3062 | 94.0483 | 90.2491 | 90.3324 | 90.1362 | 79.1147 | 80.7385 | 75.1317 | 82.4048 | 83.1243 | 93.2508 | 93.1331 | 93.3341 | 90.9786 | 90.8152 | 91.1208 | 91.0485 | 91.8273 | 92.201 | 91.9572 | 91.7495 | 92.0616 | 92.018 | 80.8852 | 83.0009 | 81.1238 | 83.6378 | 92.8795 | 92.894 | 92.976 | 92.974 | 92.3383 | 92.2948 | 92.1274 | 92.3788 | 92.5992 | 92.5817 | 95.1821 | 95.294 | 95.5025 | 95.5004 | 95.4101 | 95.3973 | 95.4721 | 95.5802 | 95.772 | 95.6607 | 95.9082 | 96.1706 | 96.1108 | 96.159 | 96.437 | 96.4757 | 96.4977 | 96.6747 | 96.7502 | 96.8656 | 94.0195 | 94.0829 | 94.3488 | 95.436 | 95.313 | 95.3545 | 96.2325 | 95.8601 | 95.9635 | 96.4336 | 96.1592 | 96.7221 | 96.8044 | 96.7931 | 96.8775 | 94.3812 | 94.4654 | 94.8659 | 93.0313 | 93.0994 | 93.1 | 92.9725 | 92.7447 | 92.9139 | 79.9064 | 80.5134 | 84.7357 | 86.7045 | 84.8064 | 85.4846 | 96.1085 | 96.2286 | 96.2804 | 95.3313 | 95.4848 | 95.4423 | 94.7408 | 94.8839 | 94.6602 | 95.0519 | 95.2797 | 95.3688 | 95.3185 | 95.3008 | 95.3035 | 96.327 | 96.8995 | 96.3799 | 93.7126 | 93.375 | 93.7167 | 95.7342 | 95.7837 | 95.7527 | 95.8601 | 95.9113 | 95.9675 | 93.9741 | 93.5624 | 94.3853 | 85.234 | 85.8953 | 86.7501 | 84.3838 | 84.2862 | 84.6735 | 85.2042 | 86.2392 | 86.7063 | 92.9164 | 92.8234 | 92.7767 | 92.4526 | 92.4079 | 92.3044 | 96.4462 | 95.7986 | 96.0178 | 95.5828 | 95.5162 | 95.6043 | 94.7136 | 94.6826 | 94.7568 | 94.8841 | 94.9096 | 94.6166 | 95.0637 | 95.3399 | 95.144 | 95.2061 | 95.0717 | 95.3139 | 95.3223 | 95.2604 | 95.2506 | 95.2644 | 95.3394 | 95.2583 | 95.9634 | 95.7826 | 95.8968 | 94.25 | 94.5519 | 94.7123 | 94.1376 | 94.568 | 94.2739
242 | Volumetric as % of table | % | 98.1819 | 98.1452 | 98.1648 | 97.6993 | 97.9148 | 97.8097 | 95.9098 | 95.8123 | 95.7434 | 94.2779 | 94.2678 | 94.8765 | 94.8154 | 94.6198 | 94.738 | 87.6981 | 87.6863 | 87.9581 | 89.3436 | 89.5178 | 90.7778 | 94.2814 | 94.2387 | 94.4915 | 94.329 | 94.4364 | 94.4335 | 94.158 | 94.5539 | 94.2823 | 97.8882 | 97.8493 | 97.8877 | 97.5546 | 97.3406 | 97.2433 | 97.7786 | 99.1499 | 99.3074 | 99.3783 | 99.2899 | 99.0973 | 99.0243 | 99.3107 | 99.2281 | 98.2475 | 98.4177 | 98.5347 | 98.0408 | 98.0838 | 97.8608 | 98.2245 | 98.1394 | 97.9834 | 96.6159 | 96.708 | 96.7009 | 95.836 | 95.6001 | 95.7114 | 96.4271 | 96.8293 | 96.5646 | 91.4081 | 91.5005 | 91.2996 | 79.6871 | 81.3252 | 75.6767 | 83.0123 | 83.7266 | 95.747 | 95.621 | 95.8288 | 92.1539 | 91.9858 | 92.2994 | 92.2285 | 93.0174 | 93.389 | 93.1416 | 93.125 | 93.4512 | 93.3974 | 81.5051 | 83.6206 | 81.7219 | 84.2469 | 97.2212 | 97.2486 | 97.3265 | 97.3342 | 96.6747 | 96.5855 | 96.3893 | 96.5859 | 96.8193 | 96.7655 | 99.5955 | 99.7087 | 99.9355 | 99.9358 | 99.7519 | 99.7516 | 99.8264 | 99.8859 | 101.1789 | 101.046 | 101.3371 | 100.6481 | 100.5738 | 100.6249 | 100.8245 | 100.8534 | 100.8744 | 101.1939 | 101.2541 | 101.3805 | 95.2497 | 95.3133 | 95.5727 | 100.8513 | 100.7204 | 100.7442 | 100.6042 | 100.2169 | 100.3295 | 100.9389 | 100.6333 | 101.2178 | 101.3045 | 101.2897 | 101.3813 | 95.6241 | 95.706 | 96.0974 | 94.2498 | 94.3043 | 94.3198 | 94.1708 | 93.9344 | 94.113 | 80.4824 | 81.0938 | 85.3352 | 87.3394 | 85.4241 | 86.1053 | 98.7008 | 98.7912 | 98.8484 | 97.8691 | 98.0329 | 97.9744 | 100.1221 | 100.2693 | 100.0626 | 99.4986 | 99.7479 | 99.8368 | 99.6764 | 99.6219 | 99.6535 | 100.837 | 101.4287 | 100.8551 | 94.9246 | 94.6062 | 94.9255 | 100.094 | 100.1599 | 100.1344 | 100.3543 | 100.4203 | 100.4988 | 95.1918 | 94.7753 | 95.6128 | 85.8715 | 86.5366 | 87.391 | 84.9833 | 84.9411 | 85.3327 | 85.8527 | 86.8876 | 87.3561 | 94.1231 | 94.0246 | 93.974 | 93.6594 | 93.6119 | 93.5087 | 99.039 | 98.3685 | 98.5625 | 98.1372 | 98.0704 | 98.162 | 100.1033 | 100.0086 | 100.0813 | 100.221 | 100.2611 | 99.9465 | 99.3599 | 99.6311 | 99.4452 | 99.5093 | 99.3595 | 99.6063 | 99.746 | 99.6856 | 99.6784 | 99.7393 | 99.8174 | 99.7362 | 100.4238 | 100.2931 | 100.364 | 95.4705 | 95.7789 | 95.9403 | 95.3572 | 95.7966 | 95.4885
243 | Corrected Volumetric Effciency for Hz | % | 95.6138 | 95.5759 | 95.5841 | 95.1706 | 95.3599 | 95.2629 | 94.6687 | 94.5708 | 94.5086 | 93.0692 | 93.0628 | 93.6619 | 93.6028 | 93.404 | 93.5311 | 87.0653 | 87.0511 | 87.3277 | 88.7089 | 88.8757 | 90.1312 | 93.0763 | 93.0323 | 93.2858 | 93.1204 | 93.2297 | 93.2317 | 92.9557 | 93.3423 | 93.078 | 95.3279 | 95.2846 | 95.3216 | 95.0044 | 94.7955 | 94.6975 | 95.2262 | 94.7324 | 94.8868 | 94.9415 | 94.8658 | 94.6885 | 94.6221 | 94.9078 | 94.8339 | 93.0018 | 93.1605 | 93.2593 | 93.6538 | 93.7235 | 93.5102 | 93.9455 | 93.8835 | 93.7546 | 91.4575 | 91.5305 | 91.5329 | 93.3393 | 93.1032 | 93.1911 | 93.9157 | 94.3062 | 94.0483 | 90.2491 | 90.3324 | 90.1362 | 79.1147 | 80.7385 | 75.1317 | 82.4048 | 83.1243 | 93.2508 | 93.1331 | 93.3341 | 90.9786 | 90.8152 | 91.1208 | 91.0485 | 91.8273 | 92.201 | 91.9572 | 91.7495 | 92.0616 | 92.018 | 80.8852 | 83.0009 | 81.1238 | 83.6378 | 92.8795 | 92.894 | 92.976 | 92.974 | 92.3383 | 92.2948 | 92.1274 | 92.3788 | 92.5992 | 92.5817 | 95.1821 | 95.294 | 95.5025 | 95.5004 | 95.4101 | 95.3973 | 95.4721 | 95.5802 | 95.772 | 95.6607 | 95.9082 | 96.1706 | 96.1108 | 96.159 | 96.437 | 96.4757 | 96.4977 | 96.6747 | 96.7502 | 96.8656 | 94.0195 | 94.0829 | 94.3488 | 95.436 | 95.313 | 95.3545 | 96.2325 | 95.8601 | 95.9635 | 96.4336 | 96.1592 | 96.7221 | 96.8044 | 96.7931 | 96.8775 | 94.3812 | 94.4654 | 94.8659 | 93.0313 | 93.0994 | 93.1 | 92.9725 | 92.7447 | 92.9139 | 79.9064 | 80.5134 | 84.7357 | 86.7045 | 84.8064 | 85.4846 | 96.1085 | 96.2286 | 96.2804 | 95.3313 | 95.4848 | 95.4423 | 94.7408 | 94.8839 | 94.6602 | 95.0519 | 95.2797 | 95.3688 | 95.3185 | 95.3008 | 95.3035 | 96.327 | 96.8995 | 96.3799 | 93.7126 | 93.375 | 93.7167 | 95.7342 | 95.7837 | 95.7527 | 95.8601 | 95.9113 | 95.9675 | 93.9741 | 93.5624 | 94.3853 | 85.234 | 85.8953 | 86.7501 | 84.3838 | 84.2862 | 84.6735 | 85.2042 | 86.2392 | 86.7063 | 92.9164 | 92.8234 | 92.7767 | 92.4526 | 92.4079 | 92.3044 | 96.4462 | 95.7986 | 96.0178 | 95.5828 | 95.5162 | 95.6043 | 94.7136 | 94.6826 | 94.7568 | 94.8841 | 94.9096 | 94.6166 | 95.0637 | 95.3399 | 95.144 | 95.2061 | 95.0717 | 95.3139 | 95.3223 | 95.2604 | 95.2506 | 95.2644 | 95.3394 | 95.2583 | 95.9634 | 95.7826 | 95.8968 | 94.25 | 94.5519 | 94.7123 | 94.1376 | 94.568 | 94.2739
244
245 | Assumed Subcooling | ºC | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
246 | Enthalpy liquid at DG with assumed subcooling | KJ/kg | 252.0422 | 251.9148 | 252.0478 | 251.8329 | 251.9357 | 251.7998 | 239.2891 | 239.4555 | 239.2999 | 239.0914 | 239.3245 | 239.3472 | 239.3827 | 239.3105 | 239.1496 | 231.8877 | 231.8953 | 231.6046 | 231.6265 | 231.8114 | 231.641 | 239.2111 | 239.3586 | 239.2346 | 239.1268 | 239.1056 | 239.1611 | 239.2058 | 239.2183 | 239.298 | 252.1155 | 252.0477 | 251.9471 | 251.9143 | 251.9926 | 251.9118 | 251.9441 | 264.8845 | 264.9003 | 264.9233 | 264.8918 | 264.8869 | 264.8904 | 264.8538 | 264.8504 | 266.5088 | 266.3956 | 266.3729 | 265.0332 | 264.859 | 264.8177 | 264.1219 | 263.9299 | 263.8169 | 266.3907 | 266.5134 | 266.3965 | 251.9414 | 251.9302 | 252.0902 | 251.9328 | 251.8857 | 251.8434 | 239.1209 | 239.2602 | 239.219 | 231.6193 | 231.6872 | 231.8677 | 232.0939 | 231.7178 | 251.8739 | 251.8212 | 251.9229 | 239.1392 | 239.1651 | 239.1976 | 239.3468 | 239.2337 | 239.18 | 239.1584 | 239.0729 | 239.0687 | 239.1208 | 232.1009 | 232.1856 | 232.0082 | 231.8833 | 264.5737 | 264.847 | 264.9228 | 264.822 | 264.9099 | 264.8559 | 264.7938 | 263.996 | 264.0262 | 264.0702 | 264.7994 | 264.9021 | 264.7277 | 264.735 | 264.1963 | 264.3675 | 264.218 | 263.8884 | 266.4344 | 266.4134 | 266.4741 | 264.9237 | 264.6419 | 264.7358 | 263.9698 | 263.8007 | 263.8812 | 265.0476 | 264.6822 | 264.8445 | 239.4465 | 239.4556 | 239.0955 | 266.6086 | 266.6266 | 266.5589 | 264.1601 | 264.0107 | 263.9636 | 264.7867 | 264.825 | 264.8411 | 264.7594 | 264.6516 | 264.6065 | 239.3824 | 239.4894 | 239.1308 | 239.4455 | 239.2236 | 239.3825 | 239.2031 | 239.0452 | 239.1397 | 231.727 | 231.7301 | 231.6986 | 231.8548 | 231.7821 | 231.7064 | 251.9908 | 251.7718 | 251.748 | 251.8625 | 251.9094 | 251.7448 | 266.6727 | 266.4978 | 266.6342 | 265.0459 | 265.0479 | 264.8558 | 264.1833 | 263.8761 | 264.0154 | 265.1981 | 264.9413 | 264.7795 | 239.0995 | 239.4414 | 239.1526 | 264.0813 | 264.0991 | 264.0502 | 264.975 | 265.1912 | 265.2487 | 239.2566 | 239.1132 | 239.2125 | 231.9817 | 231.9383 | 231.855 | 231.7006 | 231.8442 | 231.8333 | 231.813 | 231.5928 | 231.4361 | 239.3341 | 239.2558 | 239.0507 | 239.328 | 239.1712 | 239.1756 | 252.1147 | 252.0391 | 251.6804 | 251.9414 | 251.8368 | 251.761 | 266.5527 | 266.2834 | 266.3332 | 266.4138 | 266.401 | 266.2336 | 263.9455 | 263.7432 | 263.9639 | 263.8411 | 263.6789 | 263.7725 | 264.6804 | 264.5955 | 264.6575 | 264.9643 | 265.0113 | 265.0082 | 264.7966 | 264.9416 | 264.7798 | 239.1629 | 239.0453 | 239.1113 | 239.2667 | 239.2099 | 239.1207
247 | Suction enthalpy | KJ/kg | 410.5988 | 410.834 | 410.7913 | 412.6953 | 412.6765 | 412.6035 | 414.7517 | 414.6521 | 414.5375 | 413.6497 | 413.5144 | 413.3518 | 413.131 | 413.0822 | 413.0885 | 411.6885 | 411.5973 | 411.3634 | 413.411 | 412.9647 | 412.8886 | 412.0786 | 411.6417 | 411.5163 | 411.0019 | 410.9843 | 410.9743 | 411.0823 | 410.9918 | 410.9396 | 412.3366 | 412.2237 | 412.0534 | 411.8219 | 411.6407 | 411.4218 | 412.1205 | 410.2804 | 410.2645 | 410.257 | 410.3312 | 410.3468 | 410.395 | 410.5446 | 410.8656 | 408.9269 | 409.2793 | 408.5159 | 410.4202 | 410.4182 | 410.3971 | 411.0814 | 410.8859 | 410.6906 | 408.0078 | 408.1048 | 408.2118 | 412.1669 | 412.0205 | 412.0527 | 412.408 | 412.4243 | 412.4319 | 412.9127 | 413.283 | 413.6703 | 412.8833 | 412.9246 | 412.9183 | 412.4238 | 412.3448 | 410.6295 | 410.4979 | 410.0451 | 411.6766 | 411.5949 | 411.4846 | 411.1166 | 411.5799 | 411.6023 | 411.6899 | 412.023 | 412.0608 | 412.0838 | 412.2246 | 413.0035 | 413.0567 | 412.8122 | 409.7464 | 410.036 | 410.3399 | 410.4155 | 409.6171 | 410.6118 | 410.8904 | 414.4393 | 414.8638 | 414.4055 | 416.9257 | 416.8978 | 416.8806 | 416.8486 | 416.7523 | 416.6903 | 416.6752 | 416.6134 | 408.9761 | 409.2313 | 409.2239 | 409.6353 | 409.8208 | 410.5235 | 411.3467 | 411.5526 | 411.7725 | 409.2577 | 409.9033 | 409.3565 | 412.2889 | 412.1437 | 412.3106 | 408.3339 | 408.1734 | 407.9611 | 409.6189 | 409.3679 | 409.0017 | 410.702 | 410.3908 | 410.5206 | 409.3928 | 409.5704 | 409.5737 | 411.4868 | 411.4839 | 411.2306 | 412.9167 | 413.1295 | 413.8673 | 413.6792 | 413.2696 | 412.9258 | 412.3954 | 412.5565 | 412.644 | 412.6428 | 412.3572 | 412.2746 | 410.8522 | 410.8139 | 410.7693 | 411.5833 | 411.404 | 410.9949 | 409.3795 | 408.3465 | 407.1389 | 409.3125 | 409.1365 | 409.1607 | 409.2558 | 409.0055 | 409.0704 | 410.7734 | 411.8971 | 411.17 | 413.3614 | 413.1889 | 413.0139 | 411.1501 | 411.1108 | 411.2978 | 411.4298 | 411.4038 | 410.6409 | 412.004 | 412.0712 | 411.9875 | 412.5182 | 412.3355 | 412.2751 | 412.1744 | 412.4362 | 412.5856 | 412.5667 | 412.6636 | 412.8797 | 412.1746 | 412.1736 | 412.4331 | 411.6273 | 411.8038 | 411.8173 | 411.4516 | 411.4011 | 411.5798 | 411.9126 | 411.7028 | 411.5991 | 408.7064 | 408.6856 | 408.5895 | 408.4838 | 408.2306 | 407.9068 | 409.9783 | 409.8546 | 410.1028 | 409.8195 | 409.8657 | 410.0048 | 410.0054 | 409.9389 | 409.6977 | 409.8596 | 409.9155 | 409.892 | 410.2989 | 410.1279 | 410.0258 | 412.3228 | 412.4389 | 412.4255 | 412.3547 | 412.48 | 412.6567
248 | Mass flow rate | kg/s | 3.4113 | 3.3961 | 3.3989 | 3.6032 | 3.6028 | 3.5954 | 2.245 | 2.2506 | 2.2466 | 1.9719 | 1.9843 | 1.9989 | 2.0022 | 1.9923 | 1.9941 | 0.90279 | 0.90239 | 0.90339 | 0.95738 | 0.96313 | 0.97594 | 1.9955 | 2.0039 | 2.0079 | 2.1523 | 2.1567 | 2.1625 | 2.1544 | 2.1618 | 2.1624 | 3.4232 | 3.4153 | 3.4132 | 3.6009 | 3.6014 | 3.5939 | 3.5601 | 4.9802 | 4.9928 | 4.989 | 4.9863 | 4.9803 | 4.9786 | 4.9947 | 4.986 | 4.9395 | 4.9277 | 4.9444 | 5.3674 | 5.3761 | 5.3614 | 5.3669 | 5.3656 | 5.3682 | 4.872 | 4.8748 | 4.8678 | 3.2563 | 3.2448 | 3.2439 | 3.3194 | 3.3287 | 3.3173 | 1.9283 | 1.927 | 1.9185 | 0.81133 | 0.82824 | 0.77394 | 0.89741 | 0.9016 | 3.5591 | 3.5572 | 3.5789 | 2.0998 | 2.0996 | 2.1068 | 2.1139 | 2.2208 | 2.2316 | 2.2242 | 2.0907 | 2.0913 | 2.0981 | 0.87332 | 0.89993 | 0.87827 | 0.90689 | 4.8635 | 4.8719 | 4.8808 | 4.8639 | 5.295 | 5.2907 | 5.2826 | 5.1749 | 5.1771 | 5.2175 | 5.2843 | 5.3043 | 5.293 | 5.2932 | 5.3034 | 5.3113 | 5.3045 | 5.3194 | 5.076 | 5.0697 | 5.0724 | 5.5437 | 5.5157 | 5.5064 | 5.491 | 5.4786 | 5.4826 | 5.1164 | 5.0837 | 5.1154 | 2.2677 | 2.2716 | 2.2653 | 5.0749 | 5.0757 | 5.089 | 5.5529 | 5.5225 | 5.5315 | 5.5029 | 5.513 | 5.5463 | 5.1119 | 5.0984 | 5.0966 | 2.2775 | 2.2874 | 2.2923 | 2.136 | 2.1344 | 2.1239 | 1.9791 | 1.9755 | 1.9819 | 0.82416 | 0.8299 | 0.87659 | 0.93914 | 0.9198 | 0.92729 | 3.4629 | 3.4756 | 3.474 | 3.6779 | 3.6857 | 3.6916 | 5.0125 | 5.0357 | 5.0512 | 5.4851 | 5.4954 | 5.4851 | 5.4924 | 5.4956 | 5.4857 | 5.0671 | 5.0496 | 5.0464 | 2.2403 | 2.2349 | 2.2491 | 5.4632 | 5.4592 | 5.4415 | 5.4556 | 5.4714 | 5.4878 | 2.2689 | 2.2507 | 2.274 | 0.92179 | 0.92952 | 0.93996 | 0.87424 | 0.85589 | 0.85789 | 0.91385 | 0.92291 | 0.92444 | 2.1433 | 2.1403 | 2.1294 | 1.9858 | 1.9776 | 1.975 | 3.4291 | 3.4057 | 3.3592 | 3.6794 | 3.6723 | 3.6718 | 5.0149 | 5.0236 | 5.038 | 5.052 | 5.0508 | 5.0328 | 5.4704 | 5.4838 | 5.4722 | 5.4733 | 5.4556 | 5.4781 | 5.4703 | 5.4575 | 5.468 | 5.4615 | 5.4676 | 5.4607 | 5.0459 | 5.016 | 5.0417 | 2.2674 | 2.2661 | 2.2739 | 2.269 | 2.2731 | 2.2662
249 | Duty (calculated) | kw | 540.8805 | 539.7043 | 539.5458 | 579.6241 | 579.1164 | 578.1612 | 393.9223 | 394.3059 | 393.685 | 344.212 | 345.6501 | 347.8254 | 347.8734 | 346.2072 | 346.8584 | 162.323 | 162.1614 | 162.3914 | 174.0367 | 174.4735 | 176.887 | 344.9519 | 345.2318 | 345.9265 | 369.9332 | 370.6959 | 371.5539 | 370.2976 | 371.3379 | 371.1617 | 548.4659 | 547.0461 | 546.4694 | 575.8071 | 574.9503 | 573.2587 | 570.2439 | 724.1033 | 725.7734 | 725.0676 | 725.2018 | 724.4339 | 724.4052 | 727.6878 | 728.0313 | 703.4734 | 704.0912 | 702.8111 | 780.3448 | 782.5409 | 780.5032 | 788.7115 | 788.5019 | 788.4488 | 689.9625 | 690.2268 | 690.3263 | 521.7365 | 519.4672 | 518.8974 | 532.6852 | 534.3885 | 532.7135 | 335.1249 | 335.35 | 334.6935 | 147.0646 | 150.1079 | 140.1225 | 161.8291 | 162.8532 | 565.0233 | 564.4505 | 565.8985 | 362.291 | 362.0312 | 362.9766 | 363.0978 | 382.7382 | 384.7734 | 383.7492 | 361.5918 | 361.782 | 362.8972 | 157.3059 | 162.7231 | 159.0094 | 164.0821 | 706.0506 | 707.3473 | 709.7574 | 708.1543 | 766.2299 | 771.1453 | 771.7763 | 778.5322 | 780.904 | 784.3735 | 803.8838 | 806.2305 | 805.3498 | 805.1625 | 809.0632 | 809.0355 | 808.7085 | 812.4026 | 723.5485 | 724.0419 | 724.0891 | 802.2418 | 800.7644 | 802.7703 | 809.2512 | 809.4669 | 810.8308 | 737.8364 | 738.266 | 739.2393 | 391.9547 | 392.2816 | 392.3825 | 719.2411 | 718.4432 | 719.5961 | 807.7164 | 802.7335 | 802.2793 | 802.952 | 802.504 | 807.984 | 739.3523 | 738.8509 | 738.8339 | 391.9746 | 393.4178 | 394.5115 | 370.5324 | 371.1862 | 370.5925 | 345.3086 | 344.1844 | 344.4285 | 148.8988 | 150.067 | 158.6144 | 169.785 | 166.0926 | 167.4398 | 550.1263 | 552.7647 | 552.4402 | 587.4418 | 587.8488 | 587.8927 | 715.3194 | 714.3057 | 709.7185 | 791.3204 | 791.8306 | 791.5235 | 796.7927 | 797.5691 | 795.7307 | 737.6399 | 742.064 | 738.7508 | 390.4075 | 388.3136 | 391.0304 | 803.4694 | 802.5705 | 801.2543 | 798.9917 | 799.9889 | 797.88 | 391.9455 | 389.2827 | 392.8844 | 166.4161 | 167.6825 | 169.587 | 157.7773 | 154.5666 | 155.0662 | 165.1825 | 167.1127 | 167.7339 | 370.4519 | 370.0909 | 369.2008 | 342.1561 | 341.3926 | 340.9634 | 546.3814 | 542.7382 | 537.1293 | 588.6029 | 587.0715 | 586.9016 | 712.8794 | 715.3722 | 716.6835 | 717.7403 | 716.3569 | 713.0085 | 798.8606 | 801.2481 | 799.6945 | 798.9865 | 797.532 | 801.0708 | 794.9671 | 793.2079 | 793.0837 | 791.3486 | 792.2757 | 791.1702 | 734.1853 | 728.2485 | 732.2802 | 392.614 | 392.9207 | 394.1046 | 392.7386 | 393.8681 | 393.2637
250
251 | Energy balance kW/(Mref*(Hd-Hs)) no NI, No econ | kw | -1.0053 | -0.9931 | -0.98963 | -0.99203 | -0.99658 | -0.99178 | -1.023 | -1.0322 | -1.0228 | -1.0355 | -1.0259 | -1.0287 | -1.0309 | -1.032 | -1.0393 | -1.0612 | -1.1058 | -1.073 | -1.1199 | -1.0858 | -1.1496 | -1.0338 | -1.0281 | -1.0129 | -1.0329 | -1.0165 | -1.0311 | -1.0354 | -1.0275 | -1.0365 | -1.0149 | -1.0075 | -1.0085 | -1.0082 | -1.0065 | -1.0118 | -0.99042 | -0.9925 | -0.98983 | -0.99067 | -0.9906 | -0.99361 | -0.995 | -0.98507 | -0.9951 | -0.99525 | -1.0048 | -0.99349 | -0.98551 | -0.99491 | -1.0018 | -0.99686 | -1.0025 | -0.9912 | -0.98295 | -1.0021 | -0.99458 | -1.0088 | -1.0121 | -1.0178 | -1.0004 | -0.99867 | -1.0002 | -0.9942 | -0.9892 | -1.0005 | -1.1841 | -1.1449 | -1.2722 | -1.1985 | -1.1582 | -0.99958 | -0.99807 | -0.9689 | -1.0252 | -1.0326 | -1.0424 | -1.0389 | -1.0221 | -1.0168 | -1.0153 | -1.0087 | -1.0192 | -1.0136 | -1.1043 | -1.1023 | -1.1134 | -1.0646 | -0.99667 | -0.99804 | -0.99391 | -0.99454 | -0.98331 | -0.98848 | -0.9942 | -0.99128 | -0.99654 | -0.99436 | -1.1398 | -1.1289 | -1.1375 | -1.1457 | -1.1347 | -1.1381 | -1.1361 | -1.149 | -0.98929 | -0.9934 | -0.9939 | -0.98073 | -0.99225 | -1.0014 | -0.99703 | -0.99488 | -0.99526 | -0.98712 | -1.0017 | -0.99515 | -1.0108 | -1.0046 | -1.0025 | -0.9967 | -1.0008 | -0.98758 | -0.9966 | -1.0004 | -0.99587 | -1.0017 | -1.0024 | -0.98139 | -1.0004 | -0.99782 | -1.0037 | -1.02 | -1.0299 | -1.0028 | -1.0187 | -1.0002 | -1.0462 | -1.0407 | -1.058 | -1.0518 | -1.1765 | -1.1853 | -1.1286 | -1.0946 | -1.1787 | -1.162 | -0.9953 | -0.99983 | -0.9874 | -1.0124 | -1.0062 | -1.0069 | -0.99672 | -0.98115 | -0.98094 | -0.99705 | -0.98872 | -0.98625 | -1.0021 | -0.98898 | -0.99384 | -0.99153 | -1.002 | -0.99276 | -1.0336 | -1.0563 | -1.0388 | -0.99392 | -1.0053 | -0.99203 | -1.003 | -1.0061 | -0.99438 | -1.0266 | -1.0229 | -0.98533 | -1.1128 | -1.103 | -1.0626 | -1.0863 | -1.1042 | -1.0987 | -1.1144 | -1.0978 | -1.1121 | -1.0241 | -1.0153 | -1.0253 | -1.0176 | -1.0246 | -1.0009 | -1.0061 | -1.0162 | -1.0071 | -1.0122 | -1.0099 | -1.0211 | -0.99889 | -0.99449 | -0.98908 | -0.99646 | -0.99458 | -1.0007 | -0.9984 | -0.99576 | -1.0036 | -1.0093 | -1.0032 | -1.0005 | -0.99947 | -1.0002 | -0.99156 | -0.99069 | -1.0071 | -1.0018 | -1.0067 | -1.0115 | -1.0129 | -1.0253 | -1.0354 | -1.0255 | -1.0311 | -1.0303 | -1.048
252 | Energy balance kW/(Mref*(Hd-Hs)) no NI, | kw
253 | Energy balance kW/(Mref*(Hd-Hs)) | kw
254
255 | COP | - | 4.5262 | 4.5433 | 4.5176 | 4.5436 | 4.5241 | 4.5314 | 6.6588 | 6.5944 | 6.6424 | 6.3526 | 6.4056 | 6.3855 | 6.3751 | 6.3894 | 6.399 | 8.4087 | 8.1192 | 8.2731 | 8.4231 | 8.6826 | 8.3289 | 6.5489 | 6.5373 | 6.5549 | 6.4563 | 6.5563 | 6.4854 | 6.2196 | 6.2785 | 6.2546 | 4.4826 | 4.5149 | 4.4955 | 4.4759 | 4.4801 | 4.4525 | 4.5129 | 3.1502 | 3.158 | 3.1554 | 3.1564 | 3.1469 | 3.1449 | 3.1798 | 3.163 | 2.7523 | 2.7498 | 2.7601 | 3.0963 | 3.0705 | 3.0369 | 3.1327 | 3.1241 | 3.1576 | 2.7806 | 2.7278 | 2.7526 | 4.4963 | 4.4684 | 4.4503 | 4.5226 | 4.5297 | 4.5231 | 6.4184 | 6.4634 | 6.4471 | 7.6169 | 7.9389 | 7.2023 | 7.7615 | 8.162 | 4.477 | 4.4644 | 4.4723 | 6.4868 | 6.4299 | 6.3618 | 6.3778 | 6.4449 | 6.4737 | 6.501 | 6.0455 | 5.9828 | 6.01 | 7.5781 | 7.7815 | 7.7321 | 7.9896 | 3.1144 | 3.1138 | 3.1354 | 3.1348 | 3.0632 | 3.0778 | 3.0648 | 3.1398 | 3.1408 | 3.1581 | 3.1769 | 3.2107 | 3.2094 | 3.1993 | 3.2425 | 3.2277 | 3.2495 | 3.2641 | 2.8959 | 2.8934 | 2.8944 | 3.2083 | 3.1717 | 3.1655 | 3.2318 | 3.2435 | 3.247 | 3.2417 | 3.2594 | 3.2563 | 6.6315 | 6.6537 | 6.6966 | 2.8585 | 2.849 | 2.8733 | 3.2261 | 3.21 | 3.217 | 3.1827 | 3.1754 | 3.2225 | 3.2609 | 3.2734 | 3.2667 | 6.675 | 6.6763 | 6.7862 | 6.6121 | 6.6773 | 6.5772 | 6.6599 | 6.6092 | 6.6252 | 7.5557 | 7.5741 | 8.0426 | 8.2537 | 7.8934 | 8.1355 | 4.6827 | 4.6771 | 4.7111 | 4.6075 | 4.6531 | 4.6402 | 2.8616 | 2.8934 | 2.853 | 3.1494 | 3.1713 | 3.1865 | 3.2004 | 3.2188 | 3.1911 | 3.2713 | 3.2914 | 3.3006 | 6.6916 | 6.5771 | 6.7063 | 3.2077 | 3.1622 | 3.2086 | 3.1446 | 3.1398 | 3.1582 | 6.6549 | 6.6473 | 6.7561 | 7.94 | 7.9661 | 8.2047 | 8.1345 | 7.8793 | 8.0074 | 7.9652 | 8.1351 | 8.1425 | 6.6173 | 6.6676 | 6.6448 | 6.5228 | 6.4736 | 6.5331 | 4.6449 | 4.6338 | 4.6708 | 4.5872 | 4.5959 | 4.5639 | 2.832 | 2.8606 | 2.8727 | 2.8534 | 2.8561 | 2.825 | 3.2075 | 3.2127 | 3.1969 | 3.1704 | 3.1913 | 3.2039 | 3.157 | 3.1546 | 3.1556 | 3.1567 | 3.1055 | 3.1228 | 3.2315 | 3.2118 | 3.2397 | 6.7216 | 6.6717 | 6.7338 | 6.6807 | 6.7141 | 6.6937
256
257
258 | Conditions to compcalc
259 | Table Duty
260 | % of Duty
261 | Table Power
262 | % of Power
263 | Table COP
264 | % of COP
265
266 | Econ Port specific volume with assumed SH | m3/kg | 0.025133 | 0.025212 | 0.025245 | 0.025491 | 0.025545 | 0.025557 | 0.026114 | 0.026138 | 0.02618 | 0.026248 | 0.02628 | 0.026316 | 0.026379 | 0.026413 | 0.026442 | 0.026856 | 0.026918 | 0.026925 | 0.027279 | 0.02739 | 0.027401 | 0.02525 | 0.025236 | 0.025249 | 0.025205 | 0.025198 | 0.025185 | 0.025138 | 0.025123 | 0.02513 | 0.024968 | 0.024953 | 0.024978 | 0.025047 | 0.025027 | 0.025009 | 0.024981 | 0.025058 | 0.025062 | 0.025069 | 0.02514 | 0.025157 | 0.025193 | 0.025228 | 0.025314 | 0.02616 | 0.026207 | 0.026307 | 0.026822 | 0.026873 | 0.02695 | 0.027142 | 0.027248 | 0.027234 | 0.024952 | 0.025012 | 0.025037 | 0.025688 | 0.025721 | 0.025724 | 0.025893 | 0.025891 | 0.025924 | 0.026583 | 0.026619 | 0.026628 | 0.027255 | 0.027274 | 0.027309 | 0.027402 | 0.027433 | 0.025468 | 0.025495 | 0.025546 | 0.026158 | 0.026135 | 0.026165 | 0.026327 | 0.026372 | 0.026407 | 0.026414 | 0.026795 | 0.026806 | 0.026817 | 0.027259 | 0.027306 | 0.027311 | 0.027293 | 0.023463 | 0.023492 | 0.023508 | 0.023516 | 0.023772 | 0.023814 | 0.023845 | 0.024145 | 0.024183 | 0.024342 | 0.023777 | 0.023806 | 0.023834 | 0.023834 | 0.023899 | 0.023948 | 0.023992 | 0.024055 | 0.024993 | 0.025034 | 0.025075 | 0.025461 | 0.025502 | 0.025566 | 0.025643 | 0.025695 | 0.025744 | 0.026008 | 0.026126 | 0.026225 | 0.027339 | 0.027401 | 0.027405 | 0.025028 | 0.025099 | 0.025147 | 0.02548 | 0.02553 | 0.025557 | 0.025961 | 0.026012 | 0.026069 | 0.026203 | 0.026275 | 0.026364 | 0.028015 | 0.028049 | 0.028109 | 0.027021 | 0.027054 | 0.027105 | 0.027307 | 0.027347 | 0.027404 | 0.02623 | 0.026241 | 0.026243 | 0.026229 | 0.026246 | 0.026242 | 0.025855 | 0.025892 | 0.025913 | 0.02621 | 0.026226 | 0.02628 | 0.025046 | 0.025208 | 0.025314 | 0.025574 | 0.02563 | 0.025731 | 0.025906 | 0.026009 | 0.026121 | 0.025507 | 0.02555 | 0.025606 | 0.026722 | 0.026784 | 0.026808 | 0.025024 | 0.025086 | 0.025156 | 0.025337 | 0.025427 | 0.025498 | 0.02592 | 0.025959 | 0.025982 | 0.025362 | 0.025376 | 0.02538 | 0.025394 | 0.025387 | 0.025399 | 0.025411 | 0.025424 | 0.025437 | 0.025502 | 0.025503 | 0.02553 | 0.025441 | 0.025451 | 0.02547 | 0.025925 | 0.02599 | 0.026042 | 0.026421 | 0.026482 | 0.026551 | 0.023588 | 0.023621 | 0.023663 | 0.023771 | 0.023799 | 0.023904 | 0.024446 | 0.024475 | 0.024508 | 0.02456 | 0.024614 | 0.024644 | 0.024768 | 0.024805 | 0.024844 | 0.024932 | 0.024952 | 0.025017 | 0.025166 | 0.025224 | 0.025284 | 0.026272 | 0.026296 | 0.026318 | 0.02639 | 0.026428 | 0.026449
267 | Econ Port Enthalpy with assumed SH | KJ/kg | 421.6713 | 421.6157 | 421.5928 | 421.4216 | 421.384 | 421.3757 | 420.994 | 420.9778 | 420.9492 | 420.9031 | 420.8812 | 420.8571 | 420.8149 | 420.7918 | 420.7726 | 420.4959 | 420.4548 | 420.4502 | 420.2175 | 420.1454 | 420.138 | 421.5889 | 421.5988 | 421.5899 | 421.6208 | 421.6256 | 421.6345 | 421.6677 | 421.678 | 421.6731 | 421.7871 | 421.7978 | 421.7801 | 421.7313 | 421.7458 | 421.7582 | 421.7778 | 421.7242 | 421.7212 | 421.7165 | 421.666 | 421.6541 | 421.6291 | 421.6048 | 421.5447 | 420.963 | 420.9308 | 420.8635 | 420.5186 | 420.4848 | 420.4342 | 420.3076 | 420.2383 | 420.2476 | 421.7989 | 421.7566 | 421.7384 | 421.2855 | 421.2627 | 421.2608 | 421.1445 | 421.1457 | 421.1233 | 420.6775 | 420.6534 | 420.6476 | 420.2337 | 420.2211 | 420.1981 | 420.1373 | 420.1177 | 421.4374 | 421.4186 | 421.3834 | 420.9643 | 420.9798 | 420.9589 | 420.8497 | 420.8196 | 420.7961 | 420.7912 | 420.5368 | 420.5296 | 420.522 | 420.2311 | 420.2001 | 420.1969 | 420.2087 | 422.8782 | 422.8565 | 422.8441 | 422.8388 | 422.6491 | 422.6181 | 422.5959 | 422.3767 | 422.3494 | 422.2338 | 422.6455 | 422.6242 | 422.604 | 422.604 | 422.5562 | 422.52 | 422.4878 | 422.4419 | 421.7699 | 421.7405 | 421.7119 | 421.4421 | 421.4134 | 421.3692 | 421.3162 | 421.2801 | 421.2467 | 421.0662 | 420.986 | 420.9188 | 420.1784 | 420.1384 | 420.136 | 421.745 | 421.6951 | 421.6617 | 421.4293 | 421.3946 | 421.3759 | 421.0979 | 421.0632 | 421.0247 | 420.9336 | 420.885 | 420.8249 | 419.7425 | 419.721 | 419.6829 | 420.3872 | 420.3653 | 420.332 | 420.1996 | 420.1737 | 420.1365 | 420.9149 | 420.9076 | 420.9065 | 420.9157 | 420.9043 | 420.9068 | 421.1702 | 421.1449 | 421.1305 | 420.9286 | 420.9178 | 420.8815 | 421.7324 | 421.6184 | 421.5443 | 421.3637 | 421.3253 | 421.2558 | 421.1358 | 421.0655 | 420.9889 | 421.4105 | 421.3803 | 421.3421 | 420.5849 | 420.544 | 420.528 | 421.7481 | 421.7045 | 421.655 | 421.5284 | 421.4658 | 421.4167 | 421.1261 | 421.0996 | 421.0834 | 421.5113 | 421.5012 | 421.4982 | 421.4886 | 421.4935 | 421.4855 | 421.477 | 421.4677 | 421.4589 | 421.4134 | 421.413 | 421.3944 | 421.4559 | 421.4491 | 421.4359 | 421.1224 | 421.0784 | 421.043 | 420.7865 | 420.7454 | 420.6995 | 422.7855 | 422.7605 | 422.7297 | 422.6501 | 422.6297 | 422.5521 | 422.1594 | 422.1385 | 422.1147 | 422.0775 | 422.0387 | 422.0175 | 421.9287 | 421.9028 | 421.8749 | 421.8125 | 421.7986 | 421.753 | 421.6483 | 421.6073 | 421.5656 | 420.8865 | 420.8706 | 420.856 | 420.8075 | 420.7819 | 420.768
268 | Econ liquid out enthalpy | KJ/kg | 253.5869 | 253.4243 | 253.357 | 252.8573 | 252.7479 | 252.7238 | 251.6175 | 251.5709 | 251.4884 | 251.3557 | 251.2926 | 251.2231 | 251.1018 | 251.0355 | 250.9804 | 250.1883 | 250.071 | 250.058 | 249.3961 | 249.1916 | 249.1707 | 253.3458 | 253.3747 | 253.3488 | 253.439 | 253.4531 | 253.4791 | 253.5763 | 253.6067 | 253.5923 | 253.9267 | 253.9582 | 253.9062 | 253.7629 | 253.8054 | 253.8419 | 253.8996 | 253.7421 | 253.7332 | 253.7195 | 253.5715 | 253.5367 | 253.4634 | 253.3922 | 253.2165 | 251.5281 | 251.4354 | 251.2417 | 250.253 | 250.1567 | 250.0122 | 249.6521 | 249.455 | 249.4814 | 253.9613 | 253.8372 | 253.7836 | 252.4615 | 252.3954 | 252.3897 | 252.0526 | 252.056 | 251.9911 | 250.7077 | 250.6387 | 250.622 | 249.442 | 249.4063 | 249.3409 | 249.1687 | 249.1132 | 252.9034 | 252.8486 | 252.7462 | 251.5321 | 251.5766 | 251.5165 | 251.2019 | 251.1155 | 251.0478 | 251.0337 | 250.3052 | 250.2846 | 250.2628 | 249.4345 | 249.3466 | 249.3376 | 249.3712 | 257.1753 | 257.1098 | 257.0725 | 257.0565 | 256.4858 | 256.393 | 256.3265 | 255.6714 | 255.5901 | 255.2463 | 256.4752 | 256.4111 | 256.3506 | 256.3506 | 256.2076 | 256.0992 | 256.0029 | 255.8658 | 253.8763 | 253.7899 | 253.7059 | 252.9171 | 252.8336 | 252.7048 | 252.5508 | 252.4458 | 252.3487 | 251.8261 | 251.5944 | 251.4008 | 249.2851 | 249.1718 | 249.1649 | 253.8031 | 253.6568 | 253.5587 | 252.8799 | 252.7789 | 252.7243 | 251.9179 | 251.8174 | 251.7061 | 251.4436 | 251.3036 | 251.1306 | 248.055 | 247.9948 | 247.8878 | 249.8784 | 249.8161 | 249.7214 | 249.3454 | 249.2717 | 249.1663 | 251.3896 | 251.3685 | 251.3654 | 251.3919 | 251.3591 | 251.3662 | 252.1272 | 252.0539 | 252.0122 | 251.4291 | 251.398 | 251.2935 | 253.7661 | 253.4319 | 253.2153 | 252.6889 | 252.5772 | 252.3751 | 252.0274 | 251.8242 | 251.6028 | 252.8249 | 252.7373 | 252.6259 | 250.4426 | 250.3258 | 250.2798 | 253.8123 | 253.6844 | 253.5391 | 253.1691 | 252.9862 | 252.8432 | 251.9994 | 251.9227 | 251.8757 | 253.1191 | 253.0894 | 253.0809 | 253.0527 | 253.067 | 253.0436 | 253.0188 | 252.9918 | 252.9662 | 252.8336 | 252.8325 | 252.7781 | 252.9573 | 252.9376 | 252.8991 | 251.9886 | 251.8615 | 251.7591 | 251.0204 | 250.9023 | 250.7705 | 256.8957 | 256.8206 | 256.728 | 256.489 | 256.4277 | 256.1953 | 255.0254 | 254.9636 | 254.8931 | 254.783 | 254.6682 | 254.6055 | 254.3434 | 254.2671 | 254.185 | 254.0014 | 253.9605 | 253.8267 | 253.5196 | 253.3995 | 253.2777 | 251.3079 | 251.2621 | 251.2201 | 251.0805 | 251.007 | 250.967
269 | Econ Vol Flow Econ / Suc Thermodynamic | - | -0.0038402 | -0.0037477 | -0.0032594 | -0.0025586 | -0.0020305 | -0.0023066 | -0.030734 | -0.030366 | -0.030549 | -0.030867 | -0.030401 | -0.030239 | -0.029992 | -0.02995 | -0.030221 | -0.046821 | -0.046608 | -0.047142 | -0.045675 | -0.045099 | -0.045394 | -0.034523 | -0.034406 | -0.034617 | -0.034982 | -0.035075 | -0.035087 | -0.035122 | -0.035127 | -0.035032 | -0.0044376 | -0.0046674 | -0.0047836 | -0.0045359 | -0.0044566 | -0.0047339 | -0.0047834 | 0.028006 | 0.028101 | 0.028168 | 0.028553 | 0.028671 | 0.028919 | 0.029051 | 0.029567 | 0.036966 | 0.036812 | 0.037469 | 0.04008 | 0.039947 | 0.040319 | 0.039405 | 0.039558 | 0.039203 | 0.029159 | 0.029837 | 0.029656 | -0.0013129 | -0.0011752 | -0.00075631 | -0.00030471 | -0.00043239 | -0.00037529 | -0.029828 | -0.029313 | -0.029315 | -0.045764 | -0.045556 | -0.045231 | -0.044577 | -0.045217 | -0.0025904 | -0.002589 | -0.0020889 | -0.031497 | -0.031575 | -0.031386 | -0.030568 | -0.030526 | -0.030551 | -0.030552 | -0.027646 | -0.027538 | -0.027476 | -0.044614 | -0.044464 | -0.04482 | -0.045239 | 0.017183 | 0.018054 | 0.018355 | 0.018088 | 0.019971 | 0.020088 | 0.020125 | 0.019503 | 0.019762 | 0.020994 | 0.019098 | 0.019567 | 0.01923 | 0.019247 | 0.018384 | 0.019122 | 0.01898 | 0.018582 | 0.029377 | 0.02958 | 0.029919 | 0.030882 | 0.03024 | 0.030847 | 0.029064 | 0.028863 | 0.029406 | 0.034912 | 0.034398 | 0.035698 | -0.026256 | -0.026024 | -0.026774 | 0.030138 | 0.030663 | 0.030854 | 0.028925 | 0.028792 | 0.028853 | 0.033456 | 0.034059 | 0.034486 | 0.035301 | 0.035384 | 0.035803 | -0.02378 | -0.023442 | -0.024097 | -0.027383 | -0.027765 | -0.027046 | -0.026805 | -0.027063 | -0.026653 | -0.048725 | -0.048649 | -0.048879 | -0.04833 | -0.048504 | -0.04866 | -0.00034802 | -0.00072217 | -0.00067631 | 0.0011224 | 0.0013269 | 0.0011747 | 0.030259 | 0.030909 | 0.032098 | 0.031999 | 0.032359 | 0.032392 | 0.031713 | 0.031544 | 0.032617 | 0.0318 | 0.03108 | 0.031145 | -0.029208 | -0.028183 | -0.028873 | 0.025516 | 0.025917 | 0.026158 | 0.029832 | 0.031076 | 0.031774 | -0.032072 | -0.032155 | -0.031881 | -0.050344 | -0.05042 | -0.050642 | -0.051273 | -0.049954 | -0.049869 | -0.050151 | -0.050464 | -0.050567 | -0.033388 | -0.033553 | -0.033769 | -0.033652 | -0.033855 | -0.033762 | 0.00032354 | 0.00045655 | -0.00020187 | 0.002403 | 0.0024399 | 0.0025893 | 0.021171 | 0.020792 | 0.021195 | 0.022053 | 0.02218 | 0.022398 | 0.021756 | 0.021403 | 0.022177 | 0.022169 | 0.022044 | 0.022509 | 0.025633 | 0.025597 | 0.026061 | 0.027399 | 0.027667 | 0.028063 | 0.028472 | 0.029123 | 0.029185 | -0.030903 | -0.030978 | -0.030797 | -0.030279 | -0.030189 | -0.030332
270 | Econ Vol Flow Econ / Suc Measured | - | -3.5438e-05 | -5.8976e-05 | -4.2364e-05 | -2.9069e-05 | -4.6554e-05 | -3.6527e-05 | -6.3265e-05 | -6.449e-05 | -1.7494e-05 | -6.2851e-05 | -6.2145e-05 | -4.0617e-05 | -7.0545e-05 | -3.1341e-05 | -2.9381e-05 | -6.7269e-05 | -0.00022498 | -2.8842e-05 | -6.5021e-05 | -0.00011803 | -2.0058e-05 | -0.00011152 | -5.2134e-05 | -7.4526e-05 | -0.00010843 | -6.2519e-05 | -8.0123e-05 | -5.9548e-05 | -7.612e-05 | -7.7234e-05 | -4.4674e-05 | -2.7614e-05 | -5.8097e-05 | -4.0983e-05 | -7.8008e-05 | -4.3143e-05 | -3.525e-05 | 0.02702 | 0.028127 | 0.026048 | 0.036369 | 0.048472 | 0.038607 | 0.036416 | 0.034983 | -2.0807e-05 | -2.2461e-05 | -1.6008e-05 | -1.722e-05 | -2.2007e-05 | -9.7939e-06 | -1.338e-05 | 7.2454e-06 | -7.4526e-06 | -2.0256e-05 | -3.3505e-05 | -3.1662e-05 | -6.0908e-05 | -2.6495e-05 | -3.7446e-05 | -4.9687e-05 | -3.5114e-05 | -2.3594e-05 | -3.7045e-05 | -1.6357e-05 | -1.4897e-05 | -1.8087e-05 | 1.3936e-05 | -3.7949e-05 | -2.4937e-05 | 1.9349e-05 | -2.6774e-05 | -3.2986e-05 | -4.8403e-05 | -1.0395e-05 | -3.874e-05 | -5.1459e-05 | -3.727e-05 | -6.196e-05 | -2.9744e-05 | -4.1226e-05 | -5.0689e-05 | -4.7816e-05 | -1.015e-05 | -2.3188e-05 | -6.3485e-05 | -5.2234e-05 | -4.6363e-05 | 0.031326 | 0.026001 | 0.030548 | 0.027373 | -3.7147e-05 | -3.274e-05 | -3.4264e-05 | -2.5736e-05 | -2.369e-05 | -3.1546e-05 | -3.2143e-05 | -3.7998e-05 | -4.2908e-05 | -2.8505e-05 | -2.2248e-05 | -4.7622e-05 | -3.3927e-05 | -1.8678e-05 | -1.8053e-05 | -2.7047e-05 | -3.5762e-05 | -8.5104e-06 | -4.0329e-05 | -1.9112e-05 | -1.987e-05 | -2.876e-05 | -2.4987e-05 | 0.025453 | 0.022331 | 0.025561 | 4.4148e-06 | -2.6279e-05 | -8.8398e-06 | -3.4531e-05 | -2.1755e-05 | -2.7719e-05 | -1.2282e-05 | -1.4246e-05 | 0.00020314 | -1.8785e-05 | -8.902e-06 | -2.1557e-05 | 0.035489 | 0.035503 | 0.035447 | 1.382e-05 | -1.3162e-06 | -1.869e-05 | -1.4324e-05 | -2.2178e-05 | -4.6998e-05 | 2.0619e-05 | 3.4603e-06 | 9.988e-06 | -8.3667e-05 | -4.7163e-05 | -9.7297e-05 | -0.00014276 | -0.00010802 | -2.4039e-05 | -2.8693e-05 | -2.8855e-05 | -1.8447e-05 | -1.2501e-05 | -1.9423e-05 | -3.4678e-05 | -3.1304e-05 | -1.0718e-05 | -2.2976e-05 | 0.0009407 | 0.0016767 | 0.0013966 | -1.7196e-05 | -4.7358e-06 | -2.338e-06 | 0.033538 | 0.023741 | 0.023869 | -3.9073e-05 | 1.0223e-05 | -3.4701e-05 | -2.3269e-05 | -9.9934e-06 | -1.7395e-05 | -2.015e-05 | -2.2364e-05 | -1.6027e-05 | -3.1837e-05 | 1.3401e-06 | -2.6299e-05 | -0.00013753 | -0.00011212 | -0.00011151 | -3.2372e-05 | -4.8958e-05 | -8.9855e-05 | -0.00010988 | -8.9526e-05 | -0.00011004 | -6.7124e-05 | -6.8321e-05 | -3.33e-05 | -2.7047e-05 | -3.6308e-05 | -3.1714e-05 | -2.2008e-05 | -1.1093e-05 | -2.5817e-05 | 2.2619e-06 | -1.124e-05 | -1.0425e-05 | 0.0026701 | 0.0011346 | 0.0013772 | -1.5418e-05 | -1.9561e-05 | -3.2768e-05 | -1.4917e-05 | -1.951e-05 | -1.9e-05 | -2.7998e-05 | -2.3703e-05 | -1.1813e-05 | -2.6593e-05 | -1.2881e-05 | -1.8664e-05 | -1.0517e-05 | -2.1162e-05 | -1.0717e-05 | 0.035783 | 0.035862 | 0.035832 | 1.436e-06 | -1.6334e-06 | -1.197e-05 | 5.366e-06 | -3.8523e-06 | 2.1257e-05
271 | Econ Balance (Measured/Thermo) |  | 0.0092282 | 0.015737 | 0.012998 | 0.011361 | 0.022927 | 0.015836 | 0.0020585 | 0.0021237 | 0.00057267 | 0.0020362 | 0.0020442 | 0.0013432 | 0.0023522 | 0.0010465 | 0.00097219 | 0.0014367 | 0.0048271 | 0.0006118 | 0.0014235 | 0.0026172 | 0.00044186 | 0.0032301 | 0.0015153 | 0.0021529 | 0.0030996 | 0.0017824 | 0.0022835 | 0.0016955 | 0.002167 | 0.0022047 | 0.010067 | 0.0059164 | 0.012145 | 0.0090352 | 0.017504 | 0.0091136 | 0.0073693 | 0.96481 | 1.0009 | 0.92474 | 1.2737 | 1.6906 | 1.335 | 1.2535 | 1.1832 | -0.00056288 | -0.00061016 | -0.00042724 | -0.00042965 | -0.00055089 | -0.00024291 | -0.00033954 | 0.00018316 | -0.00019011 | -0.00069465 | -0.0011229 | -0.0010676 | 0.046391 | 0.022546 | 0.049512 | 0.16306 | 0.081209 | 0.062867 | 0.001242 | 0.00055801 | 0.00050816 | 0.00039523 | -0.0003059 | 0.00083901 | 0.00055943 | -0.00042792 | 0.010336 | 0.012741 | 0.023172 | 0.00033005 | 0.0012269 | 0.0016395 | 0.0012193 | 0.0020298 | 0.00097356 | 0.0013494 | 0.0018335 | 0.0017364 | 0.00036941 | 0.00051975 | 0.0014278 | 0.0011654 | 0.0010249 | 1.8231 | 1.4402 | 1.6643 | 1.5133 | -0.0018601 | -0.0016298 | -0.0017026 | -0.0013196 | -0.0011988 | -0.0015026 | -0.0016831 | -0.0019419 | -0.0022313 | -0.001481 | -0.0012102 | -0.0024904 | -0.0017875 | -0.0010052 | -0.00061455 | -0.00091434 | -0.0011953 | -0.00027558 | -0.0013336 | -0.00061956 | -0.00068366 | -0.00099643 | -0.00084971 | 0.72907 | 0.64921 | 0.71602 | -0.00016815 | 0.0010098 | 0.00033016 | -0.0011458 | -0.00070949 | -0.00089838 | -0.0004246 | -0.00049478 | 0.0070404 | -0.00056146 | -0.00026137 | -0.00062509 | 1.0053 | 1.0034 | 0.99004 | -0.00058116 | 5.6147e-05 | 0.0007756 | 0.00052311 | 0.00079878 | 0.0017377 | -0.00076921 | -0.00012786 | -0.00037475 | 0.0017171 | 0.00096946 | 0.0019906 | 0.0029538 | 0.0022271 | 0.00049402 | 0.082448 | 0.039956 | 0.027276 | -0.011137 | -0.014638 | -0.029521 | -0.0010346 | -0.00034677 | -0.00071581 | 0.029398 | 0.051817 | 0.043114 | -0.00054223 | -0.00015013 | -7.1682e-05 | 1.0547 | 0.76386 | 0.76639 | 0.0013377 | -0.00036274 | 0.0012018 | -0.00091194 | -0.00038559 | -0.000665 | -0.00067544 | -0.00071967 | -0.00050441 | 0.00099266 | -4.1676e-05 | 0.00082493 | 0.0027319 | 0.0022237 | 0.002202 | 0.00063136 | 0.00098005 | 0.0018018 | 0.002191 | 0.0017741 | 0.0021761 | 0.0020104 | 0.0020362 | 0.00098612 | 0.00080371 | 0.0010725 | 0.00093932 | -0.068023 | -0.024299 | 0.12789 | 0.0009413 | -0.0046067 | -0.004026 | 0.12612 | 0.054567 | 0.064976 | -0.00069911 | -0.00088193 | -0.001463 | -0.00068565 | -0.00091156 | -0.00085674 | -0.0012629 | -0.0010752 | -0.0005248 | -0.0010374 | -0.00050323 | -0.00071618 | -0.00038386 | -0.00076489 | -0.0003819 | 1.2568 | 1.2314 | 1.2278 | -4.6469e-05 | 5.2729e-05 | 0.00038868 | -0.00017722 | 0.0001276 | -0.00070083
272 | Economised Duty |  | 535.6112 | 534.5778 | 535.096 | 575.9332 | 576.1901 | 574.839 | 366.2443 | 367.0384 | 366.3025 | 320.0279 | 321.9014 | 324.0861 | 324.4098 | 322.8472 | 323.2661 | 145.8013 | 145.7599 | 145.7209 | 157.0245 | 157.7342 | 159.779 | 316.7466 | 317.1455 | 317.5865 | 339.1284 | 339.7522 | 340.5906 | 339.3372 | 340.2333 | 340.2514 | 542.2657 | 540.5213 | 539.7824 | 569.1504 | 568.4215 | 566.3223 | 563.2824 | 779.595 | 781.5283 | 780.9635 | 781.6478 | 780.9613 | 781.2955 | 784.9356 | 786.0378 | 777.4702 | 777.8107 | 777.6258 | 859.6757 | 861.5819 | 859.8804 | 866.3691 | 866.1682 | 865.4049 | 750.519 | 752.0208 | 751.7233 | 520.0429 | 517.9577 | 517.9259 | 532.2875 | 533.8217 | 532.2234 | 312.7819 | 313.4231 | 312.8162 | 132.6045 | 135.4322 | 126.5993 | 146.506 | 147.1696 | 561.359 | 560.7958 | 562.9523 | 336.2688 | 335.9721 | 337.0229 | 338.0377 | 356.3516 | 358.2896 | 357.336 | 338.108 | 338.3261 | 339.5198 | 142.168 | 147.2795 | 143.7895 | 148.2225 | 742.0331 | 745.0422 | 748.0737 | 745.925 | 810.8357 | 815.9196 | 816.5062 | 821.6113 | 824.5786 | 830.4121 | 847.8718 | 851.2695 | 849.69 | 849.5426 | 851.4302 | 852.9516 | 852.2854 | 855.078 | 787.2941 | 788.0393 | 788.8548 | 868.8031 | 865.8954 | 869.0182 | 871.9533 | 871.6753 | 874.0589 | 805.4831 | 804.8007 | 808.0095 | 369.6438 | 370.2102 | 369.5724 | 784.2278 | 784.2737 | 785.754 | 870.3541 | 864.7612 | 864.4495 | 873.7675 | 874.2148 | 880.8346 | 807.4213 | 806.9046 | 807.5146 | 372.2224 | 373.9627 | 374.4374 | 348.2479 | 348.5775 | 348.6336 | 325.236 | 323.9818 | 324.5566 | 132.6938 | 133.7693 | 141.3747 | 151.4369 | 148.0857 | 149.2094 | 549.6542 | 551.7842 | 551.5222 | 589.0355 | 589.7337 | 589.5587 | 780.0139 | 780.1013 | 777.5005 | 859.0997 | 860.3626 | 859.9811 | 863.5574 | 863.8011 | 863.823 | 800.3355 | 803.6893 | 800.0833 | 364.995 | 363.9877 | 366.0042 | 859.5716 | 859.4268 | 858.4508 | 863.3998 | 866.7674 | 865.9582 | 363.0333 | 360.452 | 364.0886 | 146.932 | 148.0221 | 149.6357 | 139.1105 | 136.4022 | 136.8701 | 145.8034 | 147.3633 | 147.8306 | 341.5181 | 341.0331 | 339.9697 | 315.0908 | 314.1686 | 313.8598 | 546.814 | 543.3432 | 536.865 | 591.9918 | 590.5033 | 590.5383 | 761.3078 | 762.9096 | 765.0742 | 767.8807 | 766.7302 | 763.5292 | 847.6568 | 849.3938 | 849.331 | 848.5642 | 846.6905 | 851.2881 | 851.5134 | 849.5747 | 850.3477 | 851.2225 | 852.697 | 852.2296 | 791.0875 | 786.143 | 790.2697 | 365.0771 | 365.2368 | 366.57 | 365.9328 | 367.0517 | 366.4178
273 | Econ Power
274
275 | LI comp Power | kw | 0.2303 | 0.23196 | 0.22974 | 0.23439 | 0.2322 | 0.23341 | 0.22629 | 0.22458 | 0.2272 | 0.2269 | 0.22606 | 0.22421 | 0.22624 | 0.22553 | 0.2254 | 0.21636 | 0.2177 | 0.21765 | 0.21903 | 0.21936 | 0.88912 | 0.22583 | 0.22417 | 0.2245 | 0.22259 | 0.22452 | 0.22415 | 0.22484 | 0.22469 | 0.22504 | 0.23423 | 0.23403 | 0.23425 | 0.23541 | 0.2329 | 0.23403 | 0.2347 | 0.24378 | 0.2434 | 0.24239 | 0.24314 | 0.24367 | 0.24447 | 0.24445 | 0.24313 | 0.24661 | 0.24695 | 0.24623 | 0.24379 | 0.24312 | 0.24429 | 0.24472 | 0.24465 | 0.24264 | 0.25417 | 0.25252 | 0.25366 | 0.24091 | 0.24104 | 0.23978 | 0.24204 | 0.24157 | 0.2424 | 0.23342 | 0.23418 | 0.23409 | 0.22652 | 0.22587 | 0.22593 | 0.22588 | 0.22339 | 0.24001 | 0.24109 | 0.2422 | 0.23094 | 0.23175 | 0.23271 | 0.23123 | 0.23246 | 0.23132 | 0.23277 | 0.23548 | 0.23482 | 0.23576 | 0.22795 | 0.22887 | 0.22972 | 0.2276 | 0.252 | 0.25231 | 0.25089 | 0.2523 | 0.25205 | 0.25458 | 0.25364 | 0.25836 | 0.25935 | 0.25889 | 0.25774 | 0.25719 | 0.25676 | 0.25511 | 0.25682 | 0.25626 | 0.25493 | 0.25427 | 0.2549 | 0.25555 | 0.25462 | 0.25218 | 0.25298 | 0.25269 | 0.25313 | 0.25295 | 0.25397 | 0.25107 | 0.25016 | 0.25079 | 0.23491 | 0.23351 | 0.2334 | 0.25784 | 0.25601 | 0.25756 | 0.2535 | 0.25329 | 0.25396 | 0.25374 | 0.25451 | 0.25548 | 0.25139 | 0.25235 | 0.25072 | 0.23365 | 0.2339 | 0.23434 | 0.23771 | 0.23939 | 0.23931 | 0.23903 | 0.23771 | 0.23684 | 0.23267 | 0.23217 | 0.23385 | 0.23345 | 0.23235 | 0.23174 | 0.24528 | 0.24492 | 0.2464 | 0.24594 | 0.24528 | 0.24502 | 0.26074 | 0.25995 | 0.2597 | 0.25562 | 0.2555 | 0.25549 | 0.25405 | 0.25552 | 0.25541 | 0.25621 | 0.25744 | 0.25726 | 0.23851 | 0.23787 | 0.23919 | 0.26515 | 0.26363 | 0.26485 | 0.26521 | 0.26422 | 0.26443 | 0.24327 | 0.24393 | 0.24312 | 0.87867 | 2.9536 | 2.9552 | 0.23924 | 0.24002 | 0.24056 | 2.9639 | 2.9586 | 2.9586 | 0.24425 | 0.24452 | 0.24531 | 0.24477 | 0.24575 | 0.24654 | 0.25185 | 0.25263 | 0.25234 | 0.25495 | 0.25408 | 0.25441 | 0.26952 | 0.27168 | 0.26996 | 0.27086 | 0.27059 | 0.26988 | 0.26742 | 0.26683 | 0.26671 | 0.26795 | 0.26741 | 0.26729 | 0.26643 | 0.26767 | 0.26677 | 0.26837 | 0.26827 | 0.26622 | 0.2655 | 0.26622 | 0.26577 | 0.24723 | 0.2466 | 0.2456 | 0.2463 | 0.24661 | 0.24621
276
277
278 | Pressure Loss data
279 | Suction line PD
280 | Rig Data
281 | FCV01 Position |  | 19.9991 | 19.9991 | 19.9991 | 19.9991 | 19.9991 | 19.9991 | 19.9991 | 19.9991 | 19.9991 | 10.9991 | 10.9991 | 10.9991 | 10.9991 | 10.9991 | 10.9991 | 7.9997 | 7.9997 | 7.9997 | 11.9995 | 11.9995 | 11.9995 | 3.9999 | 3.9999 | 3.9999 | 4.9984 | 4.9984 | 4.9984 | 4.9984 | 4.9984 | 4.9984 | 20.9995 | 20.9995 | 20.9995 | 24.9993 | 24.9993 | 24.9993 | 23.9989 | 19.9991 | 19.9991 | 19.9991 | 19.9991 | 19.9991 | 19.9991 | 19.9991 | 19.9991 | 10.9991 | 10.9991 | 10.9991 | 14.9989 | 14.9989 | 14.9989 | 14.9989 | 14.9989 | 14.9989 | 20.9995 | 20.9995 | 20.9995 | 2.9995 | 2.9995 | 2.9995 | 2.9995 | 2.9995 | 2.9995 | 2.9995 | 2.9995 | 2.9995 | 0.99861 | 0.99861 | 0.99861 | 0.99861 | 0.99861 | 16.9997 | 16.9997 | 16.9997 | 14.9989 | 14.9989 | 14.9989 | 14.9989 | 17.9982 | 17.9982 | 17.9982 | 17.9982 | 17.9982 | 17.9982 | 2.9995 | 2.9995 | 2.9995 | 2.9995 | 25.9998 | 25.9998 | 25.9998 | 25.9998 | 25.9998 | 23.9989 | 23.9989 | 26.9982 | 26.9982 | 27.9987 | 11.9995 | 11.9995 | 11.9995 | 11.9995 | 11.9995 | 11.9995 | 11.9995 | 11.9995 | 2.9995 | 2.9995 | 2.9995 | 14.9989 | 14.9989 | 14.9989 | 14.9989 | 14.9989 | 14.9989 | 11.9995 | 13 | 13 | 15.9993 | 15.9993 | 15.9993 | 11.9995 | 11.9995 | 11.9995 | 13.9984 | 13.9984 | 13.9984 | 17.9982 | 17.9982 | 17.9982 | 16.9997 | 16.9997 | 16.9997 | 16.9997 | 16.9997 | 16.9997 | 10.9991 | 10.9991 | 4.9984 | 9.9986 | 9.9986 | 9.9986 | 0.99861 | 0.99861 | 0.99861 | 0.99861 | 0.99861 | 0.99861 | 5.9988 | 5.9988 | 5.9988 | 8.9982 | 8.9982 | 8.9982 | 13 | 13 | 13 | 13.9984 | 13.9984 | 13.9984 | 13.9984 | 13.9984 | 13.9984 | 14.9989 | 14.9989 | 14.9989 | 19.9991 | 19.9991 | 19.9991 | 10.9991 | 10.9991 | 10.9991 | 11.9995 | 11.9995 | 11.9995 | 18.9986 | 18.9986 | 18.9986 | 0.99861 | 0.99861 | 0.99861 | 0.99861 | 0.99861 | 0.99861 | 0.99861 | 0.99861 | 0.99861 | 13.9984 | 13.9984 | 13.9984 | 11.9995 | 11.9995 | 11.9995 | 15.9993 | 15.9993 | 15.9993 | 19.9991 | 19.9991 | 19.9991 | 13 | 13 | 13 | 13 | 13 | 13.9984 | 22.9984 | 22.9984 | 22.9984 | 22.9984 | 22.9984 | 22.9984 | 22 | 22 | 22 | 22 | 22 | 22 | 20.9995 | 20.9995 | 20.9995 | 13 | 13 | 13 | 13 | 13 | 13
282 | FCV02 Position |  | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998
283 | TCV031 Position |  | 10.9983 | 10.9983 | 9.9999 | 13.9995 | 11.9987 | 11.9987 | 12.9991 | 13.9995 | 12.9991 | 11.9987 | 11.9987 | 10.9983 | 10.9983 | 10.9983 | 10.9983 | 2.9991 | 1.9987 | 0.99835 | 0.99835 | 2.9991 | 0.99835 | 1.9987 | 1.9987 | 1.9987 | 3.9995 | 4.9999 | 4.9999 | 5.9983 | 5.9983 | 5.9983 | 2.9991 | 2.9991 | 2.9991 | 2.9991 | 2.9991 | 2.9991 | 3.9995 | 2.9991 | 2.9991 | 2.9991 | 2.9991 | 2.9991 | 2.9991 | 2.9991 | 2.9991 | 5.9983 | 5.9983 | 5.9983 | 5.9983 | 5.9983 | 5.9983 | 6.9987 | 6.9987 | 6.9987 | 7.9991 | 7.9991 | 7.9991 | 4.9999 | 5.9983 | 5.9983 | 5.9983 | 5.9983 | 5.9983 | 7.9991 | 7.9991 | 7.9991 | 2.9991 | 2.9991 | 2.9991 | 0.99835 | 0.99835 | 12.9991 | 12.9991 | 12.9991 | 8.9995 | 8.9995 | 8.9995 | 8.9995 | 8.9995 | 8.9995 | 8.9995 | 8.9995 | 8.9995 | 8.9995 | 11.9987 | 9.9999 | 4.9999 | 2.9991 | 4.9999 | 4.9999 | 2.9991 | 5.9983 | 6.9987 | 6.9987 | 8.9995 | 7.9991 | 6.9987 | 6.9987 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 1.9987 | 1.9987 | 1.9987 | 1.9987 | 2.9991 | 2.9991 | 1.9987 | 2.9991 | 0.99835 | 2.9991 | 2.9991 | 1.9987 | 2.9991 | 0.99835 | 0.99835 | 1.9987 | 0.99835 | 0.99835 | 0.99835 | 2.9991 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 1.9987 | 1.9987 | 1.9987 | 11.9987 | 11.9987 | 11.9987 | 10.9983 | 10.9983 | 10.9983 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 1.9987 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 1.9987 | 1.9987 | 0.99835 | 1.9987 | 1.9987 | 1.9987 | 0.99835 | 0.99835 | 0.99835 | 6.9987 | 7.9991 | 7.9991 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 7.9991 | 7.9991 | 7.9991 | 5.9983 | 5.9983 | 6.9987 | 9.9999 | 9.9999 | 9.9999 | 9.9999 | 9.9999 | 9.9999 | 9.9999 | 9.9999 | 9.9999 | 9.9999 | 9.9999 | 9.9999 | 9.9999 | 9.9999 | 9.9999 | 9.9999 | 9.9999 | 9.9999 | 9.9999 | 9.9999 | 9.9999 | 8.9995 | 8.9995 | 8.9995 | 8.9995 | 7.9991 | 7.9991 | 7.9991 | 7.9991 | 7.9991 | 7.9991 | 7.9991 | 7.9991
284
285 | Setpoint Suction Gauge | ºC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
286 | Setpoint Pressure Conversion Discharge | BarA | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928
287 | Setpoint Discharge Gauge | ºC | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
288 | Setpoint Pressure Conversion Discharge | BarA | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702
289
290 | Comp comcalc ID | - | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168
291
292
293 | Raw Data
294 | Copy of data from labview input - can be pasted into labview input cells to re-run log.
295 | Variable |  | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs
296 | a_Suction Pressure Comp (AI0) |  | 3.5968 | 3.5873 | 3.5884 | 3.6017 | 3.5943 | 3.5891 | 3.7889 | 3.7995 | 3.794 | 3.7862 | 3.8072 | 3.807 | 3.811 | 3.7996 | 3.7987 | 3.8575 | 3.8547 | 3.8411 | 3.8506 | 3.8567 | 3.8494 | 3.799 | 3.8079 | 3.8029 | 3.7896 | 3.7916 | 3.8008 | 3.7998 | 3.7963 | 3.8064 | 3.6017 | 3.5936 | 3.5869 | 3.5897 | 3.5944 | 3.587 | 3.594 | 3.3789 | 3.3815 | 3.3771 | 3.3791 | 3.3818 | 3.3835 | 3.3868 | 3.3888 | 3.1203 | 3.1137 | 3.1083 | 3.3788 | 3.3818 | 3.3794 | 3.38 | 3.378 | 3.3809 | 3.1144 | 3.1155 | 3.1128 | 3.5974 | 3.5923 | 3.5883 | 3.5973 | 3.5935 | 3.5906 | 3.8027 | 3.8042 | 3.8035 | 3.8404 | 3.8418 | 3.8577 | 3.8611 | 3.8468 | 3.5918 | 3.5918 | 3.5974 | 3.7965 | 3.8012 | 3.7992 | 3.8079 | 3.7993 | 3.8028 | 3.8017 | 3.6002 | 3.591 | 3.6037 | 3.8266 | 3.857 | 3.8543 | 3.8554 | 3.3572 | 3.3671 | 3.3747 | 3.365 | 3.3672 | 3.383 | 3.3887 | 3.3732 | 3.3736 | 3.3916 | 3.3847 | 3.3921 | 3.3787 | 3.3781 | 3.3858 | 3.3898 | 3.3829 | 3.3872 | 3.1149 | 3.1188 | 3.1122 | 3.384 | 3.3732 | 3.3782 | 3.3736 | 3.369 | 3.3743 | 3.3834 | 3.3709 | 3.3776 | 3.803 | 3.8043 | 3.788 | 3.1147 | 3.116 | 3.1191 | 3.3869 | 3.3778 | 3.3733 | 3.37 | 3.3797 | 3.3825 | 3.3777 | 3.373 | 3.3691 | 3.79 | 3.8016 | 3.7897 | 3.8016 | 3.8004 | 3.7965 | 3.8041 | 3.7984 | 3.7979 | 3.852 | 3.8523 | 3.8661 | 3.8482 | 3.8472 | 3.844 | 3.5865 | 3.5939 | 3.5897 | 3.6003 | 3.5993 | 3.5985 | 3.1162 | 3.1087 | 3.1058 | 3.3819 | 3.3775 | 3.3687 | 3.3765 | 3.3746 | 3.3702 | 3.3889 | 3.3777 | 3.381 | 3.792 | 3.7928 | 3.7994 | 3.378 | 3.3731 | 3.3674 | 3.374 | 3.3809 | 3.3759 | 3.8014 | 3.7902 | 3.7934 | 3.8394 | 3.8376 | 3.8404 | 3.8626 | 3.794 | 3.7913 | 3.8104 | 3.8042 | 3.7946 | 3.8043 | 3.8029 | 3.7912 | 3.7974 | 3.788 | 3.7866 | 3.6 | 3.5988 | 3.5962 | 3.599 | 3.5911 | 3.5855 | 3.1069 | 3.1137 | 3.118 | 3.1204 | 3.1154 | 3.1086 | 3.3846 | 3.3807 | 3.385 | 3.3785 | 3.3734 | 3.3813 | 3.3765 | 3.37 | 3.3721 | 3.3698 | 3.3726 | 3.3709 | 3.3801 | 3.3639 | 3.375 | 3.7952 | 3.7838 | 3.7898 | 3.8022 | 3.7946 | 3.7985
297 | b_subcooler temperature (AI1) |  | 29.0021 | 28.9869 | 29.0149 | 29.0102 | 28.8169 | 28.7461 | 21.38 | 21.375 | 21.1908 | 21.3214 | 21.3547 | 21.3058 | 21.2804 | 21.1561 | 21.0461 | 17.2186 | 17.1122 | 17.0143 | 17.2088 | 17.2278 | 17.079 | 19.313 | 19.3444 | 19.2727 | 19.5562 | 19.5731 | 19.5359 | 19.641 | 19.6704 | 19.6941 | 27.3652 | 27.2356 | 27.238 | 26.8615 | 26.9966 | 26.8959 | 26.6132 | 34.1279 | 34.0904 | 34.1235 | 34.0809 | 34.1036 | 33.9928 | 33.9812 | 34.0222 | 34.4804 | 34.3391 | 34.4312 | 33.0054 | 32.8919 | 32.7878 | 32.5998 | 32.3773 | 32.1706 | 34.3243 | 34.448 | 34.3434 | 25.8604 | 26.0478 | 25.8512 | 25.5922 | 25.5837 | 25.4993 | 19.3921 | 19.3127 | 19.2213 | 16.2609 | 16.3237 | 16.4641 | 16.7296 | 16.4696 | 27.0216 | 26.8224 | 26.9503 | 18.9743 | 19.0189 | 18.9786 | 18.7989 | 18.5951 | 18.595 | 18.5008 | 17.9245 | 17.9224 | 17.8117 | 14.3898 | 14.334 | 14.3407 | 14.4527 | 32.2101 | 32.4764 | 32.144 | 32.5293 | 31.4977 | 31.3917 | 31.6605 | 30.8659 | 31.3142 | 30.666 | 35.0574 | 35.1961 | 34.9777 | 34.8514 | 34.4416 | 34.624 | 34.4875 | 34.1503 | 35.3256 | 35.5907 | 35.7076 | 34.4023 | 34.1469 | 34.2401 | 33.8044 | 33.8787 | 34.0404 | 35.5448 | 35.5852 | 35.1979 | 19.8947 | 19.7594 | 19.6051 | 36.6178 | 36.3798 | 36.359 | 34.0754 | 33.9537 | 33.7652 | 34.7419 | 34.6066 | 34.736 | 35.5194 | 35.5097 | 35.4311 | 20.0211 | 19.9949 | 19.9039 | 22.063 | 21.8672 | 21.9719 | 21.9546 | 21.8406 | 21.8592 | 18.8304 | 18.8767 | 18.8597 | 19.0283 | 19.0492 | 18.9425 | 30.0631 | 29.7971 | 29.9067 | 29.4712 | 29.3586 | 29.3106 | 37.4451 | 37.1653 | 37.0418 | 35.7082 | 35.69 | 35.5846 | 34.673 | 34.7085 | 34.6919 | 37.3191 | 37.2599 | 37.2178 | 21.3508 | 21.2377 | 21.0307 | 35.9837 | 35.9584 | 35.9104 | 36.6502 | 37.0727 | 37.0964 | 25.3512 | 25.3718 | 25.4129 | 19.4012 | 19.3732 | 19.3277 | 19.2996 | 19.3307 | 19.3196 | 19.2128 | 19.0668 | 18.8917 | 22.5512 | 22.4514 | 22.2631 | 22.7403 | 22.6424 | 22.6483 | 31.6999 | 31.6159 | 31.2395 | 30.8532 | 30.7128 | 30.6204 | 39.4681 | 39.2231 | 39.2775 | 39.2256 | 39.171 | 39.2278 | 37.4068 | 37.0862 | 37.544 | 37.1761 | 37.1323 | 37.2393 | 38.0098 | 37.9609 | 38.0288 | 37.9533 | 38.3937 | 38.1908 | 38.6797 | 38.6428 | 38.3668 | 21.8786 | 21.848 | 21.9644 | 22.0188 | 21.972 | 21.8369
298 | c_Suction Flowmeter Pressure Low Duty (AI2) |  | 3.0727 | 3.06 | 3.0603 | 3.0945 | 3.0878 | 3.0809 | 3.2053 | 3.2166 | 3.21 | 3.1886 | 3.2126 | 3.212 | 3.2155 | 3.2064 | 3.2007 | 3.2369 | 3.2348 | 3.2174 | 3.2337 | 3.2385 | 3.2305 | 3.2028 | 3.212 | 3.2094 | 3.1978 | 3.2001 | 3.2076 | 3.2092 | 3.2036 | 3.2157 | 3.0763 | 3.068 | 3.0585 | 3.0754 | 3.0792 | 3.0739 | 3.0786 | 3.0073 | 3.0076 | 3.0086 | 3.0084 | 3.0111 | 3.0141 | 3.0183 | 3.0171 | 2.745 | 2.7292 | 2.729 | 3.07 | 3.0767 | 3.0753 | 3.0782 | 3.0729 | 3.0808 | 2.7598 | 2.7619 | 2.7587 | 3.0688 | 3.0675 | 3.062 | 3.0756 | 3.0748 | 3.0696 | 3.2071 | 3.2113 | 3.2084 | 3.2148 | 3.2181 | 3.234 | 3.2416 | 3.2224 | 3.0962 | 3.095 | 3.1043 | 3.2137 | 3.2166 | 3.2115 | 3.2218 | 3.218 | 3.2217 | 3.2207 | 2.9934 | 2.9848 | 2.9987 | 3.2065 | 3.2435 | 3.2371 | 3.2397 | 2.9956 | 3.0077 | 3.0161 | 3.0026 | 3.0773 | 3.0921 | 3.0974 | 3.0677 | 3.0686 | 3.097 | 3.0909 | 3.0972 | 3.0816 | 3.0806 | 3.0901 | 3.0977 | 3.0893 | 3.0904 | 2.7885 | 2.7941 | 2.7919 | 3.1262 | 3.1142 | 3.1206 | 3.1139 | 3.1093 | 3.1122 | 3.0545 | 3.0412 | 3.0547 | 3.2157 | 3.2148 | 3.1985 | 2.7886 | 2.7911 | 2.7915 | 3.1299 | 3.1183 | 3.1119 | 3.1123 | 3.1244 | 3.1301 | 3.0591 | 3.0508 | 3.0517 | 3.2046 | 3.2148 | 3.2056 | 3.2086 | 3.2045 | 3.1996 | 3.2031 | 3.1967 | 3.1979 | 3.2167 | 3.2171 | 3.2349 | 3.2104 | 3.2193 | 3.2139 | 3.0679 | 3.0746 | 3.0698 | 3.1023 | 3.1049 | 3.1068 | 2.7722 | 2.7688 | 2.7681 | 3.1068 | 3.1079 | 3.0905 | 3.0999 | 3.1032 | 3.0962 | 3.0614 | 3.0466 | 3.0483 | 3.2016 | 3.1953 | 3.207 | 3.108 | 3.1059 | 3.1008 | 3.1078 | 3.1133 | 3.1087 | 3.2153 | 3.2055 | 3.2058 | 3.1966 | 3.1956 | 3.1944 | 3.2238 | 3.1449 | 3.1434 | 3.1619 | 3.1577 | 3.1501 | 3.2087 | 3.2057 | 3.1927 | 3.1884 | 3.1755 | 3.1775 | 3.0715 | 3.0752 | 3.0686 | 3.1018 | 3.0899 | 3.0896 | 2.7595 | 2.7739 | 2.7777 | 2.7819 | 2.7778 | 2.7675 | 3.1078 | 3.0993 | 3.1086 | 3.1035 | 3.0965 | 3.1106 | 3.0995 | 3.0931 | 3.0977 | 3.0901 | 3.0971 | 3.097 | 3.042 | 3.0213 | 3.0368 | 3.2172 | 3.2029 | 3.21 | 3.2226 | 3.2139 | 3.2164
299 | d_subcooler pressure (AI3) |  | 9.0002 | 8.9912 | 8.9998 | 8.9588 | 8.9705 | 8.945 | 6.8293 | 6.8588 | 6.8315 | 6.8095 | 6.8421 | 6.8413 | 6.8431 | 6.8356 | 6.8237 | 5.7206 | 5.7275 | 5.6903 | 5.6971 | 5.711 | 5.6866 | 6.8125 | 6.8522 | 6.8078 | 6.7626 | 6.77 | 6.7819 | 6.7988 | 6.8022 | 6.8017 | 9.0113 | 8.9963 | 8.9771 | 8.9626 | 8.9822 | 8.9664 | 8.9854 | 11.4843 | 11.494 | 11.498 | 11.4855 | 11.4912 | 11.4775 | 11.4744 | 11.4901 | 11.8758 | 11.8536 | 11.8333 | 11.4984 | 11.4629 | 11.431 | 11.3023 | 11.2416 | 11.2163 | 11.8745 | 11.9031 | 11.8864 | 9.0023 | 9.0112 | 9.0542 | 9.0087 | 9.0116 | 8.9993 | 6.8374 | 6.8495 | 6.844 | 5.712 | 5.7267 | 5.7522 | 5.7803 | 5.7265 | 8.9801 | 8.9797 | 8.9886 | 6.8241 | 6.8348 | 6.8364 | 6.8536 | 6.8437 | 6.8274 | 6.827 | 6.7996 | 6.8156 | 6.8082 | 5.7817 | 5.7942 | 5.7731 | 5.7527 | 11.4817 | 11.5341 | 11.5583 | 11.5418 | 11.5023 | 11.4757 | 11.4747 | 11.3068 | 11.3099 | 11.3014 | 11.4212 | 11.4423 | 11.4114 | 11.4291 | 11.3004 | 11.3327 | 11.293 | 11.2133 | 11.7399 | 11.7918 | 11.7959 | 11.3982 | 11.3621 | 11.3688 | 11.1791 | 11.1387 | 11.165 | 11.5077 | 11.4343 | 11.4395 | 6.8513 | 6.8671 | 6.8044 | 11.846 | 11.8669 | 11.8384 | 11.2524 | 11.2022 | 11.2043 | 11.4026 | 11.381 | 11.3853 | 11.4312 | 11.4322 | 11.4122 | 6.8499 | 6.8611 | 6.8051 | 6.853 | 6.8037 | 6.8398 | 6.8245 | 6.805 | 6.7943 | 5.7221 | 5.7085 | 5.7126 | 5.7464 | 5.7349 | 5.7088 | 9.0045 | 8.9505 | 8.9488 | 8.95 | 8.967 | 8.9314 | 11.8867 | 11.844 | 11.8593 | 11.4539 | 11.4566 | 11.4067 | 11.2584 | 11.1924 | 11.2158 | 11.5392 | 11.4829 | 11.4669 | 6.7814 | 6.8403 | 6.7769 | 11.2346 | 11.2337 | 11.2237 | 11.4266 | 11.4815 | 11.5007 | 6.8022 | 6.7892 | 6.7891 | 5.7301 | 5.7313 | 5.7166 | 5.6936 | 5.7215 | 5.7234 | 5.7157 | 5.6849 | 5.6502 | 6.817 | 6.81 | 6.7739 | 6.8356 | 6.7891 | 6.793 | 9.0169 | 9.0051 | 8.9438 | 8.9452 | 8.9441 | 8.9228 | 11.8621 | 11.7967 | 11.8092 | 11.8275 | 11.8145 | 11.7831 | 11.2102 | 11.1827 | 11.2397 | 11.1994 | 11.1623 | 11.1825 | 11.3823 | 11.3652 | 11.3827 | 11.4401 | 11.4552 | 11.4665 | 11.4776 | 11.5113 | 11.4684 | 6.7681 | 6.7595 | 6.7787 | 6.8031 | 6.7954 | 6.7653
300 | e_Suction Flow Low Duty (AI4) |  | 337.5 | 337.5 | 337.5 | 63.271 | 337.5 | 337.5 | 337.5 | 79.3762 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 62.6372 | 337.5 | 337.5 | 337.5 | 337.5 | 34.8992 | 63.7147 | 337.5 | 337.5 | 337.5 | 283.0505 | 337.5 | 63.5516 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 327.8145 | 61.6379 | 62.2928 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 279.7698 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 61.9268 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 62.8289 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 280.1211 | 337.5 | 53.2033 | 337.5 | 286.7679 | 337.5 | 337.5 | 337.5 | 337.5 | 62.6991 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 61.0153 | 337.5 | 337.5 | 337.5 | 62.0509 | 307.1505 | 337.5 | 337.5 | 62.5315 | 337.5 | 23.8928 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 63.0696 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 311.0876 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 57.5395 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 62.3779 | 62.5444 | 337.5 | 62.3906 | 337.5 | 337.5 | 337.5 | 61.4216 | 337.5 | 337.5 | 337.5 | 337.5 | 69.6895 | 337.5 | 63.3226 | 63.5784 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 41.2871 | 337.5 | 337.5 | 337.5 | 337.5 | 55.1762 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 178.8154 | 337.5 | 337.5 | 337.5 | 59.5524 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 31.9574 | 337.5 | 60.6035 | 337.5 | 337.5 | 337.5 | 46.8926 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 302.3039 | 337.5 | 50.415 | 337.5 | 337.5 | 337.5 | 45.4871
301 | f_Suction Flowmeter Pressure High Duty (AI5) |  | 3.7034 | 3.6923 | 3.6945 | 3.7203 | 3.714 | 3.7085 | 3.838 | 3.8489 | 3.8445 | 3.8266 | 3.8474 | 3.8475 | 3.8504 | 3.8402 | 3.8378 | 3.8766 | 3.8707 | 3.8579 | 3.8729 | 3.8773 | 3.8707 | 3.8401 | 3.8472 | 3.8453 | 3.8317 | 3.8354 | 3.8423 | 3.8442 | 3.84 | 3.8494 | 3.7088 | 3.6999 | 3.6933 | 3.7075 | 3.7073 | 3.705 | 3.7095 | 3.6166 | 3.6173 | 3.6182 | 3.6183 | 3.6219 | 3.6229 | 3.6276 | 3.626 | 3.3766 | 3.3696 | 3.3647 | 3.6655 | 3.6717 | 3.6681 | 3.6711 | 3.6699 | 3.6726 | 3.3914 | 3.3951 | 3.3922 | 3.7038 | 3.7028 | 3.6968 | 3.706 | 3.7068 | 3.7008 | 3.8443 | 3.8449 | 3.846 | 3.8561 | 3.8584 | 3.8732 | 3.8782 | 3.8653 | 3.7247 | 3.7226 | 3.7296 | 3.8468 | 3.8505 | 3.847 | 3.8552 | 3.8521 | 3.8563 | 3.8524 | 3.6494 | 3.6417 | 3.6543 | 3.8501 | 3.8812 | 3.8781 | 3.8795 | 3.6076 | 3.6189 | 3.6282 | 3.6153 | 3.6727 | 3.6845 | 3.6905 | 3.6679 | 3.6665 | 3.6912 | 3.6817 | 3.6906 | 3.6771 | 3.6759 | 3.6839 | 3.6895 | 3.6808 | 3.686 | 3.4138 | 3.416 | 3.4132 | 3.7119 | 3.6981 | 3.705 | 3.7002 | 3.6967 | 3.6994 | 3.6569 | 3.6451 | 3.6564 | 3.8468 | 3.8471 | 3.833 | 3.4136 | 3.4147 | 3.4154 | 3.7124 | 3.7009 | 3.6995 | 3.6977 | 3.7083 | 3.7157 | 3.6591 | 3.6511 | 3.6491 | 3.8374 | 3.8464 | 3.8401 | 3.8424 | 3.8403 | 3.8358 | 3.8416 | 3.8331 | 3.8347 | 3.8566 | 3.8593 | 3.8737 | 3.8539 | 3.8544 | 3.8526 | 3.6984 | 3.7057 | 3.704 | 3.7281 | 3.7293 | 3.728 | 3.3997 | 3.3977 | 3.395 | 3.6944 | 3.6901 | 3.6801 | 3.6926 | 3.6883 | 3.6831 | 3.6604 | 3.6516 | 3.6532 | 3.8359 | 3.8301 | 3.8405 | 3.6934 | 3.6947 | 3.687 | 3.693 | 3.7021 | 3.6962 | 3.8478 | 3.8382 | 3.8389 | 3.8417 | 3.8401 | 3.8399 | 3.8637 | 3.7947 | 3.7922 | 3.8103 | 3.8065 | 3.7971 | 3.8437 | 3.8405 | 3.8274 | 3.8249 | 3.8148 | 3.817 | 3.7051 | 3.7058 | 3.7009 | 3.7274 | 3.7179 | 3.7156 | 3.3919 | 3.3992 | 3.4037 | 3.4088 | 3.4047 | 3.3939 | 3.6978 | 3.694 | 3.6965 | 3.6924 | 3.6853 | 3.6995 | 3.6906 | 3.6826 | 3.686 | 3.6824 | 3.6849 | 3.6841 | 3.6469 | 3.6277 | 3.6387 | 3.8471 | 3.8369 | 3.8421 | 3.8539 | 3.8477 | 3.849
302 | g_Spare6 (AI6) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
303 | h_Suction Flow High Duty (AI7) |  | 708.5533 | 708.239 | 708.9824 | 753.3499 | 754.6669 | 753.9793 | 459.6092 | 459.1117 | 458.4765 | 402.5823 | 402.5339 | 405.1102 | 404.9291 | 403.8661 | 404.6599 | 179.8175 | 180.006 | 180.6444 | 192.8903 | 193.2239 | 196.0088 | 402.7638 | 402.2725 | 402.9232 | 432.2026 | 432.5648 | 432.9053 | 431.5543 | 433.2524 | 432.0915 | 717.0727 | 716.8703 | 717.2743 | 752.582 | 752.1472 | 750.0536 | 744.4851 | 1058.93 | 1061.3358 | 1060.2397 | 1059.7164 | 1057.6105 | 1057.1208 | 1059.3345 | 1060.6859 | 1120.7046 | 1122.7851 | 1125.4913 | 1126.2432 | 1125.8052 | 1122.9724 | 1128.7409 | 1127.6508 | 1125.5224 | 1094.5429 | 1094.4888 | 1094.2393 | 682.6334 | 679.5682 | 680.3845 | 695.7665 | 697.6081 | 696.4332 | 389.4074 | 389.6914 | 388.8562 | 163.5925 | 166.9995 | 155.5166 | 179.5908 | 180.9583 | 735.1244 | 734.6323 | 734.4339 | 421.724 | 421.0643 | 422.7079 | 422.476 | 444.7665 | 446.4117 | 445.5893 | 444.5517 | 445.6618 | 445.5565 | 175.3381 | 180.2559 | 176.42 | 182.0249 | 1032.9634 | 1033.6461 | 1034.0407 | 1036.3232 | 1100.9827 | 1103.1869 | 1101.1818 | 1107.5314 | 1112.7848 | 1109.5549 | 1106.4373 | 1107.5957 | 1107.953 | 1106.9884 | 1107.5945 | 1107.8572 | 1108.7734 | 1107.5527 | 1138.231 | 1138.4527 | 1142.0461 | 1141.9203 | 1141.2077 | 1141.1278 | 1145.9468 | 1145.4018 | 1146.4713 | 1066.1123 | 1071.2948 | 1069.3823 | 457.3374 | 457.0021 | 458.2307 | 1135.4609 | 1134.0225 | 1134.7348 | 1144.781 | 1140.8975 | 1140.9929 | 1147.2442 | 1141.9289 | 1147.5331 | 1068.0927 | 1069.1057 | 1069.6966 | 458.1127 | 459.1281 | 460.5906 | 432.0657 | 432.1927 | 432.6537 | 402.8876 | 402.368 | 402.4024 | 165.5452 | 166.7393 | 175.6701 | 189.3809 | 185.1499 | 186.6649 | 721.4893 | 722.4118 | 722.2458 | 763.2945 | 764.0845 | 765.0877 | 1133.5116 | 1132.8965 | 1126.0625 | 1134.0115 | 1136.7857 | 1137.393 | 1134.7679 | 1137.4385 | 1134.6126 | 1063.7015 | 1072.4233 | 1068.1636 | 455.8056 | 454.8754 | 455.8404 | 1141.5298 | 1139.8152 | 1139.1977 | 1141.3384 | 1142.9751 | 1143.4111 | 456.1142 | 453.9677 | 458.4884 | 186.2945 | 187.6422 | 189.594 | 174.9865 | 174.8234 | 175.5865 | 186.106 | 188.1258 | 189.2072 | 431.7579 | 431.3527 | 431.2683 | 400.6899 | 400.7723 | 400.0052 | 715.6684 | 710.2543 | 701.2182 | 765.1471 | 764.9557 | 764.682 | 1131.1487 | 1130.6586 | 1131.5999 | 1131.7888 | 1131.9556 | 1130.0768 | 1134.7434 | 1136.2509 | 1136.3222 | 1135.5056 | 1134.2828 | 1134.8401 | 1137.0787 | 1136.5509 | 1135.5334 | 1136.037 | 1137.9212 | 1135.7186 | 1063.9666 | 1063.7318 | 1064.1486 | 456.6768 | 458.1315 | 459.0695 | 456.3715 | 458.1036 | 457.2845
304 | i_Suction Orifice Meter Pressure (AI8) |  | 3.6758 | 3.6644 | 3.6705 | 3.6877 | 3.6863 | 3.6779 | 3.8293 | 3.8382 | 3.8343 | 3.8213 | 3.8409 | 3.8422 | 3.8433 | 3.8336 | 3.8282 | 3.8756 | 3.8735 | 3.856 | 3.8731 | 3.8784 | 3.8715 | 3.8344 | 3.8415 | 3.8397 | 3.8255 | 3.8266 | 3.8332 | 3.8361 | 3.8331 | 3.8404 | 3.6831 | 3.6728 | 3.6675 | 3.6826 | 3.6794 | 3.6735 | 3.6803 | 3.5481 | 3.5496 | 3.5505 | 3.5514 | 3.5526 | 3.5538 | 3.5599 | 3.5616 | 3.3022 | 3.2934 | 3.2919 | 3.5812 | 3.5881 | 3.5827 | 3.5863 | 3.5838 | 3.5866 | 3.3081 | 3.3152 | 3.3094 | 3.6831 | 3.6812 | 3.6711 | 3.6819 | 3.682 | 3.678 | 3.8382 | 3.8405 | 3.8411 | 3.8554 | 3.8625 | 3.8756 | 3.8783 | 3.8683 | 3.6928 | 3.688 | 3.6981 | 3.8405 | 3.8409 | 3.8385 | 3.8478 | 3.8444 | 3.849 | 3.8462 | 3.6404 | 3.6361 | 3.6467 | 3.8491 | 3.8824 | 3.8803 | 3.881 | 3.5336 | 3.5451 | 3.5526 | 3.5419 | 3.5812 | 3.5953 | 3.5991 | 3.5806 | 3.5825 | 3.6027 | 3.5932 | 3.5989 | 3.5887 | 3.5867 | 3.5919 | 3.598 | 3.5949 | 3.5978 | 3.3181 | 3.3226 | 3.3133 | 3.6081 | 3.5952 | 3.6013 | 3.5956 | 3.5958 | 3.599 | 3.5679 | 3.5541 | 3.567 | 3.8387 | 3.8398 | 3.8213 | 3.319 | 3.3222 | 3.3213 | 3.6086 | 3.599 | 3.598 | 3.5944 | 3.6047 | 3.6118 | 3.5723 | 3.5622 | 3.5611 | 3.832 | 3.8366 | 3.8303 | 3.837 | 3.8328 | 3.8283 | 3.8341 | 3.8272 | 3.8319 | 3.859 | 3.8605 | 3.8767 | 3.8528 | 3.8544 | 3.8517 | 3.6691 | 3.6747 | 3.6724 | 3.6921 | 3.6929 | 3.694 | 3.3126 | 3.306 | 3.3061 | 3.5963 | 3.5948 | 3.5821 | 3.5941 | 3.5918 | 3.5857 | 3.576 | 3.5635 | 3.5706 | 3.8283 | 3.8228 | 3.8324 | 3.5924 | 3.5943 | 3.5849 | 3.5937 | 3.6008 | 3.5953 | 3.8394 | 3.8303 | 3.8295 | 3.8425 | 3.8422 | 3.8425 | 3.8657 | 3.7945 | 3.7929 | 3.8127 | 3.8081 | 3.7995 | 3.8363 | 3.8331 | 3.8218 | 3.8187 | 3.8099 | 3.8116 | 3.6791 | 3.6785 | 3.6759 | 3.6959 | 3.6868 | 3.681 | 3.3031 | 3.3109 | 3.3146 | 3.3188 | 3.3176 | 3.3065 | 3.6044 | 3.5972 | 3.6006 | 3.5975 | 3.5878 | 3.6015 | 3.5933 | 3.5857 | 3.5894 | 3.5851 | 3.5889 | 3.5852 | 3.562 | 3.5474 | 3.5582 | 3.84 | 3.8297 | 3.8356 | 3.8454 | 3.8408 | 3.8402
305 | j_Differential pressure_keller (AI9) |  | 11.4237 | 11.2712 | 11.116 | 26.7362 | 26.8795 | 30.243 | 23.5601 | 23.8764 | 23.4327 | 19.4411 | 19.3321 | 19.5496 | 19.6763 | 19.4346 | 19.1448 | -41.1048 | -39.229 | -40.2851 | -33.653 | -32.236 | -31.7316 | -44.2682 | -44.1651 | -44.208 | -41.3113 | -42.2265 | -40.9873 | -41.7795 | -41.8862 | -41.4374 | -11.7218 | -13.2601 | -12.5922 | -7.4391 | -8.5503 | -7.8958 | -10.7588 | 46.1296 | 49.1754 | 51.2038 | 53.992 | 54.408 | 52.5981 | 50.9724 | 50.5157 | 53.2873 | 54.3793 | 55.519 | 74.1703 | 75.7378 | 73.8866 | 75.876 | 74.0134 | 74.2967 | 63.1563 | 56.5162 | 60.2441 | -12.1231 | -9.1849 | -11.2451 | -9.4513 | -9.2282 | -9.319 | -42.1316 | -42.0512 | -41.508 | -51.2782 | -51.2166 | -50.8276 | -51.2353 | -51.4977 | -5.309 | -4.9317 | -6.027 | -37.4659 | -37.391 | -38.116 | -37.6995 | -35.2035 | -35.1451 | -35.172 | -37.871 | -37.9693 | -38.9195 | -49.2944 | -51.4884 | -52.0011 | -52.2686 | 49.6988 | 50.0217 | 51.5566 | 47.7059 | 68.0981 | 66.9529 | 68.1724 | 66.6396 | 68.4361 | 68.0013 | 79.0247 | 80.1724 | 78.0239 | 77.3604 | 77.5338 | 79.1872 | 79.7761 | 78.6354 | 75.5917 | 77.6488 | 76.9624 | 107.0174 | 104.939 | 109.412 | 108.2745 | 104.9177 | 110.4504 | 87.8408 | 89.4283 | 89.2542 | 14.4046 | 14.8704 | 14.4734 | 73.0744 | 73.3379 | 72.7526 | 102.1218 | 99.8221 | 101.3964 | 82.0104 | 88.6669 | 95.2842 | 84.5304 | 83.3904 | 82.702 | 21.4992 | 21.0842 | 19.5993 | 13.0339 | 12.8718 | 14.2854 | 17.9867 | 17.6517 | 16.6618 | -37.5477 | -36.8685 | -36.8109 | -37.7457 | -37.7216 | -36.9524 | 45.8257 | 44.1498 | 46.2135 | 53.1608 | 53.6882 | 52.3774 | 58.6279 | 63.9108 | 74.0172 | 55.0864 | 57.583 | 60.4757 | 66.7685 | 67.5161 | 63.0096 | 107.6746 | 107.8072 | 106.0458 | -7.2758 | -9.8827 | -7.3511 | 65.0066 | 68.452 | 66.9939 | 74.8069 | 67.6929 | 68.6795 | 19.6965 | 20.2273 | 19.597 | -23.863 | -22.6561 | -24.6594 | -22.5132 | -25.3357 | -24.0705 | -22.3322 | -22.6661 | -23.9349 | 5.0029 | 4.7886 | 4.7424 | -4.6137 | -4.5518 | -3.2092 | 43.9792 | 42.7189 | 43.0675 | 54.1241 | 53.3242 | 54.1541 | 63.2194 | 62.7523 | 66.639 | 67.6049 | 69.7597 | 71.2977 | 67.211 | 68.8515 | 64.8009 | 77.1237 | 75.5617 | 78.8485 | 94.2393 | 91.5788 | 93.5336 | 96.0182 | 99.8525 | 100.218 | 88.8285 | 86.8009 | 86.9278 | 16.402 | 18.0979 | 17.6163 | 16.7469 | 18.0252 | 19.6965
306 | k_Suction Diff Pressure (AI10) |  | 79.8628 | 79.2624 | 79.6515 | 89.5666 | 89.0704 | 88.9981 | 31.0156 | 30.5822 | 30.9036 | 22.9183 | 22.818 | 23.0146 | 23.1846 | 23.0049 | 22.6776 | 1.6981 | 1.6955 | 1.8036 | 2.7025 | 2.6085 | 2.7387 | 23.3978 | 23.4844 | 23.4356 | 27.7894 | 27.7675 | 28.393 | 28.2084 | 27.9007 | 28.0143 | 81.7623 | 82.0445 | 81.8173 | 91.2603 | 89.7492 | 89.8254 | 86.746 | 179.0383 | 179.583 | 179.664 | 180.9687 | 179.2053 | 179.6663 | 179.2186 | 180.6522 | 191.7625 | 191.5935 | 191.1097 | 209.5718 | 209.675 | 211.0695 | 210.5388 | 210.2152 | 211.497 | 183.9637 | 184.935 | 184.1161 | 74.1054 | 74.3359 | 74.2546 | 75.61 | 75.6386 | 76.1941 | 21.5537 | 21.3326 | 21.1526 | 1.2244 | 1.4253 | 1.3989 | 1.7453 | 2.0865 | 86.2212 | 85.4827 | 85.6452 | 25.9342 | 26.4164 | 26.4108 | 26.4385 | 29.8578 | 29.7686 | 29.6787 | 27.3374 | 27.1385 | 27.5139 | 1.9117 | 1.8941 | 1.8606 | 1.8466 | 170.3776 | 171.9033 | 171.0744 | 171.6025 | 201.3058 | 202.6124 | 201.8391 | 200.2897 | 200.9652 | 201.5061 | 200.7868 | 201.8515 | 200.0367 | 200.6286 | 199.9383 | 201.6509 | 200.2157 | 201.3455 | 192.5661 | 192.1864 | 192.6156 | 214.0819 | 211.4244 | 211.8216 | 210.7527 | 211.1096 | 210.1364 | 179.8359 | 178.9393 | 181.5336 | 30.5956 | 30.5311 | 30.928 | 194.3187 | 194.8563 | 195.2655 | 215.2247 | 213.4955 | 214.481 | 213.8325 | 213.2737 | 213.851 | 182.0441 | 180.9149 | 180.9762 | 31.2741 | 31.0827 | 31.643 | 28.2064 | 27.6692 | 27.5663 | 23.5541 | 22.9075 | 23.2396 | 1.2654 | 1.2836 | 1.55 | 1.8736 | 2.0917 | 2.1546 | 82.7042 | 82.1155 | 81.4888 | 91.9118 | 92.3175 | 91.9847 | 194.9318 | 195.6006 | 196.4679 | 215.1084 | 216.1721 | 214.3456 | 214.4257 | 215.2081 | 214.3566 | 181.221 | 180.1475 | 181.7608 | 31.3086 | 30.9101 | 31.3611 | 213.419 | 212.7942 | 211.3186 | 212.3947 | 212.4331 | 212.7782 | 32.2349 | 31.8279 | 31.9432 | 2.0602 | 1.9208 | 1.9973 | 1.3927 | 1.2309 | 1.3608 | 1.9755 | 2.0032 | 1.9889 | 28.2178 | 27.7539 | 27.8916 | 23.4057 | 23.4288 | 23.137 | 81.4709 | 81.3406 | 79.1175 | 93.3887 | 93.1454 | 93.0689 | 197.4326 | 196.828 | 198.3573 | 198.6575 | 199.7505 | 198.4621 | 219.37 | 217.7167 | 217.2703 | 216.7777 | 216.7868 | 216.2337 | 217.453 | 216.0191 | 215.7277 | 216.4072 | 216.7406 | 215.8726 | 184.3014 | 184.1275 | 185.1108 | 31.7654 | 31.8817 | 32.1359 | 32.0572 | 31.9048 | 31.9735
307 | l_Spare (AI11) |  | -0.003964 | -0.004101 | -0.00406 | -0.004015 | -0.003903 | -0.003871 | -0.003902 | -0.004061 | -0.004073 | -0.003981 | -0.00408 | -0.003983 | -0.003647 | -0.003697 | -0.003797 | -0.002994 | -0.003814 | -0.003802 | -0.003855 | -0.003614 | -0.003618 | -0.003997 | -0.004024 | -0.004103 | -0.004089 | -0.004088 | -0.004075 | -0.0041 | -0.004095 | -0.004094 | -0.004049 | -0.003982 | -0.003946 | -0.004015 | -0.004097 | -0.003977 | -0.004006 | -0.003866 | -0.003883 | -0.003928 | -0.004047 | -0.004055 | -0.004141 | -0.00386 | -0.003867 | -0.003881 | -0.003756 | -0.003929 | -0.003617 | -0.003612 | -0.003509 | -0.003567 | -0.003456 | -0.003492 | -0.003926 | -0.004055 | -0.003996 | -0.003848 | -0.003888 | -0.003694 | -0.003799 | -0.003816 | -0.003851 | -0.003693 | -0.003756 | -0.003719 | -0.00363 | -0.003548 | -0.003597 | -0.003629 | -0.003566 | -0.00408 | -0.003829 | -0.004061 | -0.003951 | -0.003765 | -0.003781 | -0.003735 | -0.003795 | -0.00378 | -0.003838 | -0.003707 | -0.003752 | -0.003824 | -0.003608 | -0.003602 | -0.003634 | -0.003554 | -0.003822 | -0.00383 | -0.003744 | -0.003837 | -0.003792 | -0.003814 | -0.003814 | -0.003721 | -0.003794 | -0.003723 | -0.004021 | -0.00405 | -0.003947 | -0.003973 | -0.003955 | -0.004024 | -0.004003 | -0.004008 | -0.003798 | -0.003946 | -0.003973 | -0.003882 | -0.00386 | -0.003891 | -0.003911 | -0.003874 | -0.003747 | -0.003879 | -0.003868 | -0.003896 | -0.003598 | -0.003583 | -0.00359 | -0.003945 | -0.003954 | -0.00393 | -0.003865 | -0.003909 | -0.003793 | -0.003898 | -0.003821 | -0.003856 | -0.003925 | -0.003861 | -0.003746 | -0.00361 | -0.003639 | -0.003635 | -0.007724 | -0.007803 | -0.007699 | -0.007629 | -0.007555 | -0.007752 | -0.008664 | -0.008714 | -0.009337 | -0.008703 | -0.009099 | -0.009209 | -0.006575 | -0.006665 | -0.006587 | -0.006335 | -0.006317 | -0.0062 | -0.005584 | -0.005637 | -0.005542 | -0.00569 | -0.005617 | -0.005581 | -0.005621 | -0.005635 | -0.005471 | -0.005903 | -0.005926 | -0.005913 | -0.008688 | -0.008748 | -0.008667 | -0.004154 | -0.00401 | -0.00405 | -0.00409 | -0.004014 | -0.004035 | -0.003991 | -0.003866 | -0.003895 | -0.00409 | -0.003946 | -0.003943 | -0.003924 | -0.004056 | -0.003879 | -0.003944 | -0.003947 | -0.004053 | -0.003711 | -0.003814 | -0.003733 | -0.00389 | -0.004002 | -0.00384 | -0.003757 | -0.003752 | -0.0037 | -0.003599 | -0.003552 | -0.003609 | -0.004009 | -0.003989 | -0.004049 | -0.004019 | -0.00402 | -0.00391 | -0.004008 | -0.004052 | -0.003984 | -0.004041 | -0.003899 | -0.00401 | -0.003957 | -0.00396 | -0.004041 | -0.00393 | -0.003876 | -0.003954 | -0.003941 | -0.00391 | -0.003889 | -0.003745 | -0.003745 | -0.003765 | -0.003677 | -0.003625 | -0.003648
308 | m_Oil Injection Pressure (before filter)(PT-56) (AI12) |  | 0.2023 | 0.20286 | 0.18882 | 0.19436 | 0.19092 | 0.18632 | 0.1877 | 0.18411 | 0.19442 | 0.19046 | 0.17336 | 0.15967 | 0.19479 | 0.19555 | 0.18971 | 0.16849 | 0.17727 | 0.18103 | 0.16808 | 0.1577 | 0.16335 | 0.15315 | 0.14213 | 0.15508 | 0.1449 | 0.14949 | 0.14118 | 0.14707 | 0.13967 | 0.14259 | 0.13415 | 0.15307 | 0.13302 | 0.12947 | 0.13001 | 0.1331 | 0.11083 | 0.11745 | 0.1261 | 0.11123 | 0.10768 | 0.10355 | 0.10459 | 0.10917 | 0.095876 | 0.068488 | 0.071218 | 0.075196 | 0.059831 | 0.059339 | 0.060618 | 0.051594 | 0.053438 | 0.056411 | -0.10298 | -0.082212 | -0.090678 | -0.098338 | -0.086707 | -0.085145 | -0.086707 | -0.075327 | -0.083518 | -0.115 | -0.094807 | -0.10209 | -0.11255 | -0.096415 | -0.10069 | -0.11356 | -0.111 | -0.087397 | -0.08334 | -0.083984 | -0.092286 | -0.096926 | -0.097734 | -0.08086 | -0.087764 | -0.10328 | -0.097819 | -0.10725 | -0.094216 | -0.10587 | -0.11058 | -0.11956 | -0.10861 | -0.11071 | -0.094603 | -0.090645 | -0.096132 | -0.097622 | -0.096697 | -0.1006 | -0.094977 | -0.10831 | -0.10069 | -0.097412 | -0.12791 | -0.12852 | -0.12961 | -0.13175 | -0.1216 | -0.13736 | -0.13951 | -0.13365 | -0.38521 | -0.38726 | -0.38799 | -0.40874 | -0.40163 | -0.39662 | -0.40115 | -0.40261 | -0.40996 | -0.403 | -0.41595 | -0.40728 | -0.41641 | -0.41418 | -0.4122 | 0.30176 | 0.2975 | 0.30189 | 0.29643 | 0.28657 | 0.30058 | 0.27816 | 0.28326 | 0.28054 | 0.28498 | 0.27183 | 0.28771 | 0.25677 | 0.25645 | 0.2534 | 0.47929 | 0.48214 | 0.47097 | 0.47123 | 0.47949 | 0.47372 | 0.47567 | 0.47772 | 0.48204 | 0.49206 | 0.48324 | 0.47623 | 0.47267 | 0.4739 | 0.4738 | 0.46632 | 0.4696 | 0.46895 | 0.43638 | 0.43777 | 0.429 | 0.43478 | 0.42679 | 0.42176 | 0.41833 | 0.41834 | 0.41589 | 0.33645 | 0.348 | 0.34464 | 0.31292 | 0.30898 | 0.30428 | 0.60126 | 0.60389 | 0.60186 | 0.5757 | 0.57547 | 0.56846 | 3.0433 | 3.0381 | 3.0386 | 1.4333 | 1.4453 | 1.4376 | 1.4358 | 1.4364 | 1.4335 | 1.4417 | 1.434 | 1.4444 | 1.4324 | 1.4314 | 1.4374 | 1.4268 | 1.4262 | 1.4225 | 1.397 | 1.3992 | 1.3921 | 1.3924 | 1.3923 | 1.3883 | 1.353 | 1.3535 | 1.3501 | 1.3501 | 1.3422 | 1.3325 | 1.226 | 1.2178 | 1.219 | 1.2151 | 1.2072 | 1.2065 | 1.1945 | 1.2002 | 1.1875 | 1.1834 | 1.1888 | 1.1729 | 1.1684 | 1.1694 | 1.1706 | 1.1194 | 1.1172 | 1.1234 | 1.1046 | 1.0947 | 1.1017
309 | n_Oil Pressure Orifice Plate (AI13) |  | 9.3183 | 9.3199 | 9.3445 | 9.3019 | 9.301 | 9.2725 | 7.216 | 7.2369 | 7.2123 | 7.1232 | 7.16 | 7.1641 | 7.1869 | 7.1284 | 7.1155 | 6.0591 | 6.091 | 5.9969 | 6.0379 | 6.0713 | 6.0444 | 7.1988 | 7.2165 | 7.2055 | 7.19 | 7.1929 | 7.2011 | 7.1817 | 7.1734 | 7.2027 | 9.3912 | 9.375 | 9.3468 | 9.3258 | 9.3393 | 9.3237 | 9.3245 | 11.9587 | 11.9684 | 11.961 | 11.9669 | 11.9721 | 11.9583 | 11.9732 | 11.9466 | 12.2897 | 12.2486 | 12.2409 | 11.9885 | 11.9489 | 11.9303 | 11.7817 | 11.7267 | 11.7098 | 12.1866 | 12.2124 | 12.2007 | 9.3146 | 9.3206 | 9.3491 | 9.3206 | 9.3097 | 9.3111 | 7.1895 | 7.2235 | 7.2118 | 6.0582 | 6.0778 | 6.1045 | 6.1414 | 6.0871 | 9.2983 | 9.2854 | 9.3041 | 7.2123 | 7.2167 | 7.217 | 7.2509 | 7.2454 | 7.2304 | 7.2299 | 7.1726 | 7.1768 | 7.1773 | 6.1164 | 6.151 | 6.1303 | 6.1147 | 11.8324 | 11.8937 | 11.899 | 11.8873 | 11.9384 | 11.9145 | 11.9202 | 11.7155 | 11.7352 | 11.7295 | 11.8604 | 11.9015 | 11.8549 | 11.8499 | 11.7475 | 11.7714 | 11.743 | 11.6764 | 12.277 | 12.2994 | 12.2928 | 12.1001 | 12.0406 | 12.0488 | 11.8435 | 11.8319 | 11.8457 | 12.1085 | 11.9929 | 12.0488 | 7.3041 | 7.3014 | 7.2481 | 12.3134 | 12.3135 | 12.3073 | 11.8787 | 11.8316 | 11.8286 | 11.9783 | 12.0143 | 12.0002 | 11.9493 | 11.9136 | 11.9159 | 7.2721 | 7.2857 | 7.2336 | 7.3271 | 7.2878 | 7.3099 | 7.2825 | 7.2532 | 7.2723 | 6.0896 | 6.0728 | 6.0826 | 6.0747 | 6.0996 | 6.0931 | 9.4154 | 9.3801 | 9.3635 | 9.3821 | 9.3853 | 9.3677 | 12.3645 | 12.3444 | 12.3527 | 12.0865 | 12.0646 | 12.0312 | 11.8916 | 11.831 | 11.8508 | 12.0449 | 11.9631 | 11.9596 | 7.2617 | 7.3213 | 7.2671 | 11.7661 | 11.7669 | 11.7642 | 11.9501 | 11.9887 | 12.0024 | 7.2323 | 7.2154 | 7.2298 | 6.1234 | 6.1128 | 6.1113 | 6.0862 | 6.1048 | 6.1085 | 6.1088 | 6.078 | 6.0508 | 7.2746 | 7.2528 | 7.2362 | 7.2752 | 7.2493 | 7.2562 | 9.3865 | 9.3796 | 9.3166 | 9.358 | 9.3371 | 9.3197 | 12.2848 | 12.229 | 12.2283 | 12.2625 | 12.2511 | 12.2168 | 11.7938 | 11.7695 | 11.8029 | 11.7662 | 11.7482 | 11.7766 | 11.9592 | 11.9261 | 11.9481 | 11.9948 | 12.0266 | 12.0104 | 11.9196 | 11.9657 | 11.9248 | 7.2307 | 7.2295 | 7.242 | 7.2597 | 7.2432 | 7.2318
310 | o_Oil Temperature Orifice Plate (AI14) |  | 31.7175 | 31.8898 | 31.898 | 30.4307 | 30.1481 | 30.0147 | 24.8227 | 24.7174 | 24.3974 | 23.3593 | 23.0792 | 22.7127 | 22.251 | 22.0818 | 22.005 | 19.4261 | 19.5224 | 19.6483 | 18.59 | 18.1689 | 17.5883 | 26.1989 | 26.0528 | 25.8626 | 26.2855 | 26.4289 | 26.5404 | 26.657 | 26.7897 | 27.0011 | 33.3966 | 33.4712 | 33.4535 | 32.9174 | 32.8211 | 32.6756 | 37.2602 | 41.3436 | 41.3477 | 41.2798 | 40.9855 | 40.976 | 40.9601 | 40.6978 | 40.1321 | 36.1842 | 35.2439 | 34.6642 | 26.6952 | 25.6215 | 24.4677 | 21.4709 | 19.9685 | 18.9235 | 41.7329 | 41.6097 | 41.5205 | 32.3824 | 32.2807 | 32.2552 | 31.3883 | 31.2228 | 31.1445 | 24.9212 | 25.064 | 25.1768 | 16.5444 | 16.4665 | 16.4009 | 16.1617 | 16.1241 | 30.5172 | 30.4709 | 30.8901 | 24.9111 | 24.9004 | 24.893 | 24.5651 | 24.7244 | 24.6987 | 24.6131 | 23.3695 | 23.2757 | 23.0251 | 18.9694 | 18.8393 | 18.7843 | 18.8262 | 43.0611 | 43.0568 | 42.9161 | 42.9186 | 43.1771 | 43.3292 | 43.3649 | 43.3368 | 42.8804 | 41.2072 | 36.5552 | 36.3188 | 35.7905 | 35.438 | 34.4068 | 33.7584 | 33.1812 | 32.4522 | 41.4939 | 41.2797 | 40.9057 | 38.6219 | 38.6503 | 38.6909 | 38.6359 | 38.4659 | 38.206 | 34.4619 | 33.2104 | 32.5343 | 18.0675 | 17.9035 | 17.738 | 36.3144 | 35.6583 | 35.0687 | 30.0558 | 29.2215 | 28.3415 | 22.3259 | 21.3972 | 20.8953 | 19.6278 | 18.9572 | 18.5365 | 14.9461 | 14.8862 | 14.8184 | 22.6244 | 22.443 | 22.7439 | 20.505 | 20.2009 | 19.8564 | 19.7192 | 19.7019 | 19.6793 | 19.5719 | 19.5581 | 19.5728 | 30.8866 | 30.818 | 30.7885 | 30.2571 | 30.4709 | 30.2027 | 40.8035 | 40.2832 | 40.2979 | 38.1685 | 37.8408 | 37.385 | 36.5859 | 36.095 | 35.3836 | 29.3898 | 28.8142 | 27.8532 | 16.9053 | 16.8412 | 16.8044 | 39.3221 | 39.1511 | 38.9259 | 37.5414 | 36.5293 | 35.4607 | 17.2559 | 17.1959 | 17.1106 | 21.8564 | 21.865 | 21.9015 | 21.9321 | 21.9093 | 21.8952 | 21.8224 | 21.737 | 21.6601 | 22.3665 | 22.1738 | 21.7896 | 25.669 | 25.6817 | 25.6991 | 28.5533 | 28.2263 | 27.7281 | 25.2304 | 24.4599 | 23.9154 | 42.0782 | 41.9855 | 41.899 | 41.0498 | 40.7095 | 39.7962 | 40.2775 | 40.3258 | 40.3212 | 40.6234 | 40.6384 | 40.4532 | 39.8324 | 39.6299 | 39.3119 | 38.8758 | 38.7321 | 38.2855 | 34.7077 | 33.9007 | 33.1879 | 17.2199 | 17.1337 | 17.0577 | 16.8681 | 16.7465 | 16.6563
311 | p_pressure differential meter (not here yet) (AI15) |  | -0.5 | -0.5 | -0.50001 | -0.50001 | -0.50001 | -0.5 | -0.49999 | -0.50001 | -0.5 | -0.50001 | -0.5 | -0.5 | -0.5 | -0.5 | -0.50001 | -0.5 | -0.50001 | -0.5 | -0.5 | -0.5 | -0.5 | -0.50001 | -0.50001 | -0.5 | -0.50001 | -0.49999 | -0.50001 | -0.5 | -0.50001 | -0.5 | -0.5 | -0.5 | -0.50001 | -0.49999 | -0.5 | -0.50001 | -0.50001 | -0.50001 | -0.5 | -0.5 | -0.50001 | -0.50001 | -0.5 | -0.5 | -0.50001 | -0.50001 | -0.5 | -0.50001 | -0.5 | -0.50001 | -0.5 | -0.50001 | -0.50001 | -0.50001 | -0.5 | -0.5 | -0.50001 | -0.5 | -0.5 | -0.5 | -0.5 | -0.5 | -0.5 | -0.50001 | -0.5 | -0.5 | -0.5 | -0.50001 | -0.50001 | -0.50001 | -0.50001 | -0.50001 | -0.50001 | -0.5 | -0.50001 | -0.50001 | -0.5 | -0.5 | -0.5 | -0.50001 | -0.49999 | -0.5 | -0.5 | -0.50001 | -0.50001 | -0.50001 | -0.5 | -0.50001 | -0.5 | -0.50001 | -0.5 | -0.49999 | -0.50001 | -0.5 | -0.50001 | -0.5 | -0.50001 | -0.5 | -0.5 | -0.50001 | -0.49999 | -0.5 | -0.50001 | -0.5 | -0.5 | -0.5 | -0.5 | -0.5 | -0.50001 | -0.49999 | -0.5 | -0.50001 | -0.50001 | -0.5 | -0.5 | -0.5 | -0.50001 | -0.5 | -0.49999 | -0.50001 | -0.50001 | -0.50001 | -0.5 | -0.5 | -0.50001 | -0.49999 | -0.50001 | -0.50001 | -0.5 | -0.5 | -0.50001 | -0.5 | -0.50002 | -0.50001 | -0.5 | -0.50001 | -0.5 | -0.5 | -0.5 | -0.5 | -0.50002 | -0.5 | -0.5 | -0.5 | -0.5 | -0.49999 | -0.50001 | -0.5 | -0.5 | -0.50001 | -0.50001 | -0.5 | -0.5 | -0.50001 | -0.49999 | -0.50001 | -0.5 | -0.5 | -0.5 | -0.5 | -0.49999 | -0.5 | -0.50001 | -0.5 | -0.50001 | -0.50001 | -0.50001 | -0.50001 | -0.50001 | -0.50001 | -0.5 | -0.5 | -0.5 | -0.5 | -0.50001 | -0.5 | -0.5 | -0.50001 | -0.50001 | -0.50001 | -0.5 | -0.5 | -0.50002 | -0.50001 | -0.5 | -0.5 | -0.50001 | -0.5 | -0.50001 | -0.5 | -0.5 | -0.50001 | -0.5 | -0.50001 | -0.5 | -0.50001 | -0.50001 | -0.50001 | -0.50001 | -0.50001 | -0.5 | -0.5 | -0.5 | -0.5 | -0.50001 | -0.5 | -0.5 | -0.5 | -0.5 | -0.50001 | -0.49999 | -0.5 | -0.5 | -0.5 | -0.5 | -0.5 | -0.50001 | -0.5 | -0.50001 | -0.5 | -0.50001 | -0.50002 | -0.5 | -0.5 | -0.5 | -0.49999
312 | a_Economiser Temp at Comp (AI0) |  | 23.1507 | 23.0822 | 23.0314 | 22.6296 | 22.5849 | 22.537 | 21.5798 | 21.5382 | 21.4427 | 21.2781 | 21.225 | 21.1688 | 21.0591 | 20.9891 | 20.9295 | 20.0619 | 20.0102 | 19.9554 | 19.0473 | 18.7823 | 18.5746 | 22.5989 | 22.592 | 22.5856 | 22.5851 | 22.5704 | 22.5848 | 22.6203 | 22.6256 | 22.6394 | 22.9762 | 22.9477 | 22.9516 | 22.8491 | 22.8037 | 22.8399 | 22.9652 | 22.8799 | 22.8507 | 22.8429 | 22.7172 | 22.6382 | 22.5915 | 22.5228 | 22.4003 | 21.0526 | 20.9714 | 20.8422 | 20.0663 | 19.939 | 19.8323 | 19.5084 | 19.2777 | 19.1276 | 21.8241 | 21.7414 | 21.6717 | 20.7673 | 20.7147 | 20.6736 | 20.5433 | 20.5384 | 20.5088 | 19.4722 | 19.3873 | 19.3536 | 17.6604 | 17.5894 | 17.5609 | 17.3494 | 17.2473 | 21.2418 | 21.231 | 21.199 | 19.9991 | 19.9789 | 19.937 | 19.643 | 19.5493 | 19.5242 | 19.5208 | 19.0131 | 18.9861 | 18.9567 | 17.6915 | 17.5855 | 17.5831 | 17.5389 | 24.9401 | 24.8996 | 24.9012 | 24.8546 | 24.6722 | 24.6053 | 24.5658 | 24.0188 | 23.912 | 23.5293 | 23.4345 | 23.3864 | 23.3561 | 23.3411 | 23.2462 | 23.1835 | 23.1491 | 23.0527 | 21.7648 | 21.674 | 21.6298 | 21.111 | 21.0415 | 20.9985 | 20.8925 | 20.8325 | 20.7531 | 20.3791 | 20.2051 | 20.0522 | 18.3873 | 18.2884 | 18.2317 | 21.7326 | 21.6181 | 21.5173 | 21.0421 | 20.9607 | 20.882 | 19.942 | 19.887 | 19.8199 | 19.6187 | 19.536 | 19.4589 | 16.7604 | 16.6981 | 16.6225 | 18.2066 | 18.0843 | 18.0152 | 17.3168 | 17.2251 | 17.104 | 19.3907 | 19.3829 | 19.4077 | 19.353 | 19.3431 | 19.3408 | 20.2704 | 20.2346 | 20.2482 | 19.8033 | 19.7573 | 19.7239 | 21.517 | 21.3045 | 21.12 | 20.798 | 20.6835 | 20.5372 | 20.2806 | 20.1086 | 19.9581 | 21.5806 | 21.4833 | 21.4326 | 19.787 | 19.6938 | 19.6292 | 21.7639 | 21.6537 | 21.5465 | 21.1886 | 21.0316 | 20.9139 | 20.3771 | 20.3161 | 20.2994 | 20.8031 | 20.8062 | 20.7471 | 20.8171 | 20.78 | 20.7574 | 20.7338 | 20.727 | 20.6975 | 20.4312 | 20.4336 | 20.3804 | 20.3029 | 20.2559 | 20.2711 | 19.4516 | 19.409 | 19.31 | 18.6886 | 18.5514 | 18.4786 | 22.8618 | 22.823 | 22.775 | 22.7056 | 22.67 | 22.5483 | 21.1121 | 21.1138 | 21.0166 | 20.9721 | 20.8944 | 20.8311 | 20.6277 | 20.5479 | 20.4465 | 20.304 | 20.2152 | 20.1339 | 19.8873 | 19.7832 | 19.736 | 18.0277 | 17.9877 | 18.0087 | 17.9228 | 17.8538 | 17.7851
313 | b_Spare1 (AI1) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
314 | c_Spare2 (AI2) |  | -9.9998 | -9.9999 | -9.9996 | -9.9998 | -9.9999 | -9.9998 | -9.9999 | -9.9999 | -9.9998 | -9.9997 | -9.9998 | -9.9998 | -9.9999 | -9.9997 | -9.9997 | -9.9998 | -9.9997 | -9.9997 | -9.9999 | -9.9997 | -9.9999 | -9.9997 | -9.9997 | -9.9998 | -9.9997 | -9.9996 | -9.9999 | -9.9997 | -10 | -9.9998 | -9.9998 | -9.9997 | -9.9999 | -9.9999 | -9.9999 | -9.9999 | -9.9998 | -10 | -9.9997 | -9.9999 | -9.9997 | -9.9997 | -9.9998 | -9.9999 | -9.9998 | -9.9998 | -9.9998 | -9.9998 | -9.9997 | -9.9998 | -9.9999 | -9.9998 | -10.0001 | -9.9998 | -9.9998 | -9.9998 | -10 | -9.9997 | -9.9998 | -9.9998 | -9.9999 | -9.9998 | -9.9998 | -10 | -9.9999 | -9.9998 | -9.9998 | -10.0001 | -9.9999 | -9.9998 | -9.9999 | -9.9996 | -9.9997 | -9.9997 | -9.9998 | -9.9999 | -9.9997 | -9.9996 | -9.9998 | -9.9998 | -10.0001 | -9.9997 | -9.9998 | -9.9997 | -9.9999 | -9.9997 | -9.9998 | -9.9998 | -9.9999 | -10 | -9.9997 | -9.9998 | -9.9996 | -9.9999 | -9.9998 | -9.9997 | -9.9998 | -9.9997 | -9.9998 | -9.9999 | -9.9998 | -9.9998 | -9.9999 | -9.9998 | -9.9998 | -10 | -10 | -9.9999 | -9.9998 | -9.9998 | -9.9998 | -9.9999 | -10 | -10 | -9.9999 | -9.9999 | -9.9998 | -9.9997 | -9.9998 | -9.9997 | -10 | -9.9999 | -9.9997 | -9.9999 | -9.9998 | -10 | -9.9998 | -9.9998 | -9.9999 | -9.9999 | -9.9997 | -9.9999 | -9.9998 | -9.9998 | -9.9999 | -9.9996 | -9.9999 | -9.9998 | -9.9998 | -9.9997 | -10 | -9.9997 | -9.9997 | -9.9997 | -10 | -9.9996 | -9.9998 | -9.9999 | -9.9997 | -9.9995 | -9.9999 | -9.9999 | -9.9997 | -10 | -9.9998 | -9.9998 | -9.9997 | -9.9998 | -9.9998 | -9.9999 | -9.9998 | -9.9997 | -9.9998 | -9.9999 | -9.9998 | -9.9998 | -9.9998 | -9.9997 | -9.9998 | -9.9998 | -9.9997 | -10.0001 | -10.0001 | -9.9997 | -9.9998 | -9.9998 | -9.9998 | -9.9999 | -9.9997 | -9.9998 | -9.9998 | -9.9999 | -9.9999 | -9.9997 | -9.9999 | -9.9998 | -9.9998 | -9.9998 | -9.9998 | -10 | -9.9997 | -9.9998 | -9.9998 | -9.9998 | -9.9999 | -9.9997 | -9.9999 | -9.9998 | -9.9999 | -9.9997 | -9.9998 | -9.9998 | -9.9997 | -10 | -9.9997 | -9.9998 | -9.9996 | -9.9996 | -9.9997 | -9.9998 | -9.9999 | -9.9997 | -9.9998 | -9.9999 | -9.9999 | -9.9998 | -9.9997 | -10 | -10 | -9.9997 | -9.9999 | -9.9998 | -9.9998 | -9.9998 | -9.9997 | -9.9997
315 | d_Economiser Flowmeter Pressure (AI3) |  | 7.3987 | 7.3728 | 7.3621 | 7.2829 | 7.2657 | 7.2618 | 7.0885 | 7.0812 | 7.0684 | 7.0478 | 7.038 | 7.0272 | 7.0084 | 6.9982 | 6.9897 | 6.8679 | 6.85 | 6.848 | 6.7473 | 6.7164 | 6.7132 | 7.3604 | 7.365 | 7.3608 | 7.3752 | 7.3774 | 7.3816 | 7.397 | 7.4019 | 7.3996 | 7.453 | 7.4581 | 7.4497 | 7.4268 | 7.4336 | 7.4394 | 7.4487 | 7.4235 | 7.4221 | 7.4199 | 7.3963 | 7.3907 | 7.3791 | 7.3677 | 7.3398 | 7.0745 | 7.0601 | 7.0301 | 6.8778 | 6.8631 | 6.841 | 6.7861 | 6.7562 | 6.7602 | 7.4586 | 7.4387 | 7.4301 | 7.2205 | 7.2101 | 7.2092 | 7.1564 | 7.1569 | 7.1468 | 6.9476 | 6.937 | 6.9344 | 6.7543 | 6.7489 | 6.739 | 6.7129 | 6.7045 | 7.2902 | 7.2815 | 7.2654 | 7.0752 | 7.0821 | 7.0727 | 7.0239 | 7.0105 | 7.0001 | 6.9979 | 6.8858 | 6.8826 | 6.8793 | 6.7531 | 6.7398 | 6.7385 | 6.7435 | 7.9831 | 7.9722 | 7.966 | 7.9634 | 7.8689 | 7.8536 | 7.8427 | 7.7352 | 7.7219 | 7.6659 | 7.8672 | 7.8566 | 7.8466 | 7.8466 | 7.8231 | 7.8053 | 7.7895 | 7.767 | 7.445 | 7.4311 | 7.4177 | 7.2924 | 7.2792 | 7.2588 | 7.2346 | 7.2181 | 7.2028 | 7.121 | 7.0849 | 7.0548 | 6.7305 | 6.7134 | 6.7123 | 7.4332 | 7.4099 | 7.3942 | 7.2865 | 7.2705 | 7.2619 | 7.1353 | 7.1196 | 7.1023 | 7.0614 | 7.0397 | 7.0129 | 6.5459 | 6.5369 | 6.521 | 6.8206 | 6.8111 | 6.7967 | 6.7396 | 6.7285 | 6.7126 | 7.053 | 7.0497 | 7.0493 | 7.0534 | 7.0483 | 7.0494 | 7.168 | 7.1566 | 7.1501 | 7.0592 | 7.0543 | 7.0381 | 7.4273 | 7.3741 | 7.3396 | 7.2563 | 7.2387 | 7.2069 | 7.1524 | 7.1207 | 7.0862 | 7.2778 | 7.264 | 7.2464 | 6.9069 | 6.8889 | 6.8819 | 7.4347 | 7.4143 | 7.3911 | 7.3323 | 7.3033 | 7.2807 | 7.148 | 7.136 | 7.1287 | 7.3244 | 7.3197 | 7.3183 | 7.3138 | 7.3161 | 7.3124 | 7.3085 | 7.3042 | 7.3001 | 7.2792 | 7.279 | 7.2704 | 7.2987 | 7.2956 | 7.2895 | 7.1464 | 7.1265 | 7.1105 | 6.9958 | 6.9776 | 6.9573 | 7.9367 | 7.9243 | 7.9089 | 7.8695 | 7.8594 | 7.8211 | 7.6301 | 7.62 | 7.6086 | 7.5908 | 7.5722 | 7.5621 | 7.5199 | 7.5076 | 7.4944 | 7.465 | 7.4584 | 7.437 | 7.388 | 7.3689 | 7.3495 | 7.0404 | 7.0332 | 7.0267 | 7.0051 | 6.9938 | 6.9876
316 | e_Economiser Flowmeter Temperature (AI4) |  | 20.1535 | 20.0278 | 19.9371 | 19.5368 | 19.47 | 19.3929 | 18.4614 | 18.4495 | 18.3912 | 18.23 | 18.1992 | 18.1358 | 18.0441 | 18.0096 | 17.9529 | 17.222 | 17.1901 | 17.1633 | 16.6275 | 16.5101 | 16.3762 | 19.8748 | 19.8541 | 19.9038 | 19.9711 | 20.0154 | 20.0184 | 20.1064 | 20.165 | 20.1863 | 20.5085 | 20.5206 | 20.496 | 20.4816 | 20.4876 | 20.4556 | 20.5798 | 20.4911 | 20.4617 | 20.4527 | 20.314 | 20.3134 | 20.2445 | 20.1679 | 20.0281 | 18.6473 | 18.5668 | 18.421 | 17.626 | 17.5138 | 17.3988 | 17.1151 | 16.9485 | 16.8119 | 20.4248 | 20.3386 | 20.2922 | 19.1581 | 19.1341 | 19.0917 | 18.8376 | 18.791 | 18.7583 | 17.6398 | 17.6151 | 17.574 | 16.454 | 16.4191 | 16.3969 | 16.249 | 16.2016 | 19.3667 | 19.3183 | 19.2715 | 18.293 | 18.2607 | 18.2461 | 18.0021 | 17.8893 | 17.8928 | 17.8683 | 17.2925 | 17.2638 | 17.2338 | 16.4118 | 16.3593 | 16.3619 | 16.3501 | 22.7509 | 22.6864 | 22.669 | 22.6609 | 22.259 | 22.1419 | 22.1063 | 21.5907 | 21.4975 | 21.2153 | 22.2312 | 22.1809 | 22.1396 | 22.0743 | 22.0051 | 21.9113 | 21.866 | 21.7742 | 20.3673 | 20.2953 | 20.2134 | 19.6299 | 19.558 | 19.4647 | 19.3563 | 19.2454 | 19.1962 | 18.7113 | 18.5413 | 18.3979 | 16.5204 | 16.4726 | 16.4283 | 20.0736 | 19.9616 | 19.8733 | 19.3902 | 19.3205 | 19.2398 | 18.6629 | 18.5668 | 18.5253 | 18.3186 | 18.1914 | 18.0475 | 15.3278 | 15.2785 | 15.1971 | 16.9871 | 16.9418 | 16.845 | 16.3478 | 16.2808 | 16.2235 | 17.9042 | 17.9047 | 17.9032 | 17.8792 | 17.8524 | 17.8293 | 18.7127 | 18.6337 | 18.6054 | 18.1197 | 18.0648 | 18.0132 | 19.8962 | 19.6397 | 19.476 | 19.0832 | 19.0016 | 18.8722 | 18.5714 | 18.4379 | 18.2552 | 19.1342 | 19.1011 | 18.9822 | 17.1027 | 17.045 | 16.9975 | 19.8261 | 19.7168 | 19.6358 | 19.3129 | 19.2028 | 19.0622 | 18.015 | 17.9474 | 17.8708 | 18.6462 | 18.638 | 18.6115 | 18.6008 | 18.601 | 18.5866 | 18.5635 | 18.5834 | 18.5627 | 18.4728 | 18.4249 | 18.4058 | 18.5879 | 18.5617 | 18.5726 | 17.9043 | 17.8052 | 17.7106 | 17.1186 | 17.0154 | 16.8996 | 21.1258 | 21.0824 | 21.0178 | 20.8657 | 20.7791 | 20.615 | 19.804 | 19.7397 | 19.6642 | 19.5748 | 19.4892 | 19.4362 | 19.2312 | 19.1669 | 19.1296 | 18.9947 | 18.9028 | 18.8255 | 18.5698 | 18.4644 | 18.372 | 16.6161 | 16.5755 | 16.5427 | 16.4501 | 16.391 | 16.3402
317 | f_Economiser Flow (AI5) |  | -0.025937 | -0.043148 | -0.031002 | -0.022691 | -0.036411 | -0.028543 | -0.029477 | -0.030018 | -0.008136 | -0.025593 | -0.025298 | -0.016643 | -0.028887 | -0.012808 | -0.012021 | -0.012168 | -0.040689 | -0.005235 | -0.012611 | -0.022937 | -0.003956 | -0.04541 | -0.021216 | -0.030412 | -0.047475 | -0.027412 | -0.035132 | -0.026035 | -0.033411 | -0.033805 | -0.033067 | -0.020429 | -0.043 | -0.031936 | -0.060654 | -0.03351 | -0.027166 | 30.7931 | 32.1068 | 29.751 | 41.5055 | 55.2093 | 43.9462 | 41.5772 | 39.9145 | -0.025396 | -0.027461 | -0.019594 | -0.021167 | -0.027068 | -0.012021 | -0.016496 | 0.008927 | -0.009169 | -0.024314 | -0.040247 | -0.038034 | -0.042902 | -0.01861 | -0.02633 | -0.035723 | -0.025347 | -0.016987 | -0.014627 | -0.006464 | -0.005874 | -0.002973 | 0.002338 | -0.005923 | -0.004497 | 0.003518 | -0.020479 | -0.025199 | -0.03705 | -0.004448 | -0.016545 | -0.022052 | -0.015955 | -0.028002 | -0.013496 | -0.018659 | -0.022888 | -0.021659 | -0.004596 | -0.004104 | -0.011529 | -0.009267 | -0.00848 | 35.002 | 29.0561 | 34.1746 | 30.6214 | -0.045016 | -0.039656 | -0.041427 | -0.031199 | -0.028789 | -0.038329 | -0.040148 | -0.047524 | -0.053769 | -0.035723 | -0.027855 | -0.059621 | -0.042509 | -0.023429 | -0.022691 | -0.033952 | -0.045016 | -0.010742 | -0.050868 | -0.024118 | -0.02515 | -0.036411 | -0.031641 | 29.5967 | 25.9915 | 29.7857 | 0.002043 | -0.012168 | -0.004104 | -0.043246 | -0.027215 | -0.03469 | -0.015512 | -0.017922 | 0.25583 | -0.023773 | -0.011234 | -0.027363 | 41.3327 | 41.3405 | 41.3113 | 0.006419 | -0.000612 | -0.008726 | -0.006267 | -0.00971 | -0.020577 | 0.008386 | 0.001404 | 0.004059 | -0.013889 | -0.00789 | -0.017135 | -0.027068 | -0.020036 | -0.004497 | -0.021413 | -0.02156 | -0.013791 | -0.009906 | -0.015414 | -0.027511 | -0.038919 | -0.013348 | -0.028543 | 1.1736 | 2.0966 | 1.7481 | -0.021511 | -0.005923 | -0.002924 | 38.8679 | 27.6776 | 27.6752 | -0.01802 | 0.004698 | -0.016004 | -0.029232 | -0.012562 | -0.021856 | -0.025347 | -0.02815 | -0.020184 | -0.014725 | 0.000617 | -0.012217 | -0.025642 | -0.021069 | -0.021167 | -0.005677 | -0.008579 | -0.015807 | -0.020479 | -0.016889 | -0.020872 | -0.02933 | -0.029822 | -0.014529 | -0.010939 | -0.014676 | -0.012808 | -0.01625 | -0.008136 | -0.018708 | 0.001797 | -0.008923 | -0.008284 | 3.3197 | 1.4097 | 1.7126 | -0.0192 | -0.024363 | -0.040689 | -0.01861 | -0.024413 | -0.023724 | -0.034985 | -0.029576 | -0.014775 | -0.033264 | -0.016102 | -0.023331 | -0.013152 | -0.026478 | -0.013398 | 41.3053 | 41.3224 | 41.3332 | 0.000666 | -0.00076 | -0.005579 | 0.002486 | -0.001793 | 0.009862
318 | g_Spare6 (AI6) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
319 | pressure at comp top cover (before rotor) |  | 2.5663 | 2.5535 | 2.5615 | 2.5624 | 2.5599 | 2.553 | 2.7924 | 2.7981 | 2.7965 | 2.7921 | 2.8135 | 2.8138 | 2.8133 | 2.8071 | 2.7995 | 2.8826 | 2.877 | 2.8674 | 2.8758 | 2.8756 | 2.8777 | 2.8013 | 2.8081 | 2.8069 | 2.7847 | 2.7887 | 2.7982 | 2.7956 | 2.795 | 2.8008 | 2.5724 | 2.5639 | 2.5509 | 2.551 | 2.5495 | 2.5497 | 2.5587 | 2.2834 | 2.2812 | 2.283 | 2.281 | 2.2845 | 2.2864 | 2.2885 | 2.2861 | 2.0118 | 2.002 | 2.0034 | 2.2626 | 2.2656 | 2.2611 | 2.2637 | 2.2603 | 2.2652 | 2.0374 | 2.0477 | 2.0431 | 2.6015 | 2.603 | 2.6012 | 2.606 | 2.6032 | 2.6004 | 2.8435 | 2.8438 | 2.8416 | 2.8902 | 2.8904 | 2.9056 | 2.9097 | 2.8973 | 2.5967 | 2.592 | 2.5985 | 2.8338 | 2.8372 | 2.8354 | 2.8458 | 2.8345 | 2.8394 | 2.8343 | 2.6353 | 2.6268 | 2.6373 | 2.8866 | 2.9164 | 2.9138 | 2.9129 | 2.2878 | 2.2982 | 2.3073 | 2.2966 | 2.2813 | 2.2944 | 2.3016 | 2.2973 | 2.2909 | 2.3095 | 2.2951 | 2.3026 | 2.2896 | 2.2866 | 2.2934 | 2.3023 | 2.2888 | 2.2971 | 2.0117 | 2.0162 | 2.0085 | 2.2691 | 2.2569 | 2.2631 | 2.2618 | 2.2571 | 2.2612 | 2.2817 | 2.2749 | 2.2839 | 2.8079 | 2.8026 | 2.7926 | 2.0191 | 2.0161 | 2.0158 | 2.2774 | 2.2689 | 2.2631 | 2.2635 | 2.2701 | 2.269 | 2.2945 | 2.2859 | 2.2855 | 2.7963 | 2.803 | 2.7985 | 2.8087 | 2.8131 | 2.8022 | 2.8143 | 2.8075 | 2.8057 | 2.8731 | 2.8699 | 2.8892 | 2.8687 | 2.8686 | 2.864 | 2.575 | 2.58 | 2.5772 | 2.5733 | 2.5751 | 2.5794 | 2.012 | 2.0033 | 2.0026 | 2.2619 | 2.2593 | 2.2523 | 2.2609 | 2.2602 | 2.2539 | 2.2962 | 2.2842 | 2.2907 | 2.789 | 2.7855 | 2.7891 | 2.256 | 2.2597 | 2.2525 | 2.2535 | 2.2625 | 2.2531 | 2.7974 | 2.7868 | 2.7907 | 2.8429 | 2.8397 | 2.8402 | 2.8646 | 2.7963 | 2.793 | 2.8099 | 2.8056 | 2.7969 | 2.8007 | 2.7988 | 2.7844 | 2.7824 | 2.7757 | 2.7785 | 2.5674 | 2.5666 | 2.5651 | 2.5566 | 2.55 | 2.5475 | 2.0085 | 2.0126 | 2.0166 | 2.0159 | 2.0138 | 2.0085 | 2.2727 | 2.2699 | 2.2701 | 2.2694 | 2.2633 | 2.2694 | 2.2636 | 2.2574 | 2.2639 | 2.2595 | 2.2637 | 2.2571 | 2.2929 | 2.2854 | 2.2888 | 2.8119 | 2.7993 | 2.8076 | 2.8174 | 2.8135 | 2.8112
320 | i_Liquid Injection Flow (AI8) |  | 0.52097 | 0.52228 | 0.51856 | 0.52383 | 0.51913 | 0.5219 | 0.52213 | 0.51969 | 0.52445 | 0.52287 | 0.52214 | 0.51881 | 0.52234 | 0.5214 | 0.52309 | 0.51901 | 0.52345 | 0.52259 | 0.52245 | 0.52425 | 2.1308 | 0.52363 | 0.52213 | 0.52231 | 0.51894 | 0.52252 | 0.52322 | 0.52084 | 0.52169 | 0.52331 | 0.52161 | 0.51954 | 0.52028 | 0.52225 | 0.51986 | 0.52168 | 0.52169 | 0.52185 | 0.51922 | 0.51902 | 0.52214 | 0.52263 | 0.52283 | 0.5233 | 0.52062 | 0.52139 | 0.52232 | 0.52261 | 0.52145 | 0.52158 | 0.52163 | 0.52302 | 0.52431 | 0.52138 | 0.52242 | 0.52038 | 0.5213 | 0.5199 | 0.52089 | 0.52049 | 0.52335 | 0.52231 | 0.52328 | 0.52227 | 0.5238 | 0.52209 | 0.52245 | 0.52199 | 0.52256 | 0.52208 | 0.51901 | 0.51943 | 0.52385 | 0.52362 | 0.52067 | 0.52138 | 0.52129 | 0.52197 | 0.52215 | 0.51988 | 0.52255 | 0.52247 | 0.52298 | 0.52265 | 0.5209 | 0.52151 | 0.52401 | 0.51914 | 0.5229 | 0.52214 | 0.5195 | 0.5228 | 0.5209 | 0.52272 | 0.5207 | 0.5215 | 0.52287 | 0.52322 | 0.52429 | 0.52376 | 0.52382 | 0.52088 | 0.52394 | 0.52282 | 0.52108 | 0.52184 | 0.52135 | 0.52159 | 0.51999 | 0.5222 | 0.52415 | 0.52191 | 0.52189 | 0.52089 | 0.5219 | 0.5234 | 0.52135 | 0.52375 | 0.5242 | 0.52244 | 0.52114 | 0.52244 | 0.51929 | 0.52193 | 0.52172 | 0.5215 | 0.52307 | 0.51997 | 0.52144 | 0.52251 | 0.52156 | 0.52188 | 0.52084 | 0.52181 | 0.52297 | 0.52365 | 0.52049 | 0.5225 | 0.52299 | 0.52258 | 0.52229 | 0.52073 | 0.52067 | 0.51994 | 0.52312 | 0.52106 | 0.52084 | 0.52164 | 0.5203 | 0.52059 | 0.52417 | 0.52014 | 0.52067 | 0.52106 | 0.52118 | 0.52294 | 0.52445 | 0.52109 | 0.52138 | 0.52066 | 0.52039 | 0.52342 | 0.52174 | 0.52093 | 0.52204 | 0.52173 | 0.52371 | 0.52104 | 0.52378 | 0.52293 | 0.5208 | 0.52315 | 0.52233 | 0.52189 | 0.52176 | 0.52182 | 0.52377 | 0.52039 | 1.9166 | 6.4393 | 6.4391 | 0.52208 | 0.52176 | 0.52326 | 6.4407 | 6.4416 | 6.4388 | 0.52054 | 0.51979 | 0.52168 | 0.5216 | 0.52299 | 0.52413 | 0.52087 | 0.52231 | 0.52196 | 0.52359 | 0.5225 | 0.52323 | 0.51941 | 0.52353 | 0.52047 | 0.52314 | 0.52314 | 0.52164 | 0.52298 | 0.52145 | 0.5209 | 0.52364 | 0.52272 | 0.52165 | 0.52056 | 0.52194 | 0.52029 | 0.5232 | 0.52376 | 0.51911 | 0.51975 | 0.52158 | 0.52164 | 0.52187 | 0.52159 | 0.51906 | 0.52146 | 0.52118 | 0.51986
321 | j_Liquid Injection Temperature (AI9) |  | 19.548 | 19.4774 | 19.3849 | 19.1152 | 19.0285 | 19.0063 | 18.2818 | 18.3 | 18.2472 | 18.1184 | 18.0892 | 18.0361 | 17.9758 | 17.9264 | 17.8939 | 17.3273 | 17.3199 | 17.2655 | 16.8168 | 16.7405 | 16.5886 | 19.3445 | 19.3337 | 19.3353 | 19.3593 | 19.3535 | 19.3783 | 19.4165 | 19.4233 | 19.4224 | 19.5129 | 19.5116 | 19.5024 | 19.4119 | 19.3997 | 19.4176 | 19.3965 | 19.2768 | 19.2536 | 19.2455 | 19.1201 | 19.1091 | 19.0841 | 19.0339 | 18.8962 | 17.8546 | 17.7969 | 17.7177 | 17.1293 | 17.0588 | 16.9646 | 16.7477 | 16.5877 | 16.519 | 19.4298 | 19.3557 | 19.3329 | 18.4754 | 18.4856 | 18.4406 | 18.2724 | 18.2217 | 18.2061 | 17.4242 | 17.3995 | 17.376 | 16.5334 | 16.5028 | 16.4883 | 16.3958 | 16.367 | 18.8189 | 18.7613 | 18.7005 | 17.9405 | 17.9163 | 17.9122 | 17.7416 | 17.6518 | 17.6321 | 17.5962 | 17.1716 | 17.1395 | 17.1223 | 16.4162 | 16.3613 | 16.3399 | 16.3208 | 21.7071 | 21.6477 | 21.6439 | 21.6178 | 21.2944 | 21.238 | 21.2058 | 20.8601 | 20.7562 | 20.5337 | 21.2526 | 21.2336 | 21.1573 | 21.1121 | 21.0328 | 20.9965 | 20.91 | 20.8537 | 19.2982 | 19.2382 | 19.1841 | 18.6755 | 18.6427 | 18.5464 | 18.4656 | 18.4145 | 18.3534 | 17.9906 | 17.8531 | 17.7346 | 16.3038 | 16.2771 | 16.256 | 18.9888 | 18.927 | 18.8385 | 18.47 | 18.3757 | 18.3022 | 17.6191 | 17.5737 | 17.4959 | 17.3445 | 17.2379 | 17.1583 | 15.1456 | 15.1224 | 15.0586 | 16.6793 | 16.6592 | 16.5676 | 16.2276 | 16.1804 | 16.1308 | 17.6817 | 17.667 | 17.6517 | 17.666 | 17.6471 | 17.6128 | 17.8378 | 17.8023 | 17.7745 | 17.4083 | 17.3497 | 17.2824 | 18.8091 | 18.6361 | 18.5005 | 18.2075 | 18.1209 | 18.0216 | 17.7946 | 17.6877 | 17.5445 | 18.3109 | 18.2849 | 18.2005 | 16.8673 | 16.8071 | 16.7826 | 18.641 | 18.577 | 18.5099 | 18.2821 | 18.1983 | 18.0989 | 17.8291 | 17.8039 | 17.7723 | 18.3026 | 18.2905 | 18.2761 | 18.2478 | 18.2318 | 18.2368 | 18.2385 | 18.2057 | 18.1899 | 18.0175 | 18.0208 | 17.9786 | 17.8771 | 17.8654 | 17.8386 | 17.1986 | 17.146 | 17.0623 | 16.6281 | 16.5301 | 16.4443 | 19.8269 | 19.7715 | 19.728 | 19.6083 | 19.5591 | 19.4079 | 18.4032 | 18.3363 | 18.2876 | 18.2237 | 18.1448 | 18.0764 | 17.956 | 17.9115 | 17.9098 | 17.7976 | 17.7432 | 17.7079 | 17.5549 | 17.5007 | 17.4381 | 16.3049 | 16.2943 | 16.2742 | 16.2031 | 16.1427 | 16.1053
322 | k_Liquid Injection Pressure (AI10) |  | 0.66541 | 0.66666 | 0.65939 | 0.65434 | 0.65288 | 0.65138 | 0.64465 | 0.64095 | 0.6444 | 0.64573 | 0.64272 | 0.64013 | 0.64441 | 0.64257 | 0.63712 | 0.629 | 0.62668 | 0.62829 | 0.62215 | 0.62122 | 0.61718 | 0.68048 | 0.67539 | 0.67638 | 0.67923 | 0.68253 | 0.67867 | 0.68378 | 0.68192 | 0.68112 | 0.67864 | 0.68477 | 0.68417 | 0.68616 | 0.67771 | 0.68128 | 0.67871 | 0.67422 | 0.67955 | 0.67338 | 0.66587 | 0.66765 | 0.67128 | 0.66751 | 0.66338 | 0.63861 | 0.6364 | 0.63332 | 0.62536 | 0.61914 | 0.62362 | 0.61897 | 0.61433 | 0.60978 | 0.71964 | 0.71339 | 0.71655 | 0.70986 | 0.70798 | 0.70022 | 0.69912 | 0.69809 | 0.7002 | 0.68293 | 0.68031 | 0.68284 | 0.66986 | 0.66697 | 0.66676 | 0.67237 | 0.66607 | 0.72009 | 0.71252 | 0.71676 | 0.70007 | 0.70353 | 0.71126 | 0.69808 | 0.69899 | 0.69761 | 0.69868 | 0.68955 | 0.68253 | 0.68931 | 0.6778 | 0.67889 | 0.67703 | 0.67695 | 0.7674 | 0.76904 | 0.76593 | 0.76363 | 0.75758 | 0.76062 | 0.75796 | 0.75003 | 0.74833 | 0.74553 | 0.77448 | 0.77266 | 0.77073 | 0.76993 | 0.77105 | 0.77024 | 0.76732 | 0.76384 | 0.7343 | 0.73534 | 0.73369 | 0.72457 | 0.72031 | 0.71991 | 0.71705 | 0.7158 | 0.71694 | 0.70905 | 0.70646 | 0.70394 | 0.68388 | 0.6797 | 0.68129 | 0.74978 | 0.74838 | 0.74863 | 0.73664 | 0.73629 | 0.73699 | 0.71903 | 0.72064 | 0.71927 | 0.7131 | 0.71483 | 0.70659 | 0.67238 | 0.6719 | 0.67139 | 0.71793 | 0.71874 | 0.71453 | 0.70924 | 0.70505 | 0.70547 | 0.74533 | 0.74413 | 0.74684 | 0.74984 | 0.7494 | 0.74507 | 0.74907 | 0.74542 | 0.74249 | 0.73807 | 0.73359 | 0.73253 | 0.76002 | 0.75344 | 0.75142 | 0.74485 | 0.74296 | 0.74326 | 0.73433 | 0.73147 | 0.73174 | 0.74757 | 0.74565 | 0.74816 | 0.71665 | 0.72242 | 0.72395 | 0.79707 | 0.792 | 0.7894 | 0.78716 | 0.78184 | 0.78705 | 0.78271 | 0.77826 | 0.77913 | 0.80002 | 0.80141 | 0.80114 | 0.80132 | 0.8029 | 0.80222 | 0.80534 | 0.80191 | 0.80249 | 0.79721 | 0.80081 | 0.79825 | 0.79848 | 0.79842 | 0.79695 | 0.7744 | 0.77589 | 0.77095 | 0.76771 | 0.76537 | 0.7653 | 0.84718 | 0.84815 | 0.8469 | 0.84282 | 0.84196 | 0.8406 | 0.82287 | 0.8234 | 0.82232 | 0.82149 | 0.81891 | 0.81987 | 0.81151 | 0.81452 | 0.81335 | 0.81078 | 0.80647 | 0.80791 | 0.80623 | 0.80484 | 0.80433 | 0.78279 | 0.77812 | 0.77909 | 0.77485 | 0.77653 | 0.7783
323 | l_Spare11 (AI11) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
324 | m_ spare12 (AI12) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
325 | n_Discharge Pressure (PT-53) (AI13) |  | 10.7394 | 10.715 | 10.7405 | 10.6993 | 10.719 | 10.6929 | 8.4618 | 8.4893 | 8.4636 | 8.4292 | 8.4677 | 8.4714 | 8.4773 | 8.4653 | 8.4388 | 7.2964 | 7.2976 | 7.2541 | 7.2574 | 7.285 | 7.2595 | 8.4489 | 8.4733 | 8.4528 | 8.435 | 8.4315 | 8.4407 | 8.4481 | 8.4501 | 8.4633 | 10.7535 | 10.7405 | 10.7212 | 10.7149 | 10.7299 | 10.7144 | 10.7206 | 13.3851 | 13.3886 | 13.3936 | 13.3867 | 13.3856 | 13.3864 | 13.3784 | 13.3776 | 13.745 | 13.7197 | 13.7147 | 13.4178 | 13.3795 | 13.3704 | 13.2181 | 13.1762 | 13.1516 | 13.7187 | 13.746 | 13.7199 | 10.7201 | 10.7179 | 10.7487 | 10.7184 | 10.7094 | 10.7013 | 8.4341 | 8.457 | 8.4502 | 7.2563 | 7.2664 | 7.2934 | 7.3274 | 7.271 | 10.7071 | 10.697 | 10.7165 | 8.4371 | 8.4414 | 8.4467 | 8.4713 | 8.4527 | 8.4438 | 8.4403 | 8.4262 | 8.4255 | 8.434 | 7.3284 | 7.3412 | 7.3145 | 7.2958 | 13.3169 | 13.3768 | 13.3935 | 13.3714 | 13.3907 | 13.3788 | 13.3652 | 13.1906 | 13.1972 | 13.2068 | 13.3664 | 13.389 | 13.3506 | 13.3523 | 13.2343 | 13.2717 | 13.2391 | 13.1672 | 13.7284 | 13.7237 | 13.7373 | 13.3937 | 13.3318 | 13.3524 | 13.1849 | 13.1481 | 13.1656 | 13.421 | 13.3407 | 13.3763 | 8.4878 | 8.4893 | 8.4299 | 13.7673 | 13.7713 | 13.7562 | 13.2264 | 13.1938 | 13.1836 | 13.3636 | 13.372 | 13.3756 | 13.3576 | 13.334 | 13.3241 | 8.4772 | 8.4949 | 8.4357 | 8.4877 | 8.451 | 8.4772 | 8.4476 | 8.4216 | 8.4372 | 7.2724 | 7.2728 | 7.2681 | 7.2915 | 7.2806 | 7.2693 | 10.7296 | 10.6876 | 10.683 | 10.7049 | 10.7139 | 10.6824 | 13.7816 | 13.7425 | 13.773 | 13.4206 | 13.421 | 13.3788 | 13.2315 | 13.1645 | 13.1949 | 13.4541 | 13.3976 | 13.362 | 8.4305 | 8.487 | 8.4393 | 13.2092 | 13.2131 | 13.2024 | 13.405 | 13.4526 | 13.4653 | 8.4564 | 8.4328 | 8.4492 | 7.3105 | 7.304 | 7.2915 | 7.2684 | 7.2899 | 7.2883 | 7.2852 | 7.2523 | 7.2289 | 8.4692 | 8.4563 | 8.4225 | 8.4682 | 8.4424 | 8.4431 | 10.7534 | 10.7388 | 10.6701 | 10.7201 | 10.7 | 10.6855 | 13.7548 | 13.6947 | 13.7058 | 13.7238 | 13.721 | 13.6836 | 13.1796 | 13.1356 | 13.1836 | 13.1569 | 13.1216 | 13.142 | 13.3403 | 13.3216 | 13.3353 | 13.4026 | 13.413 | 13.4123 | 13.3658 | 13.3976 | 13.3621 | 8.441 | 8.4216 | 8.4325 | 8.4581 | 8.4487 | 8.434
326 | o_LVDT (AI14) |  | -37.4319 | -37.4329 | -37.4326 | -37.432 | -37.4327 | -37.4326 | -37.4326 | -37.4331 | -37.4344 | -37.4323 | -37.4321 | -37.4333 | -37.4331 | -37.4328 | -37.4329 | -37.4325 | -37.4323 | -37.4326 | -37.4335 | -37.4338 | -37.4323 | -37.4334 | -37.4323 | -37.4335 | -37.4319 | -37.4339 | -37.4335 | -37.4317 | -37.4326 | -37.434 | -37.4321 | -37.4342 | -37.4334 | -37.4328 | -37.4333 | -37.4332 | -37.4332 | -37.4327 | -37.4334 | -37.4327 | -37.432 | -37.4335 | -37.4337 | -37.4326 | -37.4337 | -37.4323 | -37.432 | -37.4329 | -37.4331 | -37.4327 | -37.4326 | -37.4329 | -37.4324 | -37.4323 | -37.4335 | -37.433 | -37.4332 | -37.4326 | -37.4329 | -37.4327 | -37.4329 | -37.4324 | -37.4329 | -37.4328 | -37.4327 | -37.4319 | -37.4333 | -37.4329 | -37.4322 | -37.4319 | -37.4326 | -37.4328 | -37.433 | -37.4329 | -37.4324 | -37.4338 | -37.4325 | -37.4332 | -37.4326 | -37.4327 | -37.4328 | -37.4335 | -37.4328 | -37.4336 | -37.433 | -37.4331 | -37.4342 | -37.4333 | -37.4336 | -37.433 | -37.4328 | -37.4331 | -37.4325 | -37.4327 | -37.4323 | -37.4323 | -37.4329 | -37.4329 | -37.4324 | -37.4327 | -37.4318 | -37.4322 | -37.4332 | -37.4334 | -37.4334 | -37.4329 | -37.4326 | -37.4325 | -37.4321 | -37.4328 | -37.4331 | -37.4325 | -37.4327 | -37.4328 | -37.4323 | -37.4333 | -37.433 | -37.4327 | -37.433 | -37.4326 | -37.4323 | -37.4328 | -37.4328 | -37.4326 | -37.4324 | -37.4329 | -37.4321 | -37.4327 | -37.4334 | -37.4337 | -37.4329 | -37.4319 | -37.4328 | -37.4328 | -37.4324 | -37.4315 | -37.4328 | -37.4324 | -37.4327 | -37.4333 | -37.4332 | -37.4328 | -37.4329 | -37.4333 | -37.4338 | -37.433 | -37.4331 | -37.4328 | -37.4332 | -37.4321 | -37.4327 | -37.432 | -37.4325 | -37.4328 | -37.4323 | -37.4329 | -37.4326 | -37.4333 | -37.4323 | -37.4325 | -37.4332 | -37.4334 | -37.4327 | -37.433 | -37.4314 | -37.4332 | -37.434 | -37.4328 | -37.4335 | -37.4327 | -37.4323 | -37.4331 | -37.4333 | -37.4325 | -37.4323 | -37.4322 | -37.4323 | -37.4316 | -37.4326 | -37.4323 | -37.4325 | -37.4327 | -37.433 | -37.4323 | -37.4328 | -37.4325 | -37.433 | -37.4336 | -37.4323 | -37.4331 | -37.4328 | -37.4334 | -37.4335 | -37.4338 | -37.433 | -37.4334 | -37.4318 | -37.4321 | -37.4325 | -37.4337 | -37.4327 | -37.4334 | -37.4325 | -37.4331 | -37.4332 | -37.4329 | -37.4333 | -37.4325 | -37.4324 | -37.4324 | -37.4327 | -37.4331 | -37.4323 | -37.4327 | -37.4327 | -37.4329 | -37.4321 | -37.4342 | -37.433 | -37.4325 | -37.4327 | -37.4326 | -37.433 | -37.4331 | -37.4335 | -37.434
327 | p_Spare15 (AI15) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
328 | a_Water Temp into Condenser (TE-82) (AI0) |  | 19.1706 | 19.2579 | 19.2399 | 19.3284 | 19.195 | 19.2122 | 16.3518 | 16.3348 | 16.1146 | 15.946 | 15.8575 | 15.7966 | 15.5707 | 15.5261 | 15.421 | 15.5106 | 15.2922 | 14.4391 | 13.8599 | 16.2164 | 17.8913 | 13.3663 | 13.2669 | 13.1478 | 13.2412 | 13.371 | 13.4436 | 13.6418 | 13.7093 | 13.853 | 16.1733 | 16.0673 | 16.0418 | 16.064 | 16.1212 | 16.0748 | 17.7088 | 19.5885 | 19.5834 | 19.5744 | 19.5845 | 19.599 | 19.6388 | 19.6134 | 19.3662 | 19.8731 | 19.9867 | 20.0976 | 19.5893 | 19.5332 | 19.5603 | 19.4082 | 19.2273 | 19.0251 | 20.7719 | 20.7342 | 20.8174 | 15.4273 | 15.3216 | 15.2496 | 15.2471 | 15.1754 | 15.1093 | 13.9511 | 13.8172 | 13.6947 | 12.6948 | 13.0823 | 13.7749 | 18.1605 | 18.0699 | 17.7684 | 17.9092 | 17.8826 | 13.815 | 13.8442 | 13.8815 | 13.8543 | 13.8974 | 13.8801 | 13.8312 | 13.4268 | 13.3494 | 13.3756 | 15.9948 | 15.8921 | 15.852 | 15.8267 | 20.1856 | 20.0852 | 20.1214 | 20.136 | 20.5078 | 20.4149 | 20.3691 | 20.1037 | 19.9334 | 19.4516 | 28.874 | 28.8325 | 28.7274 | 28.699 | 28.4905 | 28.3242 | 28.2643 | 28.1149 | 21.4464 | 21.4876 | 21.5159 | 21.2924 | 21.2721 | 21.2758 | 21.2081 | 21.0269 | 20.8481 | 20.2567 | 19.6765 | 20.0889 | 13.6438 | 13.6113 | 13.5818 | 33.3389 | 36.6842 | 37.3747 | 37.4102 | 36.2679 | 35.6916 | 22.9187 | 37.6857 | 40.7735 | 40.0671 | 40.3214 | 40.6087 | 12.7142 | 12.6812 | 12.6039 | 13.639 | 13.5863 | 13.5706 | 12.6107 | 12.4486 | 12.2551 | 13.9622 | 13.9383 | 13.8689 | 13.8046 | 13.6867 | 13.6523 | 17.3045 | 17.5048 | 17.534 | 17.8022 | 17.7281 | 17.6796 | 19.6289 | 19.5284 | 19.3725 | 19.1337 | 19.015 | 18.9288 | 18.9337 | 18.8658 | 18.7066 | 18.1262 | 18.0776 | 18.0933 | 12.1947 | 11.0955 | 11.0197 | 22.8478 | 22.8397 | 22.8634 | 22.4285 | 22.2296 | 22.1522 | 16.7922 | 16.7968 | 16.7683 | 13.8599 | 13.8556 | 13.9048 | 13.8986 | 13.8774 | 13.8506 | 13.8596 | 13.8718 | 13.8706 | 15.5947 | 15.5573 | 15.5764 | 15.7517 | 15.783 | 15.836 | 17.4464 | 17.4045 | 17.5036 | 17.4811 | 17.3589 | 17.2905 | 21.9983 | 21.8195 | 21.6713 | 21.7713 | 21.8011 | 21.8634 | 22.7172 | 22.7104 | 22.8797 | 22.9844 | 23.043 | 23.0751 | 22.9855 | 22.9045 | 22.8251 | 22.6153 | 22.5436 | 22.1909 | 21.7036 | 21.6659 | 21.7369 | 15.2273 | 15.3691 | 15.4407 | 15.4798 | 15.4756 | 15.4363
329 | b_Water Temp out condenser (TE-83) (AI1) |  | 44.9395 | 47.2846 | 45.8457 | 50.1188 | 47.1407 | 48.3521 | 36.4704 | 35.9823 | 36.2697 | 32.8356 | 34.3842 | 32.7164 | 31.7966 | 32.1115 | 32.9647 | 20.0584 | 15.5873 | 15.4895 | 16.5552 | 19.5249 | 15.1391 | 21.4277 | 19.7597 | 20.6889 | 24.9823 | 24.8287 | 29.4682 | 27.2473 | 25.5081 | 27.071 | 36.5213 | 42.202 | 37.9827 | 38.8177 | 36.3446 | 35.3697 | 37.5654 | 47.5238 | 45.5295 | 48.5766 | 50.1006 | 46.1432 | 46.632 | 49.6106 | 46.0687 | 53.156 | 53.7208 | 49.2415 | 52.4622 | 49.8108 | 48.4789 | 52.862 | 54.0405 | 50.7946 | 57.664 | 61.944 | 61.3853 | 38.7612 | 39.793 | 36.3515 | 40.8879 | 35.7884 | 37.9032 | 29.6009 | 30.4048 | 29.329 | 18.7343 | 18.253 | 19.3824 | 14.3899 | 15.2207 | 47.0884 | 47.5911 | 46.9919 | 30.6469 | 29.6385 | 29.7104 | 27.5687 | 28.6781 | 28.6398 | 29.7591 | 29.9805 | 30.0481 | 30.5321 | 12.702 | 13.6852 | 14.3204 | 13.0383 | 47.837 | 48.3072 | 34.9512 | 50.805 | 48.2934 | 49.9925 | 55.7676 | 59.7699 | 58.827 | 54.7037 | 34.7344 | 34.3884 | 34.4314 | 31.0737 | 38.1057 | 35.0242 | 33.4602 | 36.5148 | 39.1721 | 42.9336 | 39.0972 | 47.2853 | 42.5878 | 46.753 | 44.869 | 50.6929 | 51.1671 | 36.9144 | 48.3349 | 39.7977 | 25.8963 | 23.517 | 25.3456 | 49.6756 | 37.7648 | 40.5525 | 35.2966 | 37.0462 | 35.5421 | 42.004 | 47.9044 | 38.4117 | 40.1793 | 36.5618 | 39.2312 | 22.381 | 22.1141 | 22.1801 | 34.9776 | 35.7639 | 33.8167 | 33.5131 | 32.4609 | 33.0911 | 21.8727 | 21.3105 | 19.6911 | 20.9913 | 21.1958 | 20.5297 | 44.9197 | 47.9299 | 47.2804 | 48.4287 | 46.177 | 49.6908 | 53.6828 | 54.1247 | 53.4829 | 51.7569 | 51.2061 | 57.7445 | 56.3868 | 51.9502 | 54.8903 | 61.2735 | 56.6091 | 58.1285 | 33.711 | 33.8634 | 33.4014 | 61.5977 | 62.4826 | 61.2339 | 63.0719 | 63.2921 | 64.1162 | 34.1938 | 33.6383 | 34.7775 | 23.6567 | 23.2878 | 24.764 | 24.2498 | 23.4029 | 23.3206 | 24.3567 | 22.4373 | 23.724 | 32.1819 | 32.9339 | 31.4323 | 33.0071 | 33.3826 | 30.7415 | 50.3499 | 49.7721 | 50.0473 | 48.6153 | 46.4038 | 50.6604 | 71.9227 | 70.1114 | 70.8323 | 71.3189 | 70.3842 | 67.3117 | 68.8988 | 63.2164 | 66.8354 | 68.4861 | 68.145 | 68.8372 | 68.4802 | 67.1532 | 67.2391 | 67.378 | 68.9007 | 71.4628 | 63.0812 | 67.8563 | 63.5068 | 31.419 | 32.195 | 30.9939 | 31.3879 | 32.293 | 32.7841
330 | c_Condenser Temperature (TE-03) (AI2) |  | 37.2105 | 37.3423 | 37.2127 | 36.9054 | 36.8049 | 36.7335 | 24.0654 | 24.1051 | 24.0312 | 24.2811 | 24.4752 | 24.4257 | 24.376 | 24.2513 | 24.0958 | 21.9118 | 22.0541 | 22.3482 | 19.0591 | 18.4114 | 18.1483 | 27.4108 | 27.3923 | 27.2633 | 26.5907 | 26.6012 | 26.5479 | 26.7285 | 26.9909 | 27.5861 | 37.9778 | 37.8682 | 37.8861 | 37.8739 | 37.927 | 37.8274 | 38.0712 | 47.042 | 47.0223 | 47.0176 | 47.0333 | 47.0596 | 46.996 | 46.9506 | 46.9263 | 48.2574 | 48.2035 | 48.141 | 47.19 | 47.0855 | 47.0239 | 46.3966 | 46.255 | 46.1172 | 47.9247 | 47.9743 | 47.9002 | 37.6329 | 37.8385 | 37.8883 | 37.7473 | 37.7458 | 37.6416 | 24.1266 | 24.0718 | 24.0483 | 19.5164 | 19.3356 | 19.1964 | 18.6829 | 18.4405 | 36.5646 | 36.4489 | 36.7001 | 24.0822 | 24.0712 | 24.0346 | 24.2881 | 24.0144 | 23.9092 | 23.8813 | 23.7302 | 23.7073 | 23.6865 | 18.6384 | 18.5637 | 18.592 | 18.5524 | 47.0129 | 47.3693 | 47.1603 | 47.3929 | 46.9336 | 46.8659 | 47.1338 | 46.1954 | 46.3654 | 46.3368 | 66.6618 | 66.7422 | 66.7591 | 67.0782 | 66.1608 | 65.3907 | 65.4746 | 65.2492 | 62.4113 | 60.9815 | 57.1621 | 48.6308 | 48.5012 | 48.1724 | 46.2014 | 46.1408 | 46.2205 | 50.8492 | 54.2135 | 57.7275 | 28.564 | 28.5002 | 28.3152 | 59.874 | 60.8127 | 60.2066 | 58.2772 | 57.745 | 57.3838 | 48.0522 | 57.8868 | 57.3028 | 55.1901 | 55.1102 | 55.8277 | 28.7745 | 28.7561 | 28.5535 | 23.5561 | 23.3952 | 23.6325 | 23.9307 | 23.7626 | 23.2708 | 19.7988 | 19.7113 | 19.6105 | 19.4813 | 19.0958 | 18.9903 | 37.2631 | 37.0439 | 37.0999 | 37.1578 | 37.0797 | 36.9324 | 48.2986 | 48.117 | 48.1633 | 46.9718 | 46.9266 | 46.8632 | 46.1423 | 46.2223 | 46.2472 | 46.7232 | 46.5312 | 46.4658 | 23.7818 | 24.0447 | 23.7941 | 46.0836 | 46.1058 | 46.1002 | 46.693 | 46.9333 | 46.8215 | 29.5725 | 29.5392 | 29.6174 | 22.0308 | 22.0015 | 21.9461 | 21.9335 | 21.8251 | 21.7626 | 21.3889 | 21.304 | 21.3409 | 24.9123 | 24.8401 | 24.6648 | 25.3003 | 25.065 | 25.079 | 37.4221 | 37.2682 | 36.9689 | 37.4341 | 37.3032 | 37.2519 | 48.03 | 47.8463 | 47.8624 | 47.7371 | 47.8023 | 47.843 | 46.0524 | 45.8107 | 46.1717 | 45.9373 | 45.919 | 45.9901 | 46.5723 | 46.5655 | 46.6306 | 46.7298 | 46.9151 | 46.7764 | 47.0533 | 47.0258 | 46.7697 | 24.6901 | 24.6908 | 24.7448 | 24.7364 | 24.66 | 24.5282
331 | d_Condenser Pressure (PT-04) (AI3) |  | 9.4575 | 9.4474 | 9.4608 | 9.4097 | 9.4258 | 9.4157 | 7.2809 | 7.3048 | 7.2856 | 7.2512 | 7.296 | 7.2982 | 7.2917 | 7.2902 | 7.2674 | 6.1682 | 6.162 | 6.1299 | 6.1246 | 6.1495 | 6.1304 | 7.2764 | 7.3129 | 7.2779 | 7.2458 | 7.2321 | 7.2521 | 7.2639 | 7.2681 | 7.2748 | 9.4646 | 9.4568 | 9.4458 | 9.4211 | 9.4422 | 9.4284 | 9.447 | 11.9851 | 11.9757 | 11.9896 | 11.9809 | 11.9819 | 11.9632 | 11.9734 | 11.9787 | 12.3671 | 12.3495 | 12.3358 | 11.9933 | 11.9575 | 11.9404 | 11.7946 | 11.7399 | 11.7183 | 12.3818 | 12.4014 | 12.3889 | 9.4765 | 9.4692 | 9.4994 | 9.4585 | 9.4803 | 9.4576 | 7.2836 | 7.3135 | 7.2984 | 6.1465 | 6.1719 | 6.1916 | 6.2145 | 6.1589 | 9.4553 | 9.4339 | 9.4595 | 7.2835 | 7.2974 | 7.2894 | 7.3153 | 7.3022 | 7.2911 | 7.296 | 7.2606 | 7.2703 | 7.2746 | 6.2247 | 6.2416 | 6.2119 | 6.1975 | 11.9773 | 12.0291 | 12.0422 | 12.0188 | 11.9997 | 11.9718 | 11.971 | 11.8036 | 11.8139 | 11.7956 | 11.9435 | 11.9562 | 11.9185 | 11.9464 | 11.8135 | 11.8332 | 11.8035 | 11.7258 | 12.2648 | 12.3023 | 12.3003 | 11.9294 | 11.8706 | 11.897 | 11.6961 | 11.6503 | 11.6642 | 11.9938 | 11.9245 | 11.9493 | 7.3001 | 7.3065 | 7.2486 | 12.3752 | 12.3698 | 12.3444 | 11.7651 | 11.7256 | 11.7195 | 11.9014 | 11.9061 | 11.9013 | 11.9404 | 11.9234 | 11.9095 | 7.3014 | 7.3021 | 7.2585 | 7.3153 | 7.2716 | 7.296 | 7.2795 | 7.2583 | 7.2616 | 6.1551 | 6.1336 | 6.1437 | 6.1759 | 6.157 | 6.1401 | 9.4701 | 9.4141 | 9.4158 | 9.4246 | 9.4238 | 9.3933 | 12.3893 | 12.345 | 12.3691 | 11.9593 | 11.9658 | 11.9146 | 11.7701 | 11.7095 | 11.7228 | 12.0386 | 11.9782 | 11.9573 | 7.2411 | 7.302 | 7.2458 | 11.7421 | 11.7469 | 11.7364 | 11.9399 | 11.9883 | 12.0005 | 7.269 | 7.2438 | 7.2465 | 6.1732 | 6.1623 | 6.1507 | 6.1242 | 6.1604 | 6.1646 | 6.1551 | 6.1225 | 6.0861 | 7.2757 | 7.2665 | 7.2367 | 7.2967 | 7.2532 | 7.2512 | 9.4809 | 9.4676 | 9.4039 | 9.4177 | 9.3988 | 9.3881 | 12.3662 | 12.3054 | 12.3196 | 12.3325 | 12.3252 | 12.2916 | 11.7315 | 11.6801 | 11.7416 | 11.7102 | 11.6737 | 11.6913 | 11.8927 | 11.8743 | 11.8822 | 11.9537 | 11.9704 | 11.969 | 11.9745 | 12.0128 | 11.9612 | 7.2323 | 7.2183 | 7.2301 | 7.2577 | 7.2486 | 7.2284
332 | e_Liquid Reciever Temperature (AI4) |  | 29.7919 | 29.6403 | 29.7927 | 29.731 | 29.5642 | 29.455 | 21.8173 | 21.8672 | 21.609 | 21.6596 | 21.7639 | 21.7194 | 21.698 | 21.508 | 21.4127 | 17.2275 | 17.1544 | 17.0246 | 17.2791 | 17.2687 | 17.1197 | 19.3802 | 19.5041 | 19.4294 | 19.8333 | 19.9069 | 19.9265 | 19.9314 | 19.9789 | 19.9628 | 28.2511 | 28.1549 | 28.1877 | 27.7717 | 27.9333 | 27.8063 | 27.5638 | 35.1703 | 35.1374 | 35.1211 | 35.1275 | 35.1411 | 34.968 | 35.0275 | 35.0547 | 35.5169 | 35.4045 | 35.5792 | 34.0782 | 33.9412 | 33.8676 | 33.6533 | 33.4583 | 33.1871 | 35.291 | 35.3984 | 35.336 | 26.7387 | 27.0113 | 26.8133 | 26.5493 | 26.5671 | 26.4097 | 19.5811 | 19.5401 | 19.3927 | 16.1917 | 16.2726 | 16.384 | 16.6414 | 16.3755 | 27.8706 | 27.5711 | 27.7412 | 19.1731 | 19.1998 | 19.1668 | 19.0656 | 18.9145 | 18.8172 | 18.7174 | 18.1569 | 18.1129 | 18.0443 | 14.4297 | 14.4271 | 14.4092 | 14.451 | 33.076 | 33.2669 | 33.0264 | 33.2927 | 32.2822 | 32.212 | 32.5648 | 31.3818 | 32.2057 | 31.5219 | 35.9596 | 36.12 | 35.8515 | 35.8122 | 35.3043 | 35.5121 | 35.4678 | 35.1191 | 36.357 | 36.6341 | 36.6941 | 35.5966 | 35.2948 | 35.3649 | 34.878 | 34.9249 | 35.1476 | 36.6823 | 36.6097 | 36.3613 | 20.2797 | 20.2475 | 20.0054 | 37.6986 | 37.483 | 37.5144 | 35.1415 | 35.0416 | 35.0195 | 35.8057 | 35.6554 | 35.5957 | 36.7519 | 36.5958 | 36.5478 | 20.3036 | 20.4673 | 20.3016 | 22.6112 | 22.4146 | 22.4245 | 22.4484 | 22.279 | 22.4022 | 19.0951 | 19.0934 | 19.0829 | 19.1539 | 19.2934 | 19.1855 | 30.9115 | 30.6281 | 30.6611 | 30.2285 | 30.1831 | 30.0949 | 38.4898 | 38.181 | 38.1918 | 36.7929 | 36.7892 | 36.5988 | 35.9225 | 35.7306 | 35.7006 | 38.4095 | 38.1857 | 38.3361 | 21.6485 | 21.7534 | 21.5388 | 37.0339 | 36.9675 | 36.9494 | 37.5945 | 38.0217 | 38.2088 | 25.9783 | 25.8637 | 25.8889 | 19.6174 | 19.5974 | 19.5686 | 19.5173 | 19.5821 | 19.5598 | 19.4635 | 19.2697 | 19.0973 | 23.0721 | 22.9994 | 22.8035 | 23.2213 | 23.1104 | 23.0651 | 32.4691 | 32.3974 | 32.154 | 31.5886 | 31.5313 | 31.4165 | 40.4617 | 40.2111 | 40.2838 | 40.3378 | 40.1942 | 40.2262 | 38.4128 | 38.121 | 38.5167 | 38.1468 | 38.0696 | 38.2043 | 39.0074 | 38.9281 | 38.9821 | 38.8468 | 39.4238 | 39.2126 | 39.5855 | 39.6867 | 39.4894 | 22.3963 | 22.2825 | 22.3756 | 22.5878 | 22.5137 | 22.4184
333 | f_Liquid Receiver Pressure (AI5) |  | 9.3693 | 9.3499 | 9.3633 | 9.3259 | 9.3248 | 9.3142 | 7.245 | 7.2895 | 7.2573 | 7.2306 | 7.2798 | 7.2875 | 7.2777 | 7.2634 | 7.2565 | 6.1587 | 6.1432 | 6.1246 | 6.1205 | 6.121 | 6.1112 | 7.2537 | 7.2776 | 7.2363 | 7.2022 | 7.1896 | 7.1971 | 7.2233 | 7.2063 | 7.2423 | 9.3762 | 9.3518 | 9.3342 | 9.3318 | 9.3184 | 9.3197 | 9.3462 | 11.861 | 11.8484 | 11.8598 | 11.8638 | 11.8644 | 11.8453 | 11.8421 | 11.8404 | 12.2514 | 12.2132 | 12.1976 | 11.8811 | 11.8324 | 11.8124 | 11.664 | 11.6206 | 11.5772 | 12.2381 | 12.2675 | 12.269 | 9.3707 | 9.3969 | 9.4153 | 9.388 | 9.3863 | 9.3796 | 7.2553 | 7.2761 | 7.273 | 6.145 | 6.1545 | 6.1775 | 6.2213 | 6.1578 | 9.3429 | 9.3465 | 9.3464 | 7.2667 | 7.2714 | 7.2665 | 7.299 | 7.268 | 7.2699 | 7.259 | 7.2351 | 7.2382 | 7.2564 | 6.2136 | 6.2226 | 6.2047 | 6.1822 | 11.8405 | 11.9166 | 11.9325 | 11.9158 | 11.87 | 11.8491 | 11.8451 | 11.6693 | 11.6768 | 11.6704 | 11.7849 | 11.8095 | 11.7736 | 11.7846 | 11.646 | 11.6827 | 11.6451 | 11.5775 | 12.1282 | 12.1577 | 12.173 | 11.7633 | 11.71 | 11.7269 | 11.5349 | 11.5058 | 11.5369 | 11.8559 | 11.7879 | 11.828 | 7.2954 | 7.3009 | 7.2331 | 12.2308 | 12.219 | 12.2033 | 11.6237 | 11.5755 | 11.5648 | 11.7495 | 11.7487 | 11.7642 | 11.8015 | 11.7913 | 11.7835 | 7.2729 | 7.2907 | 7.2519 | 7.2819 | 7.2433 | 7.2773 | 7.2578 | 7.2244 | 7.2382 | 6.131 | 6.1472 | 6.1261 | 6.1583 | 6.1441 | 6.1279 | 9.3561 | 9.313 | 9.3083 | 9.3101 | 9.3258 | 9.2793 | 12.2321 | 12.2153 | 12.2155 | 11.8196 | 11.8128 | 11.7727 | 11.6261 | 11.5702 | 11.5826 | 11.8962 | 11.8464 | 11.8186 | 7.2041 | 7.2646 | 7.2147 | 11.5996 | 11.6046 | 11.5965 | 11.7805 | 11.8324 | 11.8661 | 7.2233 | 7.2145 | 7.2241 | 6.162 | 6.1595 | 6.1385 | 6.1289 | 6.1552 | 6.1539 | 6.1349 | 6.1046 | 6.0761 | 7.2477 | 7.2304 | 7.2007 | 7.2382 | 7.2159 | 7.2346 | 9.3699 | 9.359 | 9.2882 | 9.3182 | 9.3019 | 9.2693 | 12.2198 | 12.1586 | 12.1707 | 12.1895 | 12.1655 | 12.1352 | 11.5735 | 11.5341 | 11.5843 | 11.5593 | 11.5257 | 11.5508 | 11.7522 | 11.7255 | 11.7388 | 11.7921 | 11.808 | 11.8329 | 11.8423 | 11.8888 | 11.8331 | 7.1927 | 7.1817 | 7.1877 | 7.2152 | 7.2226 | 7.1986
334 | g_differential pressure (AI6) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.000872 | 0.00049 | 0.000292 | 0.000411 | 0.000514 | 0.000865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001686 | 0.001747 | 0.001749 | 0.004556 | 0.004408 | 0.004838 | 0.033904 | 0.033879 | 0.033606 | 0.033046 | 0.032879 | 0.032334 | 0.033953 | 0.034027 | 0.033877 | 0.041266 | 0.041124 | 0.041046 | 0.040974 | 0.040934 | 0.040899 | 0.040901 | 0.040729 | 0.040796 | 0.039796 | 0.039696 | 0.039438 | 0.037649 | 0.037352 | 0.036136 | 0.033378 | 0.032985 | 0.033044 | 0.032201 | 0.031702 | 0.031407 | 0.039343 | 0.039133 | 0.039123 | 0.03901 | 0.038883 | 0.03896 | 0.034662 | 0.034282 | 0.034295 | 0.033896 | 0.033598 | 0.033616 | 0.033506 | 0.033137 | 0.033145 | 0.032846 | 0.032999 | 0.032469 | 0.031778 | 0.031405 | 0.031229 | 0.030181 | 0.029864 | 0.029526 | 0.027817 | 0.028934 | 0.028416
335 | h_Spare FLOWMETER (AI7) (AI7) |  | -10.0008 | -10.0004 | -10.0001 | -10.0007 | -10.0007 | -10.001 | -10.0006 | -10.0005 | -10.0006 | -10.0002 | -10.0006 | -10.0005 | -10 | -10 | -10.0001 | -10.0006 | -10.0001 | -10.0002 | -10.0005 | -10.0004 | -10.0007 | -10.0006 | -10.0003 | -10.0005 | -10.0003 | -10.001 | -10 | -10.0006 | -10.0008 | -10.0002 | -10.0003 | -10 | -10.0001 | -10.0005 | -10.0008 | -10.001 | -10.0004 | -10.0009 | -10.0008 | -10.0009 | -10.0004 | -10.0002 | -10.0006 | -10.0009 | -10.0001 | -10.0006 | -10.0007 | -10.0007 | -10.0007 | -10.0006 | -10.0006 | -10.0006 | -10.0005 | -10.0007 | -10.0007 | -10.0008 | -10.0005 | -10.0005 | -10.0009 | -10.001 | -10.0007 | -10.0008 | -10.0003 | -10.0007 | -10.0003 | -10.0006 | -10.0008 | -9.9999 | -10.0003 | -10.0003 | -10.0004 | -10.0007 | -10.0006 | -10.0003 | -10.0005 | -10.0007 | -10.0002 | -10.0006 | -10.0003 | -10.0003 | -10.0005 | -10.001 | -10.0003 | -10.0002 | -10.0006 | -10.0005 | -10.0006 | -10.0005 | -10.0005 | -10.0003 | -10.0005 | -10.0008 | -10.0006 | -10.0004 | -10.0007 | -10.0007 | -10.0003 | -10.0005 | -10.0008 | -10.0006 | -10.0007 | -10.0007 | -10.0004 | -10.0009 | -10.0005 | -10.0005 | -10.0003 | -10.0008 | -10.0004 | -10.0007 | -10.0007 | -10.0004 | -10.001 | -10.0003 | -10.0007 | -10.0007 | -10.0002 | -10.0004 | -10.0007 | -10.0007 | -10.0004 | -10.0009 | -10.0008 | -10.0004 | -10.0007 | -10.0004 | -10.0008 | -10.0007 | -10.0007 | -10.0001 | -10.0004 | -10.0006 | -10.0011 | -10.0003 | -10.0005 | -10.0007 | -10.0002 | -10.0006 | -10.0004 | -10.0002 | -10.0008 | -10.0004 | -10.0006 | -10.0004 | -10.0006 | -10.0003 | -10.0012 | -10.0006 | -10.0004 | -10.0005 | -10.0004 | -10.0007 | -10.0006 | -10.0007 | -10.0006 | -10.0006 | -10.0005 | -10.0005 | -10.0003 | -10.0006 | -10.0007 | -10.0003 | -10.0005 | -10.0004 | -10.0005 | -10.0009 | -10.0007 | -10.0004 | -10.0002 | -10.0006 | -10.0005 | -10.0006 | -10.0006 | -10.0006 | -10.0005 | -10.0005 | -10.0006 | -10.0006 | -10.0007 | -10.0002 | -10.0006 | -10.0007 | -10.0005 | -10.0003 | -10.0004 | -10.0003 | -10.0006 | -10.0006 | -10.0007 | -10.0005 | -10.0003 | -10.0003 | -10.0006 | -10.0006 | -10.0006 | -10.0005 | -10.0006 | -10.0006 | -10.0002 | -10.0005 | -10.0008 | -10.0006 | -10.0006 | -10.0005 | -10.0009 | -10.0004 | -10.0007 | -10.0005 | -10.0007 | -10.0004 | -10.0005 | -10.0009 | -10.0006 | -10.0005 | -10.0006 | -10.0004 | -10.0007 | -10.0006 | -10.0004 | -10.0002 | -10.0002 | -10.0004 | -10.0006 | -10.0008 | -10.0005 | -10.0003
336 | i_Condenser Temperature Mixed Water (TE-99) (AI8) |  | 19.808 | 19.9041 | 19.9659 | 20.4077 | 20.2645 | 20.1412 | 17.0511 | 17.0484 | 16.9151 | 16.6319 | 16.6032 | 16.4211 | 16.2386 | 16.1021 | 16.1198 | 13.3157 | 13.2307 | 13.1771 | 13.5392 | 13.3848 | 13.0379 | 12.2625 | 12.1277 | 12.1264 | 12.7788 | 12.9195 | 13.0075 | 13.395 | 13.4606 | 13.4374 | 16.5466 | 16.3726 | 16.3156 | 16.2173 | 16.3049 | 16.3851 | 16.484 | 20.1125 | 20.1809 | 20.1349 | 20.106 | 20.1045 | 20.1726 | 20.0612 | 20.2161 | 20.3487 | 20.3079 | 20.4857 | 20.4433 | 20.3703 | 20.3401 | 20.4168 | 20.2551 | 20.2584 | 21.6441 | 21.8569 | 21.795 | 16.2158 | 16.3466 | 16.0156 | 15.6745 | 15.6702 | 15.6224 | 14.3486 | 14.3626 | 14.3192 | 11.6936 | 11.6831 | 11.5675 | 11.2354 | 11.1987 | 18.6854 | 18.7635 | 18.8396 | 13.8476 | 13.9453 | 14.0798 | 14.3295 | 14.2844 | 14.3086 | 14.2848 | 13.7626 | 13.8227 | 13.755 | 11.6006 | 11.5845 | 11.5873 | 11.6532 | 20.7456 | 20.7198 | 20.5122 | 20.7121 | 21.2238 | 21.0159 | 21.1353 | 20.9616 | 21.0294 | 20.5099 | 22.2594 | 22.3707 | 22.3793 | 22.2241 | 21.8315 | 21.857 | 21.8507 | 21.685 | 21.5696 | 21.698 | 21.667 | 22.1164 | 22.0407 | 21.9359 | 21.8219 | 21.9778 | 22.0802 | 20.8936 | 21.2423 | 20.7722 | 13.8517 | 13.7954 | 13.7348 | 20.1063 | 19.8598 | 19.6414 | 19.6878 | 19.685 | 19.6828 | 20.7625 | 20.6487 | 19.9174 | 19.5088 | 19.6435 | 19.6723 | 12.8433 | 12.8205 | 12.8107 | 14.3313 | 14.3257 | 14.3095 | 13.3425 | 13.2086 | 13.0198 | 13.3733 | 13.2899 | 13.2861 | 13.2935 | 13.1972 | 13.2637 | 17.7919 | 17.9882 | 18.3248 | 18.4825 | 18.5712 | 18.4993 | 20.2676 | 20.1839 | 20.1722 | 19.9194 | 19.8093 | 19.6875 | 19.4705 | 19.5432 | 19.5555 | 19.5099 | 19.366 | 19.3615 | 11.9983 | 11.7649 | 11.6452 | 24.2161 | 24.1472 | 24.1436 | 23.9249 | 23.6943 | 23.2803 | 17.3303 | 17.4222 | 17.3847 | 13.8765 | 13.8375 | 13.8238 | 13.775 | 13.8158 | 13.8352 | 13.8798 | 13.7879 | 13.8421 | 16.3392 | 16.2809 | 16.0858 | 16.2481 | 16.2329 | 16.2134 | 18.7149 | 18.6986 | 18.8107 | 18.708 | 18.6347 | 18.5117 | 23.986 | 23.763 | 23.8008 | 23.3313 | 23.3466 | 23.4394 | 24.3189 | 24.3008 | 24.2806 | 24.6481 | 24.7118 | 24.7074 | 24.7346 | 24.7722 | 24.6937 | 24.3923 | 24.4659 | 24.3743 | 23.1367 | 23.243 | 23.2098 | 15.5642 | 15.6707 | 15.7183 | 16.0237 | 16.0639 | 16.0197
337 | j_Condenser Water Pressure (AI9) |  | 0.81011 | 0.82458 | 0.81364 | 0.81887 | 0.81031 | 0.81495 | 0.7859 | 0.77859 | 0.77429 | 0.78298 | 0.77174 | 0.77678 | 0.77665 | 0.78153 | 0.78145 | 0.76473 | 0.76053 | 0.76639 | 0.75385 | 0.76298 | 0.7556 | 0.8051 | 0.80852 | 0.79691 | 0.80054 | 0.81815 | 0.80575 | 0.82023 | 0.81863 | 0.80933 | 0.82356 | 0.81816 | 0.83035 | 0.83285 | 0.834 | 0.82575 | 0.8455 | 0.88602 | 0.88237 | 0.87022 | 0.88039 | 0.86953 | 0.88627 | 0.8798 | 0.87788 | 0.87946 | 0.86777 | 0.87987 | 0.88607 | 0.89074 | 0.88329 | 0.86734 | 0.87937 | 0.87234 | 0.88731 | 0.89129 | 0.88732 | 0.86359 | 0.86233 | 0.87498 | 0.86526 | 0.86759 | 0.85954 | 0.82908 | 0.81388 | 0.82749 | 0.79024 | 0.79195 | 0.78973 | 0.79159 | 0.78247 | 0.85953 | 0.85633 | 0.85664 | 0.84425 | 0.83871 | 0.8437 | 0.85928 | 0.85466 | 0.85649 | 0.85343 | 0.86557 | 0.86467 | 0.8636 | 0.84704 | 0.85785 | 0.86048 | 0.85771 | 0.94021 | 0.9453 | 0.93437 | 0.94139 | 0.94299 | 0.94473 | 0.9543 | 0.95188 | 0.94431 | 0.94414 | 0.89759 | 0.8997 | 0.88977 | 0.90285 | 0.89589 | 0.88882 | 0.8896 | 0.89979 | 0.88323 | 0.88674 | 0.88133 | 0.89194 | 0.89614 | 0.89232 | 0.88896 | 0.88111 | 0.89284 | 0.86052 | 0.8669 | 0.85092 | 0.80847 | 0.81164 | 0.80792 | 0.86945 | 0.86838 | 0.86886 | 0.86818 | 0.87061 | 0.88299 | 0.85572 | 0.86431 | 0.86321 | 0.83776 | 0.8445 | 0.84871 | 0.79177 | 0.78663 | 0.78521 | 0.78821 | 0.78602 | 0.7899 | 0.78688 | 0.78821 | 0.78488 | 0.78585 | 0.78518 | 0.78874 | 0.78623 | 0.78693 | 0.78641 | 0.79035 | 0.79254 | 0.79765 | 0.7922 | 0.7999 | 0.79644 | 0.84557 | 0.84405 | 0.84008 | 0.83645 | 0.83228 | 0.83336 | 0.82553 | 0.8334 | 0.83634 | 0.81804 | 0.82347 | 0.81361 | 0.78038 | 0.7799 | 0.77494 | 0.82771 | 0.82616 | 0.82535 | 0.82557 | 0.83138 | 0.81939 | 0.77557 | 0.77327 | 0.77038 | 0.78765 | 0.78426 | 0.79065 | 0.78401 | 0.78305 | 0.78192 | 0.78624 | 0.7824 | 0.78272 | 0.77463 | 0.77279 | 0.76771 | 0.76053 | 0.75938 | 0.76437 | 0.77638 | 0.77498 | 0.7746 | 0.77603 | 0.76847 | 0.77094 | 0.84598 | 0.84576 | 0.84347 | 0.84284 | 0.84375 | 0.83962 | 0.81577 | 0.80362 | 0.81281 | 0.80416 | 0.81144 | 0.81364 | 0.81459 | 0.81681 | 0.81879 | 0.81635 | 0.82125 | 0.82187 | 0.81998 | 0.81653 | 0.81617 | 0.76211 | 0.77209 | 0.76585 | 0.76703 | 0.76733 | 0.77007
338 | k_spare (AI10) |  | -25.0007 | -25.0011 | -25.0003 | -25.0004 | -25.0004 | -25.0009 | -25.0002 | -25.0007 | -25.0006 | -25.0006 | -24.9999 | -24.9999 | -25.0008 | -25.0005 | -25.0007 | -25.0004 | -25 | -25.0004 | -25 | -25.0006 | -25.0008 | -25.0007 | -25.0005 | -24.9999 | -24.9999 | -25.0006 | -25.0003 | -25.0002 | -25.0007 | -25.0005 | -25.0007 | -25.0005 | -25.0005 | -25.0002 | -25.0005 | -25.0007 | -25.0009 | -25.0005 | -25.0003 | -25.0001 | -25.001 | -25.0004 | -25.0006 | -25.0007 | -25.0002 | -25.0005 | -25.0006 | -25.0005 | -25.0005 | -25.0004 | -25.0004 | -25.0008 | -25.0007 | -24.9998 | -25.0005 | -25.0007 | -25.0005 | -25.0007 | -25.0003 | -25 | -25.0005 | -25.0006 | -25.0005 | -25 | -25.0004 | -25.0005 | -24.9997 | -25.0006 | -25.0001 | -25.0009 | -25.0002 | -24.9999 | -25.0004 | -25.0003 | -25.0005 | -25.0008 | -25.0005 | -24.9996 | -25.001 | -25.0005 | -25.0004 | -25.0006 | -25.0006 | -25.0001 | -25.0007 | -25.0002 | -25.0008 | -25.0004 | -25.0006 | -25.0007 | -25.0008 | -25.0003 | -25.0006 | -25.0013 | -25.0005 | -25.0007 | -25.0007 | -25.0003 | -25.0007 | -25.0012 | -25.0008 | -25.0002 | -25.0007 | -25.0001 | -25.0005 | -25.0007 | -25.0002 | -25.0006 | -25.0004 | -25.0008 | -25.0004 | -25.0008 | -25.0005 | -25.0003 | -25.0007 | -25.0012 | -25.0008 | -25.0001 | -25.0008 | -25.0003 | -24.9997 | -25.0007 | -25.0007 | -25.0013 | -25.0006 | -25.0008 | -25.0003 | -25.0003 | -25.0013 | -25.0003 | -25.0008 | -25.0005 | -25.0009 | -25.0005 | -25.0005 | -25.0001 | -25.0005 | -25.0004 | -25.0011 | -25.0004 | -25.0006 | -25.0006 | -25.0005 | -25.0003 | -25.0006 | -25.0001 | -25.0007 | -25.0002 | -25.0005 | -25.0005 | -25.0007 | -25.0001 | -25.0004 | -25.0004 | -25.0008 | -25.0006 | -25.0004 | -25.0006 | -25.0007 | -25.0008 | -25.0004 | -25.0002 | -25.0004 | -25.0003 | -25.0003 | -25.0006 | -25.0009 | -25.0009 | -25.0001 | -25.0002 | -25.0004 | -25.0003 | -25.0003 | -25.001 | -25.0005 | -25.0007 | -25.0004 | -25.0006 | -25.0001 | -24.9999 | -25.0007 | -25.0003 | -25.0004 | -25.0001 | -25.0006 | -25.0004 | -25.0005 | -25.0001 | -25.0008 | -25.0005 | -25.0005 | -25.0003 | -25.0004 | -25.0007 | -25.0007 | -25.0004 | -25.0006 | -25.0006 | -25.0007 | -25.0007 | -25.0008 | -25.0001 | -25.0004 | -25.0006 | -25.0003 | -25.0008 | -25.0004 | -25.0006 | -25.0004 | -25.0004 | -25.0008 | -25.0005 | -25.001 | -25.0005 | -25.0014 | -25.0006 | -25.0006 | -25.0006 | -25.0004 | -25.0007 | -25.0008 | -25.0009 | -25.0006 | -25.0006 | -25.0004 | -25.0007
339 | l_Oil flow_Coriolis (AI11) |  | 3.3203 | 3.1158 | 2.9665 | 3.3055 | 3.3343 | 3.4 | 1.2898 | -0.087323 | -0.087149 | -0.08721 | -0.087407 | -0.087445 | -0.087371 | -0.087287 | -0.087356 | -0.087435 | -0.08743 | -0.087407 | 1.1153 | 1.3586 | 0.95133 | 1.7877 | 1.7826 | 1.7745 | 1.8736 | 1.8327 | 1.798 | 1.7297 | 1.7758 | 1.8303 | 3.2635 | 2.9657 | 2.9667 | 3.4473 | 3.4487 | 3.4911 | 3.1709 | 3.5254 | 3.4988 | 3.4647 | 3.4244 | 3.5817 | 3.4874 | 3.396 | 3.5166 | 3.3631 | 3.4401 | 3.409 | 3.3709 | 3.4555 | 3.4289 | 3.3061 | 3.3695 | 3.2814 | 3.1415 | 3.227 | 3.4368 | 2.4513 | 2.8303 | 2.3925 | 2.7399 | 2.8007 | 2.6863 | 1.7121 | 1.6289 | 1.7105 | 0.95405 | 0.96186 | 0.9611 | 0.95635 | 0.94654 | 3.3347 | 3.225 | 2.9106 | 1.7246 | 1.6962 | 1.815 | 1.7036 | 1.7167 | 1.6121 | 1.6906 | 1.0886 | 0.97593 | 0.76148 | -0.087224 | 1.2108 | 1.632 | 1.2297 | 3.438 | 3.3868 | 3.4775 | 3.4096 | 3.4376 | 3.3661 | 3.1758 | 3.3718 | 3.434 | 3.3974 | 3.0165 | 3.2518 | 3.4668 | 3.1946 | 3.0268 | 3.0704 | 3.4377 | 2.8544 | 2.4486 | 2.4486 | 2.4395 | 2.2385 | 2.3954 | 2.4339 | 2.3551 | 2.33 | 2.3509 | 2.3829 | 2.6506 | 2.1368 | 1.0563 | 1.0465 | 1.0489 | 2.4192 | 2.4118 | 2.4414 | 2.8753 | 3.1463 | 2.9777 | 2.8234 | 2.9772 | 2.7899 | 2.4674 | 2.4217 | 2.4947 | 1.6339 | 1.7331 | 1.6461 | 1.087 | 1.0489 | 1.0594 | 1.0384 | 1.1851 | 0.99594 | -0.087317 | 0.63614 | -0.087444 | 0.64103 | -0.087417 | 1.1103 | 2.1786 | 2.1492 | 1.986 | 2.4165 | 2.3444 | 2.5862 | 2.5215 | 2.5056 | 2.6371 | 2.8738 | 3.0474 | 3.0115 | 2.8429 | 3.0321 | 3.1359 | 2.8283 | 3.2098 | 2.9735 | 1.668 | 1.7092 | 1.7219 | 3.1612 | 3.2919 | 3.3233 | 3.0149 | 3.2999 | 3.008 | 1.7411 | 1.7201 | 1.5864 | 1.4902 | 0.91062 | 0.83756 | 0.83674 | 0.85483 | 0.87748 | 0.83415 | 0.842 | 0.82669 | 1.7246 | 1.7393 | 1.6357 | 1.6306 | 1.4592 | 1.3668 | 2.3871 | 2.5857 | 2.1973 | 2.8468 | 2.9008 | 2.8286 | 3.3881 | 3.2277 | 2.8084 | 2.9125 | 3.2939 | 3.1877 | 3.342 | 3.4541 | 3.4921 | 3.445 | 3.6332 | 3.3433 | 3.49 | 3.3309 | 3.5313 | 3.6822 | 3.4381 | 3.2007 | 3.5994 | 3.4482 | 3.5546 | 1.6782 | 1.6647 | 1.668 | 1.6664 | 1.7121 | 1.795
340 | m_Oil sep diff (Bar) (AI12) |  | 0.093556 | 0.09867 | 0.10041 | 0.10093 | 0.11432 | 0.11209 | 0.077079 | 0.071561 | 0.077607 | 0.062366 | 0.069865 | 0.056254 | 0.063103 | 0.078986 | 0.055828 | 0 | 0.00082 | 0 | 0 | 0 | 0 | 0.031969 | 0.036495 | 0.034924 | 0.060112 | 0.053141 | 0.047325 | 0.004242 | 0.009007 | 0.013462 | 0.13457 | 0.12815 | 0.14034 | 0.090137 | 0.13733 | 0.095501 | 0.1668 | 0.24342 | 0.23679 | 0.24947 | 0.25905 | 0.24585 | 0.25553 | 0.24384 | 0.25338 | 0.3772 | 0.3513 | 0.38186 | 0.42546 | 0.40708 | 0.4139 | 0.3909 | 0.38811 | 0.42512 | 0.49313 | 0.47948 | 0.46151 | 0.15795 | 0.14892 | 0.15673 | 0.12326 | 0.11522 | 0.12281 | 0.01977 | 0.027919 | 0.029386 | 0.007061 | 0.004924 | 0.004827 | 0.001013 | 0.005646 | 0.12563 | 0.13162 | 0.1274 | 0.054923 | 0.059711 | 0.057888 | 0.065692 | 0.066983 | 0.063541 | 0.066146 | 0.07618 | 0.074618 | 0.074094 | 0.018845 | 0.022384 | 0.021011 | 0.024074 | 0.23628 | 0.22893 | 0.2197 | 0.24641 | 0.45046 | 0.47701 | 0.47091 | 0.41928 | 0.41317 | 0.41487 | 0.30525 | 0.28362 | 0.28713 | 0.27381 | 0.27193 | 0.26487 | 0.27756 | 0.26839 | 0.38786 | 0.40328 | 0.38196 | 0.30537 | 0.28102 | 0.39082 | 0.42993 | 0.29048 | 0.31738 | 0.25459 | 0.24752 | 0.24943 | 0.10797 | 0.10809 | 0.10722 | 0.25992 | 0.35287 | 0.32717 | 0.37635 | 0.39385 | 0.39311 | 0.35351 | 0.28452 | 0.29439 | 0.40427 | 0.59507 | 0.36614 | 0.074257 | 0.07803 | 0.081209 | 0.051692 | 0.052651 | 0.043763 | 0.074811 | 0.074955 | 0.071221 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11782 | 0.12484 | 0.13066 | 0.057835 | 0.068343 | 0.088266 | 0.27622 | 0.33109 | 0.30478 | 0.48619 | 0.46368 | 0.47874 | 0.39781 | 0.36079 | 0.39341 | 0.26533 | 0.29668 | 0.26645 | 0.11069 | 0.10669 | 0.11003 | 0.43112 | 0.41194 | 0.41125 | 0.41837 | 0.41438 | 0.39435 | 0.051946 | 0.052704 | 0.049291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.075463 | 0.072274 | 0.070567 | 0.009292 | 0 | 0.019728 | 0.11692 | 0.1173 | 0.12547 | 0.094608 | 0.096518 | 0.05236 | 0.36918 | 0.39643 | 0.39135 | 0.39645 | 0.39392 | 0.38279 | 0.42449 | 0.45485 | 0.41315 | 0.43951 | 0.44346 | 0.41962 | 0.41393 | 0.40014 | 0.38373 | 0.41279 | 0.41008 | 0.41472 | 0.21342 | 0.19708 | 0.22168 | 0.1018 | 0.10295 | 0.10275 | 0.1054 | 0.10428 | 0.098099
341 | n_spare13 (AI13) |  | -9.8997 | -9.9002 | -9.9 | -9.9 | -9.8998 | -9.9 | -9.8999 | -9.8999 | -9.9 | -9.9002 | -9.9 | -9.9002 | -9.9001 | -9.9 | -9.8999 | -9.9001 | -9.9002 | -9.9 | -9.9 | -9.9 | -9.9001 | -9.9 | -9.8999 | -9.8999 | -9.8998 | -9.8998 | -9.8999 | -9.9 | -9.8999 | -9.8998 | -9.9002 | -9.9002 | -9.8999 | -9.9 | -9.9 | -9.9 | -9.8999 | -9.8998 | -9.8998 | -9.8998 | -9.8998 | -9.8997 | -9.8999 | -9.8998 | -9.8998 | -9.9 | -9.8998 | -9.8999 | -9.8999 | -9.8998 | -9.8998 | -9.8999 | -9.8999 | -9.9 | -9.8999 | -9.8998 | -9.8997 | -9.9 | -9.8999 | -9.8998 | -9.9002 | -9.8999 | -9.8999 | -9.8999 | -9.9002 | -9.9001 | -9.8999 | -9.8999 | -9.9 | -9.8999 | -9.9001 | -9.8998 | -9.9 | -9.8999 | -9.8999 | -9.9 | -9.8999 | -9.8999 | -9.8999 | -9.9 | -9.9 | -9.8999 | -9.9 | -9.9001 | -9.8999 | -9.9001 | -9.8998 | -9.8998 | -9.9001 | -9.9 | -9.8999 | -9.8999 | -9.9 | -9.9001 | -9.8996 | -9.8997 | -9.8999 | -9.8998 | -9.9 | -9.9 | -9.8998 | -9.9 | -9.8999 | -9.8999 | -9.8999 | -9.8999 | -9.8998 | -9.8997 | -9.9 | -9.8998 | -9.8998 | -9.8998 | -9.9 | -9.8998 | -9.8999 | -9.8999 | -9.9 | -9.8999 | -9.9 | -9.9001 | -9.9001 | -9.8999 | -9.9 | -9.8999 | -9.9 | -9.8999 | -9.8999 | -9.9 | -9.8999 | -9.9 | -9.9 | -9.8999 | -9.9 | -9.9 | -9.8999 | -9.9001 | -9.8998 | -9.9 | -9.9 | -9.9 | -9.9 | -9.8999 | -9.8997 | -9.9001 | -9.8998 | -9.9001 | -9.9002 | -9.9 | -9.8998 | -9.9 | -9.9 | -9.8998 | -9.9 | -9.8999 | -9.8998 | -9.9 | -9.8999 | -9.8999 | -9.8999 | -9.8998 | -9.8999 | -9.8999 | -9.8999 | -9.8999 | -9.8999 | -9.8998 | -9.9001 | -9.8999 | -9.8999 | -9.8998 | -9.9001 | -9.9 | -9.8997 | -9.9 | -9.8999 | -9.9 | -9.9 | -9.9 | -9.9 | -9.9002 | -9.8999 | -9.9 | -9.9 | -9.8999 | -9.9001 | -9.9 | -9.9001 | -9.9001 | -9.8999 | -9.8999 | -9.9 | -9.8999 | -9.9 | -9.8999 | -9.8996 | -9.9 | -9.8998 | -9.8999 | -9.8999 | -9.8998 | -9.8999 | -9.8999 | -9.9 | -9.8998 | -9.8997 | -9.8998 | -9.8998 | -9.8999 | -9.9 | -9.8998 | -9.8997 | -9.8998 | -9.9001 | -9.8997 | -9.9 | -9.8998 | -9.9 | -9.8999 | -9.8999 | -9.9001 | -9.9001 | -9.9001 | -9.9 | -9.8998 | -9.9001 | -9.9
342 | o_Oil sump pressure (AI14) |  | 10.8801 | 10.8738 | 10.8964 | 10.8731 | 10.8853 | 10.8626 | 8.5692 | 8.5965 | 8.5772 | 8.5126 | 8.5586 | 8.5617 | 8.5665 | 8.5467 | 8.5287 | 7.3289 | 7.3305 | 7.287 | 7.2915 | 7.3183 | 7.2947 | 8.5406 | 8.5672 | 8.5365 | 8.5182 | 8.5203 | 8.5334 | 8.5412 | 8.542 | 8.5545 | 10.9645 | 10.9414 | 10.9327 | 10.9217 | 10.9291 | 10.9154 | 10.8961 | 13.7476 | 13.7561 | 13.7515 | 13.7525 | 13.7483 | 13.7416 | 13.7401 | 13.7381 | 14.1037 | 14.0787 | 14.0572 | 13.7728 | 13.7389 | 13.7222 | 13.5669 | 13.495 | 13.4872 | 13.9727 | 14.0051 | 14.0048 | 10.8588 | 10.8619 | 10.8836 | 10.8684 | 10.8587 | 10.8422 | 8.5148 | 8.5378 | 8.5269 | 7.2868 | 7.296 | 7.3226 | 7.3509 | 7.2995 | 10.8503 | 10.8239 | 10.8426 | 8.5272 | 8.5365 | 8.5307 | 8.5663 | 8.5572 | 8.5504 | 8.5481 | 8.5207 | 8.5199 | 8.525 | 7.3547 | 7.3694 | 7.3389 | 7.3258 | 13.5813 | 13.6297 | 13.651 | 13.638 | 13.6866 | 13.6796 | 13.6613 | 13.4842 | 13.4951 | 13.4864 | 13.6402 | 13.6635 | 13.6254 | 13.6329 | 13.5068 | 13.5369 | 13.4986 | 13.44 | 13.9733 | 14.0262 | 13.997 | 13.7762 | 13.7379 | 13.7303 | 13.513 | 13.5169 | 13.5334 | 13.7843 | 13.674 | 13.7188 | 8.5555 | 8.5596 | 8.4999 | 14.0165 | 14.0118 | 13.9882 | 13.512 | 13.4938 | 13.4706 | 13.6528 | 13.68 | 13.6575 | 13.6103 | 13.5785 | 13.5891 | 8.5403 | 8.5559 | 8.5039 | 8.5765 | 8.5417 | 8.5639 | 8.5333 | 8.5087 | 8.5188 | 7.2956 | 7.3009 | 7.2995 | 7.3229 | 7.3083 | 7.2952 | 10.8717 | 10.8204 | 10.8167 | 10.8627 | 10.8632 | 10.8306 | 14.0394 | 14.0159 | 14.0205 | 13.7144 | 13.6976 | 13.6893 | 13.5377 | 13.4648 | 13.4849 | 13.7127 | 13.6306 | 13.5994 | 8.5236 | 8.5925 | 8.5296 | 13.4781 | 13.5 | 13.4991 | 13.6896 | 13.7229 | 13.7414 | 8.5389 | 8.5135 | 8.5302 | 7.3354 | 7.3281 | 7.3191 | 7.3003 | 7.318 | 7.3174 | 7.3141 | 7.2812 | 7.2543 | 8.5659 | 8.5506 | 8.5165 | 8.5557 | 8.5281 | 8.5343 | 10.891 | 10.8729 | 10.8137 | 10.8827 | 10.8623 | 10.8365 | 14.0362 | 13.961 | 13.9599 | 14.0032 | 13.9909 | 13.9492 | 13.4784 | 13.4349 | 13.4776 | 13.463 | 13.425 | 13.472 | 13.6467 | 13.6215 | 13.6367 | 13.6915 | 13.7228 | 13.712 | 13.6163 | 13.6578 | 13.6104 | 8.5179 | 8.4986 | 8.5119 | 8.5379 | 8.5222 | 8.5072
343 | p_oil pump flow (AI15) |  | -4.4932 | -4.4931 | -4.493 | -4.4925 | -4.4925 | -4.4924 | -4.4909 | -4.4908 | -4.4907 | -4.4906 | -4.4906 | -4.4904 | -4.4903 | -4.4903 | -4.4902 | -4.4892 | -4.4892 | -4.4891 | -4.4887 | -4.4885 | -4.4882 | -4.4918 | -4.4919 | -4.4918 | -4.4919 | -4.492 | -4.4919 | -4.4921 | -4.4921 | -4.4923 | -4.4932 | -4.4932 | -4.4932 | -4.493 | -4.493 | -4.4931 | -4.4937 | -4.494 | -4.494 | -4.494 | -4.4939 | -4.4938 | -4.4938 | -4.4938 | -4.4936 | -4.4925 | -4.4925 | -4.4923 | -4.4914 | -4.4914 | -4.4912 | -4.4909 | -4.4906 | -4.4904 | -4.494 | -4.494 | -4.4939 | -4.492 | -4.492 | -4.492 | -4.4918 | -4.4917 | -4.4917 | -4.49 | -4.49 | -4.4899 | -4.4882 | -4.4882 | -4.4881 | -4.4879 | -4.4879 | -4.4922 | -4.4921 | -4.4921 | -4.4903 | -4.4902 | -4.4902 | -4.4899 | -4.4898 | -4.4898 | -4.4898 | -4.4893 | -4.4892 | -4.4893 | -4.4879 | -4.4879 | -4.4879 | -4.4879 | -4.4959 | -4.4959 | -4.4959 | -4.4958 | -4.4954 | -4.4954 | -4.4953 | -4.4948 | -4.4946 | -4.4942 | -4.4957 | -4.4957 | -4.4955 | -4.4955 | -4.4954 | -4.4952 | -4.4952 | -4.4951 | -4.4941 | -4.494 | -4.494 | -4.4934 | -4.4934 | -4.4933 | -4.4932 | -4.4931 | -4.493 | -4.4925 | -4.4923 | -4.4921 | -4.4888 | -4.4888 | -4.4887 | -4.4938 | -4.4937 | -4.4936 | -4.493 | -4.493 | -4.4929 | -4.4925 | -4.4924 | -4.4924 | -4.4922 | -4.4921 | -4.492 | -4.4877 | -4.4876 | -4.4876 | -4.4894 | -4.4891 | -4.4893 | -4.4886 | -4.4885 | -4.4884 | -4.4898 | -4.4898 | -4.4898 | -4.4897 | -4.4899 | -4.4896 | -4.4919 | -4.4918 | -4.4918 | -4.4915 | -4.4914 | -4.4913 | -4.494 | -4.4937 | -4.4936 | -4.4931 | -4.493 | -4.4929 | -4.4925 | -4.4924 | -4.4922 | -4.4929 | -4.4929 | -4.4927 | -4.4893 | -4.4892 | -4.4891 | -4.4938 | -4.4937 | -4.4936 | -4.4932 | -4.4931 | -4.4929 | -4.4907 | -4.4906 | -4.4905 | -4.4905 | -4.4905 | -4.4906 | -4.4905 | -4.4905 | -4.4905 | -4.4904 | -4.4904 | -4.4904 | -4.4907 | -4.4907 | -4.4906 | -4.491 | -4.491 | -4.491 | -4.4914 | -4.4913 | -4.4912 | -4.4905 | -4.4903 | -4.4902 | -4.495 | -4.4949 | -4.4949 | -4.4948 | -4.4947 | -4.4944 | -4.4937 | -4.4935 | -4.4935 | -4.4934 | -4.4934 | -4.4933 | -4.4931 | -4.493 | -4.493 | -4.4929 | -4.4928 | -4.4927 | -4.4923 | -4.4922 | -4.4921 | -4.489 | -4.489 | -4.4891 | -4.4889 | -4.4888 | -4.4887
344 | a_Compressor Discharge Valve FCV-01 (AO0) |  | 19.9991 | 19.9991 | 19.9991 | 19.9991 | 19.9991 | 19.9991 | 19.9991 | 19.9991 | 19.9991 | 10.9991 | 10.9991 | 10.9991 | 10.9991 | 10.9991 | 10.9991 | 7.9997 | 7.9997 | 7.9997 | 11.9995 | 11.9995 | 11.9995 | 3.9999 | 3.9999 | 3.9999 | 4.9984 | 4.9984 | 4.9984 | 4.9984 | 4.9984 | 4.9984 | 20.9995 | 20.9995 | 20.9995 | 24.9993 | 24.9993 | 24.9993 | 23.9989 | 19.9991 | 19.9991 | 19.9991 | 19.9991 | 19.9991 | 19.9991 | 19.9991 | 19.9991 | 10.9991 | 10.9991 | 10.9991 | 14.9989 | 14.9989 | 14.9989 | 14.9989 | 14.9989 | 14.9989 | 20.9995 | 20.9995 | 20.9995 | 2.9995 | 2.9995 | 2.9995 | 2.9995 | 2.9995 | 2.9995 | 2.9995 | 2.9995 | 2.9995 | 0.99861 | 0.99861 | 0.99861 | 0.99861 | 0.99861 | 16.9997 | 16.9997 | 16.9997 | 14.9989 | 14.9989 | 14.9989 | 14.9989 | 17.9982 | 17.9982 | 17.9982 | 17.9982 | 17.9982 | 17.9982 | 2.9995 | 2.9995 | 2.9995 | 2.9995 | 25.9998 | 25.9998 | 25.9998 | 25.9998 | 25.9998 | 23.9989 | 23.9989 | 26.9982 | 26.9982 | 27.9987 | 11.9995 | 11.9995 | 11.9995 | 11.9995 | 11.9995 | 11.9995 | 11.9995 | 11.9995 | 2.9995 | 2.9995 | 2.9995 | 14.9989 | 14.9989 | 14.9989 | 14.9989 | 14.9989 | 14.9989 | 11.9995 | 13 | 13 | 15.9993 | 15.9993 | 15.9993 | 11.9995 | 11.9995 | 11.9995 | 13.9984 | 13.9984 | 13.9984 | 17.9982 | 17.9982 | 17.9982 | 16.9997 | 16.9997 | 16.9997 | 16.9997 | 16.9997 | 16.9997 | 10.9991 | 10.9991 | 4.9984 | 9.9986 | 9.9986 | 9.9986 | 0.99861 | 0.99861 | 0.99861 | 0.99861 | 0.99861 | 0.99861 | 5.9988 | 5.9988 | 5.9988 | 8.9982 | 8.9982 | 8.9982 | 13 | 13 | 13 | 13.9984 | 13.9984 | 13.9984 | 13.9984 | 13.9984 | 13.9984 | 14.9989 | 14.9989 | 14.9989 | 19.9991 | 19.9991 | 19.9991 | 10.9991 | 10.9991 | 10.9991 | 11.9995 | 11.9995 | 11.9995 | 18.9986 | 18.9986 | 18.9986 | 0.99861 | 0.99861 | 0.99861 | 0.99861 | 0.99861 | 0.99861 | 0.99861 | 0.99861 | 0.99861 | 13.9984 | 13.9984 | 13.9984 | 11.9995 | 11.9995 | 11.9995 | 15.9993 | 15.9993 | 15.9993 | 19.9991 | 19.9991 | 19.9991 | 13 | 13 | 13 | 13 | 13 | 13.9984 | 22.9984 | 22.9984 | 22.9984 | 22.9984 | 22.9984 | 22.9984 | 22 | 22 | 22 | 22 | 22 | 22 | 20.9995 | 20.9995 | 20.9995 | 13 | 13 | 13 | 13 | 13 | 13
345 | b_Pneumatic Suction Valve FCV-02 (AO1) |  | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998
346 | c_Condenser Water Outlet Valve TCV-31 (AO2) |  | 10.9983 | 10.9983 | 9.9999 | 13.9995 | 11.9987 | 11.9987 | 12.9991 | 13.9995 | 12.9991 | 11.9987 | 11.9987 | 10.9983 | 10.9983 | 10.9983 | 10.9983 | 2.9991 | 1.9987 | 0.99835 | 0.99835 | 2.9991 | 0.99835 | 1.9987 | 1.9987 | 1.9987 | 3.9995 | 4.9999 | 4.9999 | 5.9983 | 5.9983 | 5.9983 | 2.9991 | 2.9991 | 2.9991 | 2.9991 | 2.9991 | 2.9991 | 3.9995 | 2.9991 | 2.9991 | 2.9991 | 2.9991 | 2.9991 | 2.9991 | 2.9991 | 2.9991 | 5.9983 | 5.9983 | 5.9983 | 5.9983 | 5.9983 | 5.9983 | 6.9987 | 6.9987 | 6.9987 | 7.9991 | 7.9991 | 7.9991 | 4.9999 | 5.9983 | 5.9983 | 5.9983 | 5.9983 | 5.9983 | 7.9991 | 7.9991 | 7.9991 | 2.9991 | 2.9991 | 2.9991 | 0.99835 | 0.99835 | 12.9991 | 12.9991 | 12.9991 | 8.9995 | 8.9995 | 8.9995 | 8.9995 | 8.9995 | 8.9995 | 8.9995 | 8.9995 | 8.9995 | 8.9995 | 11.9987 | 9.9999 | 4.9999 | 2.9991 | 4.9999 | 4.9999 | 2.9991 | 5.9983 | 6.9987 | 6.9987 | 8.9995 | 7.9991 | 6.9987 | 6.9987 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 1.9987 | 1.9987 | 1.9987 | 1.9987 | 2.9991 | 2.9991 | 1.9987 | 2.9991 | 0.99835 | 2.9991 | 2.9991 | 1.9987 | 2.9991 | 0.99835 | 0.99835 | 1.9987 | 0.99835 | 0.99835 | 0.99835 | 2.9991 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 1.9987 | 1.9987 | 1.9987 | 11.9987 | 11.9987 | 11.9987 | 10.9983 | 10.9983 | 10.9983 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 1.9987 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 1.9987 | 1.9987 | 0.99835 | 1.9987 | 1.9987 | 1.9987 | 0.99835 | 0.99835 | 0.99835 | 6.9987 | 7.9991 | 7.9991 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 7.9991 | 7.9991 | 7.9991 | 5.9983 | 5.9983 | 6.9987 | 9.9999 | 9.9999 | 9.9999 | 9.9999 | 9.9999 | 9.9999 | 9.9999 | 9.9999 | 9.9999 | 9.9999 | 9.9999 | 9.9999 | 9.9999 | 9.9999 | 9.9999 | 9.9999 | 9.9999 | 9.9999 | 9.9999 | 9.9999 | 9.9999 | 8.9995 | 8.9995 | 8.9995 | 8.9995 | 7.9991 | 7.9991 | 7.9991 | 7.9991 | 7.9991 | 7.9991 | 7.9991 | 7.9991
347 | d_Spare1 (AO3) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
348 | a_Spare1 (AO0) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
349 | b_Spare2 (AO2) |  | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006
350 | c_Spare3 (AO1) |  | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004
351 | d_Spare4 (AO3) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
352 | a_Run Signal (DIO0) |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
353 | b_DIO1 (DIO1) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
354 | c_DIO2 (DIO2) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
355 | d_DIO3 (DIO3) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
356 | e_DIO4 (DIO4) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
357 | f_DIO5 (DIO5) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
358 | g_DIO6 (DIO6) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
359 | h_DIO7 (DIO7) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
360 | a_Suction Temperature (TE-60) (RTD0) |  | 15.2453 | 15.4783 | 15.4345 | 17.5607 | 17.521 | 17.4276 | 20.2842 | 20.2017 | 20.063 | 19.0741 | 18.9792 | 18.8013 | 18.5706 | 18.4883 | 18.493 | 17.1189 | 17.0125 | 16.7228 | 18.9759 | 18.5056 | 18.4042 | 17.3922 | 16.9391 | 16.7895 | 16.1943 | 16.1802 | 16.1937 | 16.3087 | 16.2008 | 16.1704 | 17.1666 | 17.0217 | 16.8172 | 16.5701 | 16.3831 | 16.1233 | 16.9093 | 14.3163 | 14.3056 | 14.2855 | 14.3732 | 14.3977 | 14.4554 | 14.6297 | 14.9905 | 12.1148 | 12.491 | 11.6225 | 14.4707 | 14.4767 | 14.447 | 15.2061 | 14.9845 | 14.7759 | 11.0711 | 11.1825 | 11.2949 | 16.9689 | 16.7949 | 16.82 | 17.2337 | 17.2418 | 17.2429 | 18.3113 | 18.719 | 19.14 | 18.3754 | 18.4238 | 18.4575 | 17.928 | 17.8053 | 15.2657 | 15.1213 | 14.6392 | 16.9474 | 16.8708 | 16.7454 | 16.3672 | 16.8494 | 16.8831 | 16.9756 | 16.818 | 16.8359 | 16.894 | 17.6224 | 18.5485 | 18.5994 | 18.336 | 13.6671 | 14.0142 | 14.3711 | 14.4289 | 13.5508 | 14.6941 | 15.0175 | 18.91 | 19.3815 | 18.9184 | 21.6936 | 21.6804 | 21.6293 | 21.5924 | 21.5042 | 21.445 | 21.4117 | 21.3538 | 12.1552 | 12.4514 | 12.4251 | 13.616 | 13.7924 | 14.5835 | 15.4833 | 15.6995 | 15.957 | 13.1966 | 13.8774 | 13.2902 | 17.6319 | 17.477 | 17.6169 | 11.4366 | 11.2606 | 11.0319 | 13.6057 | 13.3032 | 12.8859 | 14.7596 | 14.4407 | 14.5919 | 13.3308 | 13.5145 | 13.5078 | 16.7238 | 16.7508 | 16.4436 | 18.3129 | 18.5421 | 19.3375 | 19.1512 | 18.6899 | 18.3133 | 17.8738 | 18.0498 | 18.1805 | 18.1335 | 17.8199 | 17.7217 | 15.4962 | 15.4738 | 15.4137 | 16.3355 | 16.1358 | 15.6846 | 12.61 | 11.434 | 10.0759 | 13.2532 | 13.0466 | 13.0493 | 13.1758 | 12.8939 | 12.9535 | 14.8885 | 16.1038 | 15.307 | 18.7739 | 18.5876 | 18.4132 | 15.277 | 15.2205 | 15.4129 | 15.5764 | 15.5655 | 14.7076 | 17.317 | 17.3614 | 17.2785 | 17.975 | 17.7715 | 17.7131 | 17.6607 | 17.7695 | 17.9254 | 17.9538 | 18.0434 | 18.2548 | 17.5106 | 17.506 | 17.7587 | 16.8961 | 17.0643 | 17.0753 | 16.19 | 16.1314 | 16.3208 | 16.6937 | 16.4427 | 16.3142 | 11.8317 | 11.827 | 11.7316 | 11.6198 | 11.323 | 10.9422 | 13.9971 | 13.8499 | 14.136 | 13.8051 | 13.8426 | 14.0177 | 14.0055 | 13.9145 | 13.6531 | 13.8262 | 13.8955 | 13.8649 | 14.34 | 14.1076 | 14.024 | 17.6488 | 17.7462 | 17.7469 | 17.7016 | 17.8186 | 18.0213
361 | b_Discharge Temperature (TE-54) (RTD1) |  | 64.9206 | 65.4558 | 65.7251 | 67.6261 | 67.6046 | 67.6164 | 56.3924 | 56.3225 | 56.2193 | 56.017 | 55.9235 | 55.7537 | 55.4961 | 55.3446 | 55.1113 | 45.7004 | 45.4766 | 45.3926 | 46.4671 | 46.0189 | 45.609 | 53.5322 | 53.2481 | 53.3954 | 52.6919 | 52.6848 | 52.5961 | 53.6881 | 53.541 | 53.3669 | 66.9299 | 66.7963 | 66.7029 | 66.5891 | 66.413 | 66.1839 | 67.2566 | 79.4 | 79.3899 | 79.3811 | 79.4592 | 79.4766 | 79.5019 | 79.6386 | 79.8189 | 83.6596 | 83.69 | 83.1033 | 80.6129 | 80.5601 | 80.7132 | 80.4026 | 80.0417 | 79.8318 | 82.6253 | 82.7389 | 82.8015 | 66.8161 | 66.7456 | 66.7452 | 67.1784 | 67.198 | 67.1985 | 55.9889 | 56.3751 | 56.574 | 46.7646 | 46.6674 | 46.5323 | 45.7305 | 45.2656 | 65.4899 | 65.4777 | 65.9108 | 53.5212 | 53.4746 | 53.3858 | 53.0156 | 53.6689 | 53.7036 | 53.7298 | 56.208 | 56.2506 | 56.3103 | 47.6678 | 48.0269 | 47.9808 | 47.9414 | 79.0585 | 79.3621 | 79.6115 | 79.6811 | 80.2055 | 80.973 | 81.2442 | 84.6134 | 84.8795 | 84.1783 | 81.3351 | 81.2728 | 80.9674 | 80.7776 | 80.4931 | 80.4914 | 80.2766 | 79.5949 | 81.6492 | 81.8133 | 81.7659 | 78.36 | 78.5664 | 79.1082 | 79.3911 | 79.5723 | 79.7772 | 77.2175 | 77.1545 | 76.8154 | 54.0542 | 53.963 | 53.9896 | 81.1123 | 80.8792 | 80.8373 | 77.4235 | 77.1664 | 76.8264 | 79.0837 | 78.7779 | 79.2053 | 76.5866 | 76.7418 | 76.5902 | 52.7574 | 52.5277 | 52.4436 | 54.6356 | 55.0605 | 55.1597 | 54.7452 | 54.0465 | 53.7595 | 46.5342 | 46.5135 | 46.384 | 46.505 | 45.5963 | 45.1859 | 64.4279 | 64.2532 | 64.3681 | 65.2223 | 64.9016 | 64.4856 | 82.3417 | 81.291 | 80.4547 | 78.0616 | 77.9128 | 77.841 | 77.0956 | 77.092 | 77.3296 | 78.4717 | 79.1191 | 78.5143 | 54.4239 | 54.1733 | 53.8665 | 79.6024 | 79.6789 | 79.8482 | 80.4132 | 80.318 | 79.6525 | 53.2308 | 53.4036 | 53.8557 | 46.8378 | 46.7412 | 46.8191 | 46.4041 | 47.0398 | 46.9755 | 46.7694 | 46.714 | 46.6495 | 53.6349 | 53.649 | 53.7512 | 53.5421 | 53.736 | 54.1174 | 65.0396 | 64.7326 | 64.928 | 65.7567 | 65.5189 | 65.2597 | 81.891 | 81.6127 | 81.551 | 81.3886 | 81.121 | 80.9454 | 78.01 | 77.8995 | 78.0808 | 77.851 | 77.8788 | 77.9965 | 78.6803 | 78.5979 | 78.6633 | 78.8859 | 78.9505 | 78.9132 | 77.7743 | 77.6319 | 77.0981 | 53.3605 | 53.4136 | 53.4166 | 53.4228 | 53.4506 | 53.2936
362 | c_Suction Flowmeter Temperature Low Duty (RTD2) |  | 23.5147 | 23.4328 | 23.3883 | 22.9184 | 22.8296 | 22.7641 | 21.2502 | 21.2102 | 21.1259 | 20.913 | 20.8716 | 20.7969 | 20.6793 | 20.5983 | 20.5379 | 19.7559 | 19.7553 | 19.741 | 18.9023 | 18.6581 | 18.3921 | 22.3693 | 22.388 | 22.3845 | 22.4817 | 22.5132 | 22.542 | 22.6549 | 22.6767 | 22.7055 | 23.3211 | 23.3074 | 23.2991 | 23.2309 | 23.2364 | 23.2459 | 23.7533 | 23.7272 | 23.714 | 23.6977 | 23.5702 | 23.5569 | 23.5119 | 23.4423 | 23.2982 | 22.3945 | 22.3239 | 22.2083 | 21.0039 | 20.8648 | 20.7187 | 20.3358 | 20.0463 | 19.8197 | 23.4144 | 23.3217 | 23.2528 | 21.6434 | 21.6334 | 21.607 | 21.4336 | 21.4112 | 21.3888 | 20.0598 | 20.0167 | 19.9864 | 17.9231 | 17.8527 | 17.7983 | 17.5471 | 17.4421 | 22.4259 | 22.3736 | 22.3127 | 20.8064 | 20.7962 | 20.7794 | 20.5932 | 20.5328 | 20.5193 | 20.5045 | 19.9872 | 19.9415 | 19.9055 | 18.7521 | 18.6795 | 18.665 | 18.6497 | 26.1837 | 26.1401 | 26.1129 | 26.0928 | 25.9967 | 25.9339 | 25.9055 | 25.1433 | 24.9805 | 24.3988 | 25.1837 | 25.1726 | 25.0833 | 25.0247 | 24.8882 | 24.7915 | 24.7017 | 24.6017 | 23.3242 | 23.2553 | 23.1951 | 22.7517 | 22.6698 | 22.5846 | 22.4558 | 22.354 | 22.258 | 21.7372 | 21.5049 | 21.3427 | 18.9132 | 18.8514 | 18.7742 | 23.0502 | 22.933 | 22.8201 | 22.2498 | 22.1316 | 22.046 | 21.4822 | 21.3977 | 21.3175 | 21.0842 | 20.9579 | 20.8466 | 17.4399 | 17.384 | 17.2631 | 19.094 | 19.0085 | 18.8638 | 17.8161 | 17.6353 | 17.4635 | 19.5179 | 19.4865 | 19.4576 | 19.451 | 19.392 | 19.3776 | 21.1707 | 21.1609 | 21.1385 | 20.7782 | 20.7431 | 20.7168 | 22.9411 | 22.7288 | 22.594 | 22.2581 | 22.1752 | 22.0486 | 21.7812 | 21.6279 | 21.4427 | 22.0095 | 21.928 | 21.811 | 19.1893 | 19.053 | 18.9404 | 23.1801 | 23.0555 | 22.9106 | 22.49 | 22.3149 | 22.1282 | 20.5268 | 20.4491 | 20.3808 | 20.9852 | 20.9849 | 20.972 | 20.9918 | 20.9613 | 20.9482 | 20.9766 | 20.972 | 20.9724 | 20.7065 | 20.656 | 20.5653 | 21.0683 | 21.0529 | 21.0454 | 20.7916 | 20.7235 | 20.5816 | 19.8399 | 19.681 | 19.5202 | 24.3405 | 24.2527 | 24.1675 | 23.9421 | 23.8604 | 23.6399 | 23.0358 | 22.9666 | 22.8859 | 22.7883 | 22.7051 | 22.6297 | 22.3788 | 22.2923 | 22.2061 | 22.0063 | 21.9375 | 21.7938 | 21.4171 | 21.2857 | 21.1613 | 18.6941 | 18.6455 | 18.608 | 18.477 | 18.3875 | 18.3212
363 | d__Suction Flowmeter Temperature High Duty (RTD3) |  | 15.2297 | 15.3698 | 15.5567 | 17.6118 | 17.6091 | 17.5038 | 20.4014 | 20.3128 | 20.1394 | 19.1442 | 19.0634 | 18.8666 | 18.6152 | 18.4872 | 18.5596 | 17.037 | 16.9921 | 16.7394 | 19.1675 | 18.549 | 18.3818 | 17.5931 | 16.9054 | 16.7132 | 16.0549 | 16.0284 | 16.0511 | 16.2887 | 16.1463 | 16.0964 | 17.3012 | 17.1679 | 17.0034 | 16.7474 | 16.5928 | 16.3034 | 16.988 | 14.6452 | 14.6343 | 14.6348 | 14.6544 | 14.7171 | 14.7525 | 14.8143 | 15.3291 | 12.3966 | 12.7973 | 12.2684 | 14.9808 | 14.9493 | 14.7773 | 15.7954 | 15.5731 | 15.2555 | 11.3692 | 11.4864 | 11.5449 | 17.1477 | 16.8812 | 16.8236 | 17.2557 | 17.2695 | 17.263 | 17.9453 | 18.2663 | 18.7981 | 18.3316 | 18.467 | 18.6333 | 18.0898 | 17.93 | 15.3888 | 15.2316 | 14.376 | 16.9786 | 16.8976 | 16.7832 | 16.4797 | 16.7158 | 16.7295 | 16.7941 | 16.6939 | 16.6729 | 16.7389 | 17.1019 | 18.4491 | 18.8525 | 18.7704 | 13.8548 | 14.3446 | 14.6265 | 14.9816 | 13.5804 | 14.8653 | 15.1748 | 19.2237 | 20.0499 | 19.3508 | 15.5393 | 15.5293 | 15.1965 | 14.9407 | 15.1549 | 15.2405 | 15.1364 | 14.6628 | 12.468 | 12.9078 | 13.2549 | 14.0641 | 14.1239 | 14.8673 | 16.0009 | 16.1561 | 16.361 | 13.0496 | 14.5876 | 13.6658 | 17.8229 | 17.3381 | 17.6227 | 12.0038 | 11.7832 | 11.4284 | 14.2679 | 13.9934 | 13.5985 | 15.6402 | 14.9683 | 15.186 | 13.7282 | 13.9645 | 14.0237 | 16.7333 | 16.8359 | 16.6708 | 18.177 | 18.2612 | 19.2329 | 19.4394 | 19.0394 | 18.4852 | 17.5775 | 17.7874 | 18.1119 | 18.222 | 17.8873 | 17.7857 | 15.5527 | 15.514 | 15.4571 | 16.5659 | 16.4167 | 16.2779 | 13.2602 | 12.073 | 10.0483 | 13.7469 | 13.6043 | 13.481 | 13.5088 | 13.6009 | 13.1505 | 14.7542 | 16.5898 | 15.9957 | 18.983 | 18.7162 | 18.4693 | 15.8354 | 15.7533 | 15.8323 | 16.0615 | 16.3192 | 15.4266 | 17.228 | 17.3372 | 17.3043 | 17.9562 | 17.6273 | 17.447 | 17.2767 | 17.3291 | 17.5956 | 17.6495 | 17.6124 | 17.8886 | 17.406 | 17.3156 | 17.5391 | 16.6276 | 16.9192 | 16.9259 | 16.3122 | 16.1987 | 16.0969 | 16.9385 | 16.7031 | 16.5126 | 12.2178 | 12.2589 | 12.139 | 11.9474 | 11.752 | 11.4318 | 14.6232 | 14.166 | 14.7633 | 14.3266 | 14.3295 | 14.4626 | 14.6045 | 14.5004 | 14.1354 | 14.2462 | 14.51 | 14.3244 | 14.8263 | 14.7981 | 14.5194 | 17.5783 | 17.7379 | 17.7548 | 17.6878 | 17.7246 | 18.0654
364 | AI0 |  | 44017 | 44017 | 44017 | 44017 | 44017 | 44017 | 44017 | 44017 | 44017 | 44017 | 44017 | 44017 | 44017 | 44017 | 44017 | 44017 | 44017 | 44017 | 44017 | 44017 | 44017 | 43987 | 43987 | 43987 | 43987 | 43987 | 43987 | 43987 | 43987 | 43987 | 43987 | 43987 | 43987 | 43987 | 43987 | 43987 | 43987 | 43987 | 43987 | 43987 | 43987 | 43987 | 43987 | 43987 | 43987 | 43987 | 43987 | 43987 | 43987 | 43987 | 43987 | 43987 | 43987 | 43987 | 43835 | 43835 | 43835 | 43835 | 43835 | 43835 | 43835 | 43835 | 43835 | 43835 | 43835 | 43835 | 43835 | 43835 | 43835 | 43835 | 43835 | 30/04/2020 | 30/04/2020 | 30/04/2020 | 30/04/2020 | 30/04/2020 | 30/04/2020 | 30/04/2020 | 30/04/2020 | 30/04/2020 | 30/04/2020 | 30/04/2020 | 30/04/2020 | 30/04/2020 | 30/04/2020 | 30/04/2020 | 30/04/2020 | 30/04/2020 | 29/04/2020 | 29/04/2020 | 29/04/2020 | 29/04/2020 | 29/04/2020 | 29/04/2020 | 29/04/2020 | 29/04/2020 | 29/04/2020 | 29/04/2020 | 28/04/2020 | 28/04/2020 | 28/04/2020 | 28/04/2020 | 28/04/2020 | 28/04/2020 | 28/04/2020 | 28/04/2020 | 22/04/2020 | 22/04/2020 | 22/04/2020 | 22/04/2020 | 22/04/2020 | 22/04/2020 | 22/04/2020 | 22/04/2020 | 22/04/2020 | 22/04/2020 | 22/04/2020 | 22/04/2020 | 22/04/2020 | 22/04/2020 | 22/04/2020 | 20/04/2020 | 20/04/2020 | 20/04/2020 | 20/04/2020 | 20/04/2020 | 20/04/2020 | 20/04/2020 | 20/04/2020 | 20/04/2020 | 20/04/2020 | 20/04/2020 | 20/04/2020 | 20/04/2020 | 20/04/2020 | 20/04/2020 | 17/04/2020 | 17/04/2020 | 17/04/2020 | 17/04/2020 | 17/04/2020 | 17/04/2020 | 16/04/2020 | 16/04/2020 | 16/04/2020 | 16/04/2020 | 16/04/2020 | 16/04/2020 | 16/04/2020 | 16/04/2020 | 16/04/2020 | 16/04/2020 | 16/04/2020 | 16/04/2020 | 15/04/2020 | 15/04/2020 | 15/04/2020 | 15/04/2020 | 15/04/2020 | 15/04/2020 | 15/04/2020 | 15/04/2020 | 15/04/2020 | 14/04/2020 | 14/04/2020 | 14/04/2020 | 14/04/2020 | 14/04/2020 | 14/04/2020 | 44078 | 44078 | 44078 | 44078 | 44078 | 44078 | 44047 | 44047 | 44047 | 44016 | 44016 | 44016 | 44016 | 44016 | 44016 | 44016 | 44016 | 44016 | 44016 | 44016 | 44016 | 44016 | 44016 | 44016 | 44016 | 44016 | 44016 | 44016 | 44016 | 44016 | 43986 | 43986 | 43986 | 43986 | 43986 | 43986 | 43986 | 43986 | 43986 | 43986 | 43986 | 43986 | 43986 | 43986 | 43986 | 43986 | 43986 | 43986 | 43986 | 43986 | 43986 | 43986 | 43986 | 43986 | 43986 | 43986 | 43986
365 | AI1 |  | 0.60972 | 0.60486 | 0.60208 | 0.5875 | 0.58542 | 0.58333 | 0.55278 | 0.55139 | 0.54861 | 0.54167 | 0.53958 | 0.5375 | 0.53333 | 0.53125 | 0.52917 | 0.49236 | 0.49028 | 0.4875 | 0.45347 | 0.44653 | 0.43958 | 0.68958 | 0.68681 | 0.68472 | 0.66875 | 0.66458 | 0.6625 | 0.65139 | 0.64931 | 0.64722 | 0.60556 | 0.60347 | 0.60139 | 0.57639 | 0.57361 | 0.57153 | 0.53542 | 0.52083 | 0.52014 | 0.51944 | 0.5125 | 0.51181 | 0.50972 | 0.50694 | 0.50139 | 0.45625 | 0.45347 | 0.45139 | 0.43542 | 0.43333 | 0.43125 | 0.42639 | 0.42361 | 0.42083 | 0.62847 | 0.62569 | 0.62361 | 0.58542 | 0.58403 | 0.58125 | 0.56528 | 0.56319 | 0.56111 | 0.51528 | 0.51319 | 0.51111 | 0.45625 | 0.45417 | 0.45278 | 0.44306 | 0.44028 | 0.68958 | 0.68681 | 0.68472 | 0.63889 | 0.63819 | 0.63611 | 0.59861 | 0.58403 | 0.58125 | 0.57917 | 0.52292 | 0.52014 | 0.51806 | 0.47014 | 0.4625 | 0.46042 | 0.45833 | 0.67986 | 0.67708 | 0.675 | 0.67292 | 0.64028 | 0.63472 | 0.63264 | 0.60972 | 0.60625 | 0.59653 | 0.69236 | 0.69167 | 0.6875 | 0.68472 | 0.67917 | 0.675 | 0.67083 | 0.66597 | 0.55069 | 0.54861 | 0.54653 | 0.53125 | 0.52917 | 0.52639 | 0.52361 | 0.52153 | 0.51944 | 0.50972 | 0.50625 | 0.50347 | 0.45972 | 0.45764 | 0.45486 | 0.68472 | 0.68125 | 0.67778 | 0.66181 | 0.65972 | 0.65764 | 0.53264 | 0.52986 | 0.52778 | 0.52222 | 0.51875 | 0.51597 | 0.45069 | 0.44861 | 0.44444 | 0.45486 | 0.45139 | 0.44653 | 0.42431 | 0.42153 | 0.41806 | 0.67639 | 0.67361 | 0.67083 | 0.66667 | 0.65972 | 0.65764 | 0.51806 | 0.51528 | 0.5125 | 0.49236 | 0.49028 | 0.48819 | 0.48264 | 0.47639 | 0.47222 | 0.46389 | 0.46181 | 0.45903 | 0.45278 | 0.45 | 0.44653 | 0.69028 | 0.68889 | 0.68681 | 0.63819 | 0.63472 | 0.63194 | 0.49444 | 0.49167 | 0.48819 | 0.48056 | 0.47708 | 0.47431 | 0.67917 | 0.67639 | 0.67431 | 0.69444 | 0.69236 | 0.69028 | 0.68819 | 0.68611 | 0.68403 | 0.67847 | 0.67569 | 0.67361 | 0.63611 | 0.63403 | 0.63194 | 0.53819 | 0.53611 | 0.53403 | 0.46042 | 0.45764 | 0.45486 | 0.43958 | 0.43681 | 0.43403 | 0.67917 | 0.67708 | 0.675 | 0.66875 | 0.66667 | 0.66181 | 0.52986 | 0.52708 | 0.52431 | 0.52222 | 0.51944 | 0.51736 | 0.51181 | 0.50972 | 0.50764 | 0.50347 | 0.50139 | 0.49861 | 0.49236 | 0.48958 | 0.4875 | 0.44444 | 0.44236 | 0.44028 | 0.43542 | 0.43264 | 0.43056
366 | AI2 |  | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL
367 | AI3 |  | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL
368 | AI4 |  | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL
369 | AI5 |  | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 1.6 | 1.6 | 1.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 2.6 | 2.6 | 2.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 1 2 2.6 | 1 2 2.6 | 1 2 2.6 | 1 2 2.6 | 1 2 2.6 | 1 2 2.6 | 1 2 2.6 | 1 2 2.6 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 1.6 | 1.6 | 1.6 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 1.6 | 1.6 | 1.6 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6
370 | AI6 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
371 | AI7 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
372 | AI8 |  | AS | AS | AS | AS | AS | AS | AS | AS | AS | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | AS | AS | AS | AS | AS | AS | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | AS | AS | AS | AS | AS | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | AS + MJ | AS + MJ | AS + MJ | AS | AS | AS | AS | AS + MJ | AS + MJ | AS + MJ | AS + MJ | AS + MJ | AS + MJ | AS | AS | AS | AS | AS | AS | AS | AS | AS | AS | AS | AS | AS | AS | AS | AS | AS | AS | AS | AS | AS | AS | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ
373 | AI9 |  | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR Test @20Hz (higher duty) | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR Test @20Hz (higher duty) | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR Test @20Hz (higher duty) | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR Test @20Hz (higher duty) | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR Test @20Hz (higher duty) | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer Withour econ plug OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer Withour econ plug OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer Withour econ plug OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer Withour econ plug OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer Withour econ plug OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer Withour econ plug OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer Withour econ plug OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer Withour econ plug OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer Withour econ plug OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer Withour econ plug OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer Withour econ plug OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer Withour econ plug OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer Withour econ plug OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer Withour econ plug OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer Withour econ plug OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice + plug Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice + plug Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice + plug Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice + plug Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice + plug Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice + plug Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice + plug Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice + plug Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice + plug Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice + plug Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice + plug Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice + plug Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice + plug Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice + plug Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice + plug Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Center Bearing orifice 3rd Bearing oil feed orifice Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Center Bearing orifice 3rd Bearing oil feed orifice Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Center Bearing orifice 3rd Bearing oil feed orifice Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Center Bearing orifice 3rd Bearing oil feed orifice Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Center Bearing orifice 3rd Bearing oil feed orifice Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Center Bearing orifice 3rd Bearing oil feed orifice Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Center Bearing orifice 3rd Bearing oil feed orifice Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Center Bearing orifice 3rd Bearing oil feed orifice Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Center Bearing orifice 3rd Bearing oil feed orifice Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR 21% of load @ 110Hz | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR 21% of load @ 110Hz | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR 21% of load @ 110Hz | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR 21% of load @ 110Hz | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR 21% of load @ 110Hz | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR 21% of load @ 110Hz | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR 21% of full load @ 120Hz | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR 21% of full load @ 120Hz | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR 47% of full load @ 120Hz | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR 47% of full load @ 120Hz | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR 47% of full load @ 120Hz | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR 47% of full load @ 120Hz | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR 47% of load @ 110Hz | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR 47% of load @ 110Hz | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR 47% of load @ 110Hz | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR 74% of load @ 110Hz | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR 74% of load @ 110Hz | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR 74% of load @ 110Hz | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR 74% of full load 120Hz | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR 74% of full load 120Hz | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR 74% of full load 120Hz | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR Slide / VVR Oil vent shut | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR Slide / VVR Oil vent shut | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR Slide / VVR Oil vent shut | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR Slide VVR/Oil vent shut | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR Slide VVR/Oil vent shut | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR Slide VVR/Oil vent shut | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR Slide VVR/Oil vent shut | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR Slide VVR/Oil vent shut | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR Slide VVR/Oil vent shut | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Center Bearing blocked 3rd Bearing oil feed blocked Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR
374 | AI10 |  | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD - target duty 524 kW | 310-240FS, 2.6VR MOD - target duty 524 kW | 310-240FS, 2.6VR MOD - target duty 524 kW | 310-240FS, 2.6VR MOD - target duty 524 kW | 310-240FS, 2.6VR MOD - target duty 524 kW | 310-240FS, 2.6VR MOD - target duty 332 kW | 310-240FS, 2.6VR MOD - target duty 332 kW | 310-240FS, 2.6VR MOD - target duty 332 kW | 310-240FS, 2.6VR MOD - target duty 332 kW | 310-240FS, 2.6VR MOD - target duty 148 kW | 310-240FS, 2.6VR MOD - target duty 148 kW | 310-240FS, 2.6VR MOD - target duty 148 kW | 310-240FS, 2.6VR MOD - target duty 148 kW | 310-240FS, 2.6VR MOD - target duty 148 kW | 310-240FS, 2.6VR MOD - target duty 569kW | 310-240FS, 2.6VR MOD - target duty 569kW | 310-240FS, 2.6VR MOD - target duty 569kW | 310-240FS, 2.6VR MOD - target duty 361kW | 310-240FS, 2.6VR MOD - target duty 361kW | 310-240FS, 2.6VR MOD - target duty 361kW | 310-240FS, 2.6VR MOD - target duty 361kW | 310-240FS, 2.6VR MOD - target duty 361kW | 310-240FS, 2.6VR MOD - target duty 361kW | 310-240FS, 2.6VR MOD - target duty 361kW | 310-240FS, 2.6VR MOD - target duty 361kW | 310-240FS, 2.6VR MOD - target duty 361kW | 310-240FS, 2.6VR MOD - target duty 361kW | 310-240FS, 2.6VR MOD - target duty 161kW | 310-240FS, 2.6VR MOD - target duty 161kW | 310-240FS, 2.6VR MOD - target duty 161kW | 310-240FS, 2.6VR MOD - target duty 161kW | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE - Target duty 347.6 | 310240FS - DAE - Target duty 347.6 | 310240FS - DAE - Target duty 347.6 | 310240FS - DAE - Target duty 347.6 | 310240FS - DAE - Target duty 347.6 | 310240FS - DAE - Target duty 347.6 | 310240FS - DAE - Target duty 547.2 | 310240FS - DAE - Target duty 547.2 | 310240FS - DAE - Target duty 547.2 | 310240FS - DAE - Target duty 547.2 | 310240FS - DAE - Target duty 547.2 | 310240FS - DAE - Target duty 547.2 | 310240FS - DAE - Target duty 585.8 | 310240FS - DAE - Target duty 585.8 | 310240FS - DAE - Target duty 585.8 | 310240FS - DAE - Target duty 585.8 | 310240FS - DAE - Target duty 585.8 | 310240FS - DAE - Target duty 585.8 | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE 310240FS - DAE 310240FS - DAE | 310240FS - DAE - Target duty 153 kW | 310240FS - DAE - Target duty 153 kW | 310240FS - DAE - Target duty 153 kW | 310240FS - DAE - Target duty 153 kW | 310240FS - DAE - Target duty 153 kW | 310240FS - DAE - Target duty 153 kW | 310240FS - DAE - Target duty 166 kW | 310240FS - DAE - Target duty 166 kW | 310240FS - DAE - Target duty 166 kW | 310240FS - DAE - Target duty 372 kW | 310240FS - DAE - Target duty 372 kW | 310240FS - DAE - Target duty 372 kW | 310240FS - DAE - Target duty 343 kW | 310240FS - DAE - Target duty 343 kW | 310240FS - DAE - Target duty 343 kW | 310240FS - DAE - Target duty 541 kW | 310240FS - DAE - Target duty 541 kW | 310240FS - DAE - Target duty 541 kW | 310240FS - DAE - Target duty 585 kW | 310240FS - DAE - Target duty 585 kW | 310240FS - DAE - Target duty 585 kW | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE
375 | AI11 |  | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134
376 | AI12 |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
377 | AI13 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
378 | AI14 |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
379 | AI15 |  | 385.735 | 385.1328 | 384.3926 | 383.1533 | 386.387 | 386.29 | 393.3895 | 393.2566 | 392.8126 | 392.4107 | 392.1945 | 392.5252 | 392.59 | 391.3191 | 391.7668 | 392.815 | 393.0038 | 392.2923 | 391.7883 | 392.8479 | 393.6353 | 391.1621 | 391.4827 | 391.6231 | 394.8878 | 395.919 | 395.5744 | 395.6564 | 395.4878 | 395.7836 | 386.4995 | 387.2161 | 386.209 | 383.9177 | 383.451 | 383.5436 | 380.266 | 387.0678 | 387.1141 | 386.715 | 388.3051 | 388.6003 | 386.9339 | 388.0573 | 386.8793 | 386.1083 | 387.2325 | 387.2848 | 387.661 | 387.3199 | 389.1295 | 389.3866 | 388.0535 | 387.9746 | 386.0808 | 390.3037 | 393.3854 | 384.4915 | 382.6445 | 387.1941 | 388.041 | 386.3311 | 385.9894 | 392.2217 | 392.497 | 393.0242 | 393.0669 | 392.8805 | 392.1883 | 392.9397 | 392.9462 | 385.4534 | 385.9318 | 385.4666 | 391.3109 | 392.0096 | 392.3896 | 391.8893 | 391.1028 | 391.6318 | 391.0598 | 389.1586 | 388.2585 | 388.0193 | 391.5457 | 391.7004 | 391.6513 | 391.6281 | 394.1862 | 394.0377 | 394.0753 | 393.7108 | 390.3849 | 390.0565 | 390.0321 | 387.9602 | 387.6589 | 386.748 | 391.1575 | 391.2625 | 391.8539 | 391.0021 | 390.918 | 390.7022 | 390.0443 | 390.6852 | 386.2664 | 387.7201 | 386.4187 | 385.6258 | 386.2263 | 386.3082 | 385.8322 | 386.313 | 386.077 | 387.1243 | 384.8367 | 385.8713 | 389.9212 | 390.6934 | 390.4132 | 388.0284 | 387.7968 | 385.5854 | 391.2403 | 390.3618 | 390.6406 | 388.0632 | 387.6086 | 388.1396 | 388.5059 | 389.1731 | 388.4681 | 392.7734 | 392.2895 | 392.4039 | 389.1583 | 388.4236 | 388.9763 | 386.8425 | 387.427 | 388.3141 | 394.2373 | 392.8414 | 394.1276 | 394.1279 | 393.7126 | 393.8521 | 384.4383 | 382.4084 | 382.4591 | 380.6678 | 380.8088 | 380.7841 | 385.9788 | 388.4112 | 386.6851 | 387.3548 | 388.1031 | 385.9949 | 383.6124 | 383.9015 | 383.8327 | 393.0576 | 393.307 | 392.1948 | 393.6078 | 394.125 | 393.3839 | 387.068 | 387.3742 | 387.6238 | 387.2894 | 387.2281 | 387.8787 | 394.4284 | 394.9185 | 394.3318 | 391.5428 | 392.2126 | 392.3051 | 392.1862 | 392.4463 | 393.1044 | 392.0617 | 392.7169 | 391.9505 | 393.0471 | 392.4918 | 393.485 | 391.1986 | 389.6418 | 390.5072 | 384.7327 | 384.0511 | 383.9133 | 382.5064 | 382.5863 | 383.3703 | 390.3917 | 389.8806 | 389.5439 | 389.6052 | 390.4742 | 389.9022 | 384.466 | 385.0862 | 385.1826 | 384.8484 | 385.9821 | 385.1639 | 385.4979 | 384.6889 | 384.8355 | 384.3029 | 384.8881 | 384.7271 | 386.7691 | 387.0174 | 386.7713 | 389.764 | 389.2766 | 389.8944 | 389.5468 | 390.1634 | 389.7628
380 | Date |  | 393.9749 | 393.4142 | 392.2578 | 390.9904 | 394.8124 | 394.7076 | 392.6014 | 392.91 | 392.6588 | 391.0334 | 390.9886 | 390.7425 | 391.3545 | 389.3866 | 390.6586 | 394.0321 | 394.265 | 393.2913 | 392.836 | 394.2957 | 394.9097 | 389.1173 | 388.9279 | 389.3839 | 393.8973 | 394.2282 | 394.0718 | 394.6437 | 394.13 | 394.9829 | 394.5494 | 394.8925 | 393.8838 | 392.0005 | 392.5687 | 392.052 | 388.3751 | 381.3617 | 382.4113 | 380.4896 | 383.0838 | 382.5013 | 382.6371 | 382.0497 | 381.9776 | 382.4868 | 383.7468 | 384.1285 | 383.8503 | 385.13 | 385.1713 | 385.1044 | 383.2865 | 383.0254 | 381.8683 | 386.4217 | 387.2332 | 392.6136 | 391.3571 | 394.3681 | 395.2393 | 393.9332 | 393.6915 | 390.1962 | 390.1006 | 390.6992 | 393.2138 | 392.9273 | 392.4963 | 393.7762 | 393.3405 | 393.7981 | 393.7752 | 393.8197 | 389.7375 | 389.7364 | 390.5642 | 389.8905 | 390.2445 | 390.8649 | 390.3955 | 388.7134 | 387.4984 | 387.3201 | 392.7039 | 393.0231 | 392.7546 | 392.6679 | 389.1196 | 386.8175 | 386.186 | 386.4724 | 386.8192 | 384.3913 | 384.1288 | 383.4532 | 381.8725 | 383.0827 | 387.6346 | 385.6198 | 386.3508 | 385.4752 | 384.74 | 385.4522 | 384.3005 | 384.2383 | 384.4596 | 384.53 | 382.136 | 382.6006 | 380.7853 | 382.1909 | 381.5777 | 382.6405 | 382.0448 | 382.3062 | 379.0173 | 380.6895 | 389.8078 | 390.872 | 390.9857 | 385.1261 | 386.0327 | 383.0533 | 387.1915 | 386.4386 | 385.0125 | 385.0146 | 384.1147 | 383.7226 | 384.1563 | 382.2769 | 383.7354 | 392.2608 | 391.4256 | 392.2731 | 386.9452 | 386.1435 | 386.5744 | 384.1817 | 385.0788 | 386.017 | 394.5173 | 393.1307 | 394.3738 | 394.4861 | 393.8972 | 394.4909 | 392.2379 | 389.9401 | 390.2834 | 388.3575 | 388.4059 | 388.4544 | 383.8016 | 384.6028 | 384.0892 | 383.3555 | 384.4915 | 384.8742 | 380.9635 | 380.8886 | 381.7089 | 386.5121 | 386.6692 | 386.2132 | 392.8599 | 393.3441 | 392.0817 | 383.3045 | 384.9562 | 384.4667 | 385.0195 | 384.72 | 386.0963 | 393.5642 | 394.1342 | 393.4664 | 391.6559 | 392.2469 | 392.5896 | 392.1597 | 392.0434 | 392.6248 | 392.5512 | 393.2515 | 392.6169 | 391.3721 | 390.5262 | 392.1206 | 388.3649 | 387.1652 | 387.8743 | 392.0636 | 391.4456 | 391.5766 | 389.878 | 390.4479 | 391.4321 | 384.7912 | 384.8364 | 384.1166 | 383.666 | 384.3897 | 383.7888 | 380.3766 | 379.2928 | 382.8506 | 382.7148 | 382.0615 | 379.8943 | 379.9744 | 381.5645 | 380.7676 | 383.5368 | 382.2668 | 381.3159 | 381.255 | 381.2449 | 381.4081 | 388.6539 | 388.3981 | 388.2902 | 387.9699 | 388.9746 | 388.2922
381 | Time |  | 391.2808 | 391.6155 | 390.5056 | 391.4287 | 393.5194 | 393.2478 | 389.2656 | 388.8925 | 388.3023 | 388.5757 | 388.3694 | 388.6977 | 388.6993 | 387.3777 | 388.3758 | 392.0933 | 392.26 | 391.281 | 391.1024 | 392.7999 | 392.9307 | 389.6655 | 389.4943 | 389.5616 | 392.2081 | 392.6364 | 392.5833 | 391.8213 | 391.5823 | 391.8355 | 390.504 | 389.7223 | 390.6406 | 390.1956 | 391.4757 | 389.4873 | 388.5945 | 378.2448 | 378.4693 | 378.7195 | 380.1138 | 379.8886 | 378.0668 | 379.1275 | 377.8041 | 377.9981 | 378.4664 | 378.1517 | 378.7359 | 378.3372 | 379.3531 | 380.1629 | 379.5038 | 378.6259 | 376.8959 | 380.4741 | 383.6371 | 389.4464 | 388.6583 | 390.8068 | 391.7011 | 390.6139 | 392.7518 | 390.3921 | 391.5788 | 391.7321 | 392.6519 | 391.7614 | 391.829 | 392.9538 | 392.1305 | 392.1866 | 391.8255 | 391.5054 | 388.5952 | 389.0021 | 389.4646 | 388.8311 | 387.4098 | 388.0265 | 387.5187 | 385.4316 | 384.5835 | 384.5211 | 392.9779 | 392.6905 | 392.4282 | 392.4696 | 384.3642 | 385.4394 | 385.7145 | 384.8034 | 381.5387 | 381.4186 | 380.8696 | 379.7609 | 380.144 | 378.1388 | 381.3724 | 382.0777 | 382.6908 | 382.0544 | 383.4097 | 383.0437 | 382.4328 | 383.8591 | 376.816 | 378.1704 | 377.0081 | 376.334 | 376.3874 | 376.6089 | 377.3972 | 376.5607 | 376.067 | 377.8738 | 375.5023 | 377.1144 | 385.2007 | 385.8763 | 385.6395 | 377.9299 | 378.2784 | 375.522 | 381.5492 | 380.4007 | 380.6953 | 378.4195 | 378.381 | 377.9886 | 379.1902 | 380.4515 | 379.6748 | 388.3934 | 387.6425 | 387.5642 | 386.1824 | 385.7353 | 386.064 | 385.3956 | 386.3858 | 387.1795 | 393.0236 | 391.7246 | 393.1274 | 392.8652 | 391.8794 | 392.5566 | 388.8506 | 386.3064 | 387.4751 | 388.7902 | 387.4941 | 388.4305 | 377.1754 | 378.5501 | 377.6105 | 377.6129 | 378.8078 | 377.4156 | 375.1075 | 375.1915 | 375.0409 | 385.1267 | 385.8653 | 384.0839 | 389.409 | 390.002 | 390.1587 | 377.7938 | 378.6241 | 378.7119 | 378.1399 | 378.0881 | 378.6528 | 390.7939 | 390.9431 | 390.6616 | 390.236 | 390.7692 | 391.3252 | 391.122 | 390.728 | 391.4075 | 390.6681 | 391.7038 | 391.3223 | 388.8563 | 388.5456 | 389.3978 | 389.0002 | 388.4378 | 387.9814 | 388.5136 | 388.1125 | 387.9954 | 390.33 | 390.051 | 390.4805 | 381.1677 | 380.4558 | 380.4967 | 380.3591 | 380.7927 | 380.0731 | 375.4501 | 376.389 | 376.0446 | 375.6615 | 376.2504 | 376.1259 | 376.1691 | 376.0052 | 375.3262 | 375.6626 | 375.8416 | 375.6775 | 378.3147 | 377.8954 | 377.5746 | 386.0108 | 384.6071 | 385.6502 | 385.3656 | 385.7824 | 385.398
382 | Compressor Type |  | 385.735 | 385.1328 | 384.3926 | 383.1533 | 386.387 | 386.29 | 393.3895 | 393.2566 | 392.8126 | 392.4107 | 392.1945 | 392.5252 | 392.59 | 391.3191 | 391.7668 | 392.815 | 393.0038 | 392.2923 | 391.7883 | 392.8479 | 393.6353 | 391.1621 | 391.4827 | 391.6231 | 394.8878 | 395.919 | 395.5744 | 395.6564 | 395.4878 | 395.7836 | 386.4995 | 387.2161 | 386.209 | 383.9177 | 383.451 | 383.5436 | 380.266 | 387.0678 | 387.1141 | 386.715 | 388.3051 | 388.6003 | 386.9339 | 388.0573 | 386.8793 | 386.1083 | 387.2325 | 387.2848 | 387.661 | 387.3199 | 389.1295 | 389.3866 | 388.0535 | 387.9746 | 386.0808 | 390.3037 | 393.3854 | 384.4915 | 382.6445 | 387.1941 | 388.041 | 386.3311 | 385.9894 | 392.2217 | 392.497 | 393.0242 | 393.0669 | 392.8805 | 392.1883 | 392.9397 | 392.9462 | 385.4534 | 385.9318 | 385.4666 | 391.3109 | 392.0096 | 392.3896 | 391.8893 | 391.1028 | 391.6318 | 391.0598 | 389.1586 | 388.2585 | 388.0193 | 391.5457 | 391.7004 | 391.6513 | 391.6281 | 394.1862 | 394.0377 | 394.0753 | 393.7108 | 390.3849 | 390.0565 | 390.0321 | 387.9602 | 387.6589 | 386.748 | 391.1575 | 391.2625 | 391.8539 | 391.0021 | 390.918 | 390.7022 | 390.0443 | 390.6852 | 386.2664 | 387.7201 | 386.4187 | 385.6258 | 386.2263 | 386.3082 | 385.8322 | 386.313 | 386.077 | 387.1243 | 384.8367 | 385.8713 | 389.9212 | 390.6934 | 390.4132 | 388.0284 | 387.7968 | 385.5854 | 391.2403 | 390.3618 | 390.6406 | 388.0632 | 387.6086 | 388.1396 | 388.5059 | 389.1731 | 388.4681 | 392.7734 | 392.2895 | 392.4039 | 389.1583 | 388.4236 | 388.9763 | 386.8425 | 387.427 | 388.3141 | 394.2373 | 392.8414 | 394.1276 | 394.1279 | 393.7126 | 393.8521 | 384.4383 | 382.4084 | 382.4591 | 380.6678 | 380.8088 | 380.7841 | 385.9788 | 388.4112 | 386.6851 | 387.3548 | 388.1031 | 385.9949 | 383.6124 | 383.9015 | 383.8327 | 393.0576 | 393.307 | 392.1948 | 393.6078 | 394.125 | 393.3839 | 387.068 | 387.3742 | 387.6238 | 387.2894 | 387.2281 | 387.8787 | 394.4284 | 394.9185 | 394.3318 | 391.5428 | 392.2126 | 392.3051 | 392.1862 | 392.4463 | 393.1044 | 392.0617 | 392.7169 | 391.9505 | 393.0471 | 392.4918 | 393.485 | 391.1986 | 389.6418 | 390.5072 | 384.7327 | 384.0511 | 383.9133 | 382.5064 | 382.5863 | 383.3703 | 390.3917 | 389.8806 | 389.5439 | 389.6052 | 390.4742 | 389.9022 | 384.466 | 385.0862 | 385.1826 | 384.8484 | 385.9821 | 385.1639 | 385.4979 | 384.6889 | 384.8355 | 384.3029 | 384.8881 | 384.7271 | 386.7691 | 387.0174 | 386.7713 | 389.764 | 389.2766 | 389.8944 | 389.5468 | 390.1634 | 389.7628
383 | Compressor ID |  | 393.9749 | 393.4142 | 392.2578 | 390.9904 | 394.8124 | 394.7076 | 392.6014 | 392.91 | 392.6588 | 391.0334 | 390.9886 | 390.7425 | 391.3545 | 389.3866 | 390.6586 | 394.0321 | 394.265 | 393.2913 | 392.836 | 394.2957 | 394.9097 | 389.1173 | 388.9279 | 389.3839 | 393.8973 | 394.2282 | 394.0718 | 394.6437 | 394.13 | 394.9829 | 394.5494 | 394.8925 | 393.8838 | 392.0005 | 392.5687 | 392.052 | 388.3751 | 381.3617 | 382.4113 | 380.4896 | 383.0838 | 382.5013 | 382.6371 | 382.0497 | 381.9776 | 382.4868 | 383.7468 | 384.1285 | 383.8503 | 385.13 | 385.1713 | 385.1044 | 383.2865 | 383.0254 | 381.8683 | 386.4217 | 387.2332 | 392.6136 | 391.3571 | 394.3681 | 395.2393 | 393.9332 | 393.6915 | 390.1962 | 390.1006 | 390.6992 | 393.2138 | 392.9273 | 392.4963 | 393.7762 | 393.3405 | 393.7981 | 393.7752 | 393.8197 | 389.7375 | 389.7364 | 390.5642 | 389.8905 | 390.2445 | 390.8649 | 390.3955 | 388.7134 | 387.4984 | 387.3201 | 392.7039 | 393.0231 | 392.7546 | 392.6679 | 389.1196 | 386.8175 | 386.186 | 386.4724 | 386.8192 | 384.3913 | 384.1288 | 383.4532 | 381.8725 | 383.0827 | 387.6346 | 385.6198 | 386.3508 | 385.4752 | 384.74 | 385.4522 | 384.3005 | 384.2383 | 384.4596 | 384.53 | 382.136 | 382.6006 | 380.7853 | 382.1909 | 381.5777 | 382.6405 | 382.0448 | 382.3062 | 379.0173 | 380.6895 | 389.8078 | 390.872 | 390.9857 | 385.1261 | 386.0327 | 383.0533 | 387.1915 | 386.4386 | 385.0125 | 385.0146 | 384.1147 | 383.7226 | 384.1563 | 382.2769 | 383.7354 | 392.2608 | 391.4256 | 392.2731 | 386.9452 | 386.1435 | 386.5744 | 384.1817 | 385.0788 | 386.017 | 394.5173 | 393.1307 | 394.3738 | 394.4861 | 393.8972 | 394.4909 | 392.2379 | 389.9401 | 390.2834 | 388.3575 | 388.4059 | 388.4544 | 383.8016 | 384.6028 | 384.0892 | 383.3555 | 384.4915 | 384.8742 | 380.9635 | 380.8886 | 381.7089 | 386.5121 | 386.6692 | 386.2132 | 392.8599 | 393.3441 | 392.0817 | 383.3045 | 384.9562 | 384.4667 | 385.0195 | 384.72 | 386.0963 | 393.5642 | 394.1342 | 393.4664 | 391.6559 | 392.2469 | 392.5896 | 392.1597 | 392.0434 | 392.6248 | 392.5512 | 393.2515 | 392.6169 | 391.3721 | 390.5262 | 392.1206 | 388.3649 | 387.1652 | 387.8743 | 392.0636 | 391.4456 | 391.5766 | 389.878 | 390.4479 | 391.4321 | 384.7912 | 384.8364 | 384.1166 | 383.666 | 384.3897 | 383.7888 | 380.3766 | 379.2928 | 382.8506 | 382.7148 | 382.0615 | 379.8943 | 379.9744 | 381.5645 | 380.7676 | 383.5368 | 382.2668 | 381.3159 | 381.255 | 381.2449 | 381.4081 | 388.6539 | 388.3981 | 388.2902 | 387.9699 | 388.9746 | 388.2922
384 | Compressor Size |  | 391.2808 | 391.6155 | 390.5056 | 391.4287 | 393.5194 | 393.2478 | 389.2656 | 388.8925 | 388.3023 | 388.5757 | 388.3694 | 388.6977 | 388.6993 | 387.3777 | 388.3758 | 392.0933 | 392.26 | 391.281 | 391.1024 | 392.7999 | 392.9307 | 389.6655 | 389.4943 | 389.5616 | 392.2081 | 392.6364 | 392.5833 | 391.8213 | 391.5823 | 391.8355 | 390.504 | 389.7223 | 390.6406 | 390.1956 | 391.4757 | 389.4873 | 388.5945 | 378.2448 | 378.4693 | 378.7195 | 380.1138 | 379.8886 | 378.0668 | 379.1275 | 377.8041 | 377.9981 | 378.4664 | 378.1517 | 378.7359 | 378.3372 | 379.3531 | 380.1629 | 379.5038 | 378.6259 | 376.8959 | 380.4741 | 383.6371 | 389.4464 | 388.6583 | 390.8068 | 391.7011 | 390.6139 | 392.7518 | 390.3921 | 391.5788 | 391.7321 | 392.6519 | 391.7614 | 391.829 | 392.9538 | 392.1305 | 392.1866 | 391.8255 | 391.5054 | 388.5952 | 389.0021 | 389.4646 | 388.8311 | 387.4098 | 388.0265 | 387.5187 | 385.4316 | 384.5835 | 384.5211 | 392.9779 | 392.6905 | 392.4282 | 392.4696 | 384.3642 | 385.4394 | 385.7145 | 384.8034 | 381.5387 | 381.4186 | 380.8696 | 379.7609 | 380.144 | 378.1388 | 381.3724 | 382.0777 | 382.6908 | 382.0544 | 383.4097 | 383.0437 | 382.4328 | 383.8591 | 376.816 | 378.1704 | 377.0081 | 376.334 | 376.3874 | 376.6089 | 377.3972 | 376.5607 | 376.067 | 377.8738 | 375.5023 | 377.1144 | 385.2007 | 385.8763 | 385.6395 | 377.9299 | 378.2784 | 375.522 | 381.5492 | 380.4007 | 380.6953 | 378.4195 | 378.381 | 377.9886 | 379.1902 | 380.4515 | 379.6748 | 388.3934 | 387.6425 | 387.5642 | 386.1824 | 385.7353 | 386.064 | 385.3956 | 386.3858 | 387.1795 | 393.0236 | 391.7246 | 393.1274 | 392.8652 | 391.8794 | 392.5566 | 388.8506 | 386.3064 | 387.4751 | 388.7902 | 387.4941 | 388.4305 | 377.1754 | 378.5501 | 377.6105 | 377.6129 | 378.8078 | 377.4156 | 375.1075 | 375.1915 | 375.0409 | 385.1267 | 385.8653 | 384.0839 | 389.409 | 390.002 | 390.1587 | 377.7938 | 378.6241 | 378.7119 | 378.1399 | 378.0881 | 378.6528 | 390.7939 | 390.9431 | 390.6616 | 390.236 | 390.7692 | 391.3252 | 391.122 | 390.728 | 391.4075 | 390.6681 | 391.7038 | 391.3223 | 388.8563 | 388.5456 | 389.3978 | 389.0002 | 388.4378 | 387.9814 | 388.5136 | 388.1125 | 387.9954 | 390.33 | 390.051 | 390.4805 | 381.1677 | 380.4558 | 380.4967 | 380.3591 | 380.7927 | 380.0731 | 375.4501 | 376.389 | 376.0446 | 375.6615 | 376.2504 | 376.1259 | 376.1691 | 376.0052 | 375.3262 | 375.6626 | 375.8416 | 375.6775 | 378.3147 | 377.8954 | 377.5746 | 386.0108 | 384.6071 | 385.6502 | 385.3656 | 385.7824 | 385.398
385 | VR |  | 197.2947 | 195.4498 | 197.3222 | 211.1828 | 208.877 | 210.4298 | 107.5964 | 106.9401 | 105.8934 | 100.6003 | 100.9459 | 101.1183 | 100.8844 | 101.1716 | 100.58 | 41.196 | 41.9138 | 40.9422 | 44.0314 | 43.6532 | 44.268 | 100.0473 | 100.38 | 98.9103 | 104.9581 | 104.3297 | 104.139 | 106.6916 | 106.7099 | 105.8669 | 199.0384 | 201.7561 | 201.35 | 208.8348 | 210.6616 | 208.1948 | 208.9447 | 367.1387 | 366.6719 | 369.4891 | 366.4696 | 366.1901 | 369.475 | 367.8917 | 371.4444 | 410.3301 | 409.7719 | 405.7678 | 403.7374 | 406.6094 | 411.0409 | 401.9374 | 404.1312 | 401.8522 | 402.7253 | 404.2369 | 399.5616 | 193.9173 | 195.5197 | 193.944 | 194.6697 | 197.6336 | 194.3211 | 98.5969 | 98.2443 | 97.7495 | 42.4155 | 41.7892 | 42.6723 | 44.2199 | 43.9915 | 208.5746 | 204.8336 | 208.2424 | 104.0913 | 105.5597 | 105.3829 | 104.5507 | 107.3508 | 107.072 | 106.3972 | 106.4333 | 108.8735 | 107.9682 | 44.8417 | 44.1796 | 43.6032 | 44.4289 | 359.6462 | 360.3393 | 359.8021 | 360.1237 | 399.3037 | 401.4624 | 403.23 | 397.5884 | 398.5031 | 398.1938 | 403.9355 | 401.7544 | 400.4796 | 401.166 | 395.7559 | 398.2029 | 397.6313 | 393.9594 | 399.9829 | 400.6167 | 402.3714 | 403.8621 | 407.6304 | 410.6779 | 402.6581 | 403.8256 | 405.5116 | 364.8774 | 367.6853 | 365.4373 | 104.3809 | 104.141 | 102.6989 | 405.2731 | 405.2249 | 406.6244 | 398.846 | 400.5182 | 398.1597 | 403.2951 | 406.8945 | 403.5141 | 363.4616 | 361.5596 | 364.7188 | 106.2106 | 105.6429 | 103.9087 | 105.7443 | 105.7645 | 106.3692 | 100.2501 | 100.0857 | 99.2755 | 41.9809 | 42.1843 | 41.7606 | 44.2636 | 44.2237 | 43.6761 | 196.7158 | 198.2908 | 197.806 | 208.0993 | 208.3936 | 209.2083 | 401.1018 | 395.487 | 399.3512 | 402.4721 | 400.7401 | 398.0508 | 402.9233 | 399.3172 | 403.7615 | 359.0219 | 355.6795 | 354.856 | 106.6884 | 106.7749 | 106.9056 | 401.6338 | 405.6702 | 401.1818 | 405.4443 | 407.9586 | 403.714 | 107.3967 | 107.2267 | 106.3671 | 44.8991 | 45.2321 | 44.9381 | 41.996 | 42.841 | 43.2237 | 43.9768 | 44.5702 | 44.6677 | 103.4281 | 104.0729 | 103.2904 | 100.4015 | 101.0392 | 99.6232 | 196.1969 | 195.4483 | 193.7607 | 209.1946 | 212.0086 | 208.8158 | 402.6211 | 400.4607 | 399.2563 | 402.3312 | 400.3928 | 403.6392 | 402.5703 | 403.0808 | 404.0941 | 407.3103 | 404.4139 | 403.8514 | 409.7925 | 408.1666 | 407.7058 | 404.8136 | 413.9249 | 410.1725 | 368.0884 | 367.9907 | 365.9418 | 106.9666 | 105.6953 | 108.5539 | 108.4911 | 107.4811 | 107.7953
386 | Motor Size |  | 198.6702 | 199.0956 | 198.8477 | 213.0151 | 212.7122 | 212.6876 | 106.8506 | 108.5871 | 108.1186 | 100.6098 | 100.3306 | 101.1104 | 100.4599 | 101.196 | 100.4843 | 40.4575 | 41.5605 | 41.8341 | 43.2225 | 42.1086 | 44.0294 | 96.7844 | 97.7352 | 97.8312 | 103.5112 | 103.1312 | 104.5794 | 106.6256 | 107.0409 | 106.6489 | 203.3994 | 200.8406 | 203.0793 | 218.5591 | 212.8844 | 218.5082 | 213.8986 | 376.0741 | 374.7724 | 374.1692 | 374.5448 | 375.9294 | 378.0917 | 373.1916 | 373.0183 | 417.7165 | 418.0971 | 415.3696 | 408.9479 | 414.5864 | 415.5608 | 407.6325 | 408.5392 | 404.5109 | 402.5404 | 407.6571 | 398.3239 | 193.5027 | 194.1531 | 193.5975 | 195.0374 | 194.955 | 196.6561 | 95.6895 | 94.2544 | 95.2375 | 40.6576 | 40.0611 | 40.6095 | 42.6161 | 42.5085 | 212.0752 | 214.1322 | 211.9313 | 102.4169 | 103.498 | 104.5391 | 103.5562 | 106.6613 | 106.6509 | 106.4423 | 108.6787 | 109.6532 | 109.6073 | 42.2657 | 42.6891 | 42.9878 | 42.0057 | 360.675 | 362.6841 | 361.0677 | 361.5934 | 401.3242 | 401.2519 | 404.2058 | 400.6199 | 403.5039 | 406.406 | 405.4187 | 402.1727 | 400.6845 | 405.5304 | 399.7079 | 400.6594 | 397.746 | 397.3638 | 409.7689 | 408.4648 | 408.2861 | 408.4448 | 412.7133 | 411.8164 | 408.4937 | 407.3052 | 406.1302 | 373.5324 | 373.2789 | 373.7141 | 109.3896 | 110.8564 | 110.6567 | 408.3448 | 407.8336 | 408.4459 | 403.2173 | 404.5591 | 402.7563 | 409.642 | 410.0972 | 405.764 | 368.2458 | 366.5143 | 367.0172 | 107.0224 | 107.3984 | 107.3946 | 104.5636 | 103.2648 | 103.713 | 97.6098 | 97.4012 | 97.9645 | 41.9747 | 41.1678 | 41.5665 | 43.634 | 44.1199 | 43.9461 | 196.3658 | 201.0224 | 198.5457 | 216.4825 | 214.8778 | 212.9872 | 408.5803 | 401.9716 | 405.7374 | 409.0298 | 404.5637 | 407.0818 | 408.4728 | 406.1868 | 407.5453 | 362.8136 | 364.6181 | 360.7411 | 109.0842 | 108.8817 | 107.3377 | 408.0427 | 413.5165 | 406.282 | 414.4395 | 413.8753 | 411.3238 | 106.4594 | 107.2851 | 105.1669 | 44.0703 | 44.5547 | 44.0162 | 41.8858 | 42.0277 | 41.5881 | 44.053 | 43.376 | 43.7578 | 105.4862 | 105.2516 | 104.8382 | 97.9059 | 98.8856 | 98.6131 | 199.1936 | 199.2811 | 193.5825 | 216.7012 | 215.9021 | 215.7022 | 405.6433 | 404.2145 | 403.5219 | 405.4472 | 404.9515 | 408.5098 | 406.8893 | 408.263 | 407.0509 | 411.3346 | 407.2196 | 409.9289 | 409.1643 | 412.7852 | 410.9548 | 411.3275 | 417.8131 | 412.5074 | 369.6771 | 371.0632 | 369.9217 | 107.513 | 108.6321 | 105.969 | 107.5645 | 108.5956 | 107.0371
387 | Motor ID |  | 198.6858 | 196.5078 | 198.3565 | 208.2475 | 207.9318 | 205.3157 | 114.8394 | 115.4956 | 115.3265 | 105.4149 | 105.8118 | 105.7619 | 106.5637 | 105.523 | 106.4277 | 43.0202 | 43.9333 | 43.7925 | 46.3432 | 45.8141 | 46.4298 | 103.444 | 103.2821 | 103.8839 | 112.8296 | 109.581 | 111.4662 | 115.7532 | 115.2437 | 115.8268 | 202.926 | 197.9886 | 197.1766 | 210.2579 | 211.3018 | 210.9482 | 207.2708 | 382.1381 | 382.3322 | 382.2426 | 380.3893 | 381.0325 | 379.596 | 377.4726 | 382.7531 | 419.7683 | 419.9897 | 419.3864 | 415.2794 | 419.1771 | 421.2502 | 412.9662 | 415.6606 | 411.067 | 409.0878 | 413.2569 | 409.0923 | 194.5562 | 194.0718 | 192.1757 | 193.1728 | 194.2406 | 193.6759 | 101.5948 | 101.4753 | 101.95 | 45.1977 | 44.2658 | 44.9619 | 47.2288 | 45.6918 | 206.4048 | 208.3821 | 207.6377 | 109.7312 | 108.5938 | 111.418 | 111.6057 | 117.0289 | 117.0718 | 117.5792 | 118.2015 | 117.4265 | 118.7652 | 46.6779 | 46.9874 | 46.6503 | 45.8407 | 370.4674 | 371.1904 | 369.545 | 367.5979 | 409.0742 | 411.7742 | 413.4091 | 410.0592 | 409.8034 | 408.9916 | 412.9295 | 410.6845 | 411.023 | 411.1498 | 410.317 | 412.18 | 409.9423 | 411.1288 | 411.7937 | 409.6749 | 413.5101 | 412.5161 | 417.0324 | 417.5754 | 414.3751 | 408.7112 | 410.6759 | 376.8148 | 375.249 | 375.9045 | 114.9691 | 113.116 | 112.1962 | 411.8212 | 412.9598 | 410.2328 | 407.0776 | 405.5102 | 408.1494 | 414.9767 | 414.1667 | 412.1024 | 373.7148 | 373.1971 | 371.5716 | 112.1357 | 113.7607 | 112.0673 | 109.5875 | 108.6506 | 109.4506 | 102.3868 | 102.0043 | 102.3327 | 45.3689 | 44.4895 | 44.5868 | 46.2517 | 46.259 | 46.4724 | 194.1053 | 198.2338 | 197.0615 | 211.5869 | 208.4117 | 209.7799 | 411.5932 | 404.3425 | 409.9918 | 415.2467 | 409.9733 | 407.3631 | 413.3945 | 412.0783 | 412.8414 | 368.4577 | 369.1425 | 368.5876 | 115.024 | 115.579 | 114.4309 | 413.1285 | 416.0854 | 408.6791 | 417.7939 | 419.5932 | 416.514 | 114.5974 | 113.6657 | 113.554 | 46.7452 | 46.6715 | 46.7744 | 45.3876 | 44.5095 | 43.4463 | 45.6315 | 45.2585 | 47.2402 | 108.8572 | 107.09 | 107.446 | 101.5661 | 103.7026 | 102.3476 | 195.0478 | 194.9329 | 192.0004 | 213.5894 | 209.5786 | 215.3414 | 412.3854 | 410.9706 | 410.3677 | 415.0627 | 411.7228 | 415.3098 | 414.8839 | 413.8953 | 415.3515 | 416.2498 | 412.5535 | 414.8082 | 416.1111 | 413.2616 | 416.4615 | 413.0898 | 419.6893 | 421.1912 | 375.5553 | 374.1532 | 372.9978 | 114.2899 | 114.9609 | 111.2436 | 112.6181 | 112.612 | 113.094
388 | Test Operator |  | 119.4992 | 118.79 | 119.4309 | 127.5683 | 128.006 | 127.5888 | 59.1581 | 59.7945 | 59.2685 | 54.1841 | 53.9606 | 54.4708 | 54.5679 | 54.1843 | 54.205 | 19.3043 | 19.9726 | 19.6288 | 20.6619 | 20.0945 | 21.2378 | 52.6734 | 52.8096 | 52.7737 | 57.2978 | 56.5406 | 57.2907 | 59.5372 | 59.1441 | 59.3426 | 122.3535 | 121.1635 | 121.5595 | 128.6453 | 128.3336 | 128.7511 | 126.3583 | 229.86 | 229.8192 | 229.788 | 229.7588 | 230.2063 | 230.3415 | 228.8473 | 230.1678 | 255.5948 | 256.0513 | 254.6313 | 252.0243 | 254.8569 | 257.0034 | 251.7677 | 252.3911 | 249.7002 | 248.1303 | 253.0356 | 250.7873 | 116.0362 | 116.253 | 116.5996 | 117.7818 | 117.9755 | 117.775 | 52.2129 | 51.8846 | 51.9135 | 19.3076 | 18.9079 | 19.4552 | 20.8503 | 19.9527 | 126.2066 | 126.4329 | 126.5345 | 55.8506 | 56.3042 | 57.0558 | 56.9312 | 59.386 | 59.4363 | 59.0296 | 59.8121 | 60.4708 | 60.3824 | 20.7578 | 20.9116 | 20.5648 | 20.537 | 226.7017 | 227.1654 | 226.3685 | 225.8979 | 250.1444 | 250.5474 | 251.8222 | 247.958 | 248.6345 | 248.3697 | 253.0415 | 251.1063 | 250.9324 | 251.6663 | 249.521 | 250.653 | 248.8685 | 248.8877 | 249.8527 | 250.2379 | 250.1678 | 250.0491 | 252.4685 | 253.5992 | 250.4028 | 249.5629 | 249.7189 | 227.605 | 226.5059 | 227.0164 | 59.1048 | 58.9568 | 58.5944 | 251.6153 | 252.1751 | 250.4415 | 250.3699 | 250.0738 | 249.3838 | 252.2843 | 252.7251 | 250.7308 | 226.7294 | 225.7125 | 226.1696 | 58.7229 | 58.9279 | 58.1343 | 56.0385 | 55.5897 | 56.3449 | 51.8491 | 52.0769 | 51.9873 | 19.7068 | 19.8131 | 19.7217 | 20.5707 | 21.0419 | 20.5815 | 117.4799 | 118.1851 | 117.2627 | 127.4955 | 126.3336 | 126.6961 | 249.9693 | 246.878 | 248.761 | 251.2586 | 249.6893 | 248.3999 | 248.9689 | 247.7815 | 249.3591 | 225.4875 | 225.4563 | 223.8227 | 58.3426 | 59.0402 | 58.3082 | 250.4776 | 253.801 | 249.7197 | 254.0856 | 254.7866 | 252.6337 | 58.8955 | 58.5624 | 58.1529 | 20.9593 | 21.0495 | 20.6696 | 19.3961 | 19.6168 | 19.3655 | 20.7379 | 20.5422 | 20.5998 | 55.9822 | 55.5058 | 55.5622 | 52.4554 | 52.7361 | 52.1904 | 117.6301 | 117.1262 | 114.9977 | 128.3149 | 127.7376 | 128.5979 | 251.7195 | 250.0775 | 249.4836 | 251.5394 | 250.8161 | 252.39 | 249.0566 | 249.3972 | 250.1434 | 252.0137 | 249.9096 | 250.0278 | 251.8127 | 251.4453 | 251.3258 | 250.6854 | 255.1167 | 253.356 | 227.1958 | 226.7404 | 226.0356 | 58.4112 | 58.8934 | 58.5261 | 58.7867 | 58.6631 | 58.7514
389 | Text |  | 121.0052 | 120.3011 | 121.0052 | 129.2498 | 129.6764 | 129.3082 | 59.896 | 60.5904 | 59.9891 | 54.8808 | 54.6528 | 55.1598 | 55.2447 | 54.8844 | 54.9074 | 19.3043 | 19.9726 | 19.6288 | 20.6619 | 20.0945 | 21.2378 | 53.3917 | 53.5965 | 53.4939 | 58.0551 | 57.343 | 58.0521 | 60.2698 | 59.5153 | 60.0978 | 123.8604 | 122.6675 | 123.1013 | 130.2757 | 130.0259 | 130.4278 | 128.0659 | 233.3126 | 233.1979 | 233.3763 | 233.2087 | 233.7648 | 233.7109 | 232.3788 | 233.665 | 259.8334 | 260.2949 | 258.7534 | 256.1062 | 258.9574 | 261.2513 | 255.8256 | 256.6155 | 253.7489 | 252.1496 | 257.1688 | 254.8527 | 117.4686 | 117.7043 | 117.9701 | 119.1463 | 119.4082 | 119.2404 | 52.8883 | 52.5699 | 52.6022 | 19.3076 | 18.9079 | 19.4552 | 20.8503 | 19.9527 | 127.9084 | 128.1674 | 128.222 | 56.6457 | 57.1396 | 57.8228 | 57.7325 | 60.1257 | 60.1361 | 59.7488 | 60.5038 | 61.2534 | 61.1388 | 20.7578 | 20.9116 | 20.5648 | 20.537 | 230.0805 | 230.7365 | 229.9608 | 229.4551 | 254.0111 | 254.6045 | 256.0167 | 251.9009 | 252.7801 | 252.3068 | 256.9721 | 255.2648 | 254.8903 | 255.6355 | 253.5096 | 254.5253 | 252.7785 | 252.8513 | 253.6246 | 254.2038 | 254.2623 | 253.9183 | 256.7501 | 257.7773 | 254.4604 | 253.5835 | 253.7932 | 230.9585 | 230.0722 | 230.391 | 59.794 | 59.6766 | 59.3078 | 255.791 | 256.2965 | 254.5574 | 254.4336 | 254.1602 | 253.5396 | 256.361 | 256.8544 | 254.819 | 230.0892 | 229.2124 | 229.5441 | 59.4338 | 59.6337 | 58.9141 | 56.8184 | 56.3691 | 57.0827 | 52.5802 | 52.7512 | 52.6716 | 19.7068 | 19.8131 | 19.7217 | 20.5707 | 21.0419 | 20.5815 | 118.9043 | 119.7305 | 118.8477 | 129.1187 | 127.9567 | 128.3392 | 253.8509 | 250.6833 | 252.5093 | 255.214 | 253.5668 | 252.1986 | 252.9578 | 251.668 | 253.2047 | 228.8341 | 228.8026 | 227.0325 | 59.0824 | 59.7982 | 59.0778 | 254.5256 | 257.9491 | 253.7417 | 258.0413 | 258.8129 | 256.5197 | 59.6794 | 59.3391 | 58.9123 | 20.9593 | 21.0495 | 20.6696 | 19.3961 | 19.6168 | 19.3655 | 20.7379 | 20.5422 | 20.5998 | 56.7506 | 56.3085 | 56.3237 | 53.1414 | 53.4341 | 52.8411 | 119.2301 | 118.6714 | 116.4805 | 130.037 | 129.5437 | 130.3497 | 255.8562 | 254.1225 | 253.5172 | 255.6666 | 254.9997 | 256.5547 | 253.0146 | 253.5153 | 254.1274 | 255.9599 | 253.9582 | 254.225 | 256.0091 | 255.5231 | 255.4144 | 254.5846 | 259.2486 | 257.4258 | 230.6366 | 230.2307 | 229.4967 | 59.1999 | 59.5955 | 59.3007 | 59.5332 | 59.4537 | 59.5235
390 | Test Purpose |  | 19.032 | 19.0082 | 19.4554 | 20.7812 | 20.7471 | 21.0164 | 9.373 | 9.7882 | 9.2703 | 8.7169 | 8.6712 | 8.6908 | 8.621 | 8.7384 | 8.7546 | 0 | 0 | 0 | 0 | 0 | 0 | 8.7283 | 9.1502 | 8.7481 | 9.3462 | 9.5597 | 9.3716 | 9.3689 | 9.3576 | 9.4977 | 19.262 | 19.1504 | 19.422 | 20.5461 | 20.9097 | 20.8459 | 20.8441 | 39.989 | 39.5525 | 40.7667 | 39.965 | 40.633 | 39.5423 | 40.3588 | 40.2756 | 46.741 | 46.8097 | 46.0019 | 45.543 | 45.9009 | 46.9203 | 45.3846 | 46.3708 | 45.1479 | 44.8417 | 45.9216 | 45.3388 | 18.289 | 18.4269 | 17.9298 | 17.98 | 18.4419 | 18.6363 | 8.4253 | 8.4605 | 8.4842 | 0 | 0 | 0 | 0 | 0 | 20.7955 | 21.0143 | 20.7339 | 9.4574 | 9.7351 | 9.3871 | 9.5857 | 9.4023 | 9.1477 | 9.2421 | 9.1221 | 9.7599 | 9.5876 | 0 | 0 | 0 | 0 | 39.2855 | 40.4378 | 40.4877 | 40.2466 | 44.1523 | 45.271 | 46.1537 | 44.3946 | 45.5925 | 44.3982 | 44.7737 | 45.8883 | 44.7436 | 44.8728 | 44.7922 | 44.2288 | 44.288 | 44.5947 | 43.5784 | 44.7273 | 45.4465 | 44.1584 | 46.6933 | 46.2236 | 45.2605 | 44.9771 | 45.2928 | 39.215 | 40.3518 | 39.2882 | 9.052 | 9.2405 | 9.1707 | 46.0303 | 45.7782 | 45.591 | 45.2921 | 45.3932 | 45.7169 | 45.5365 | 45.8717 | 45.4621 | 39.1769 | 39.9022 | 39.2148 | 9.1655 | 9.1474 | 9.5534 | 9.3823 | 9.3415 | 9.1479 | 8.738 | 8.4077 | 8.4628 | 0 | 0 | 0 | 0 | 0 | 0 | 18.3492 | 19.1747 | 19.3451 | 20.4093 | 20.3158 | 20.4708 | 44.2223 | 43.5126 | 43.3465 | 44.7584 | 44.1745 | 43.6071 | 44.7455 | 44.0581 | 43.9624 | 38.9926 | 38.9886 | 38.0414 | 9.3208 | 9.4915 | 9.5044 | 45.2133 | 46.0739 | 44.9993 | 45.0093 | 45.4746 | 44.481 | 9.6409 | 9.5695 | 9.429 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.3072 | 9.4735 | 9.2305 | 8.5111 | 8.6085 | 8.267 | 19.4673 | 19.088 | 18.5263 | 21.0925 | 21.5558 | 21.2984 | 45.8221 | 45.1604 | 45.0433 | 45.753 | 46.0015 | 46.0392 | 44.578 | 45.5087 | 44.8223 | 44.7721 | 45.1659 | 46.0051 | 46.1627 | 45.4678 | 45.5173 | 44.386 | 46.1011 | 45.5934 | 39.6901 | 39.9366 | 39.7068 | 9.631 | 9.1205 | 9.5533 | 9.3987 | 9.6633 | 9.556
391 | Refrigerant |  | 0.98755 | 0.98744 | 0.98699 | 0.98699 | 0.98712 | 0.9867 | 0.98768 | 0.98686 | 0.98799 | 0.9873 | 0.98733 | 0.98751 | 0.98775 | 0.98724 | 0.98721 | 1 | 1 | 1 | 1 | 1 | 1 | 0.98655 | 0.98532 | 0.98654 | 0.98696 | 0.98601 | 0.98688 | 0.98784 | 0.98756 | 0.98743 | 0.98783 | 0.98774 | 0.98748 | 0.98748 | 0.98699 | 0.98715 | 0.98667 | 0.9852 | 0.98551 | 0.98462 | 0.98521 | 0.98478 | 0.98558 | 0.9848 | 0.98503 | 0.98369 | 0.9837 | 0.98407 | 0.98406 | 0.98416 | 0.98374 | 0.98414 | 0.98354 | 0.98404 | 0.98406 | 0.98393 | 0.98405 | 0.98781 | 0.98767 | 0.98838 | 0.98855 | 0.988 | 0.98771 | 0.98723 | 0.98696 | 0.98691 | 1 | 1 | 1 | 1 | 1 | 0.98669 | 0.98647 | 0.98684 | 0.98596 | 0.98538 | 0.98673 | 0.98612 | 0.9877 | 0.98836 | 0.98796 | 0.98857 | 0.98722 | 0.98763 | 1 | 1 | 1 | 1 | 0.98532 | 0.98452 | 0.98438 | 0.9845 | 0.98478 | 0.98406 | 0.98362 | 0.98435 | 0.9836 | 0.9844 | 0.9847 | 0.98371 | 0.98447 | 0.98447 | 0.98427 | 0.98479 | 0.98453 | 0.98432 | 0.98513 | 0.9844 | 0.9839 | 0.98476 | 0.98332 | 0.98379 | 0.98405 | 0.98415 | 0.98395 | 0.98548 | 0.9845 | 0.98535 | 0.98847 | 0.98794 | 0.98797 | 0.98367 | 0.98392 | 0.98383 | 0.98403 | 0.98392 | 0.98361 | 0.9841 | 0.98392 | 0.98396 | 0.9854 | 0.98473 | 0.9853 | 0.98804 | 0.98816 | 0.98677 | 0.98627 | 0.98617 | 0.98708 | 0.9861 | 0.98722 | 0.98701 | 1 | 1 | 1 | 1 | 1 | 1 | 0.98802 | 0.98709 | 0.98666 | 0.98743 | 0.98732 | 0.9872 | 0.98471 | 0.98482 | 0.98516 | 0.9845 | 0.98471 | 0.98494 | 0.98423 | 0.98456 | 0.98481 | 0.98538 | 0.98537 | 0.98586 | 0.98748 | 0.98732 | 0.98697 | 0.9841 | 0.98392 | 0.98415 | 0.98467 | 0.98444 | 0.98485 | 0.98686 | 0.98691 | 0.98711 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.98646 | 0.98574 | 0.98648 | 0.98709 | 0.98694 | 0.98769 | 0.98658 | 0.98698 | 0.98727 | 0.98676 | 0.98606 | 0.98656 | 0.98383 | 0.98408 | 0.98409 | 0.98386 | 0.98359 | 0.98377 | 0.98436 | 0.98376 | 0.98432 | 0.98458 | 0.98406 | 0.98349 | 0.98361 | 0.98404 | 0.98399 | 0.98468 | 0.98406 | 0.98419 | 0.98508 | 0.98484 | 0.98492 | 0.98668 | 0.98822 | 0.98694 | 0.98746 | 0.9867 | 0.98703
392 | Flowmeter Choice |  | 160727 | 160713 | 160705 | 160664 | 160657 | 160651 | 160567 | 160565 | 160561 | 160551 | 160549 | 160546 | 160541 | 160537 | 160535 | 160495 | 160494 | 160493 | 160479 | 160476 | 160472 | 160442 | 160439 | 160436 | 160416 | 160410 | 160407 | 160392 | 160389 | 160386 | 160315 | 160309 | 160304 | 160230 | 160223 | 160216 | 160105 | 160058 | 160054 | 160049 | 160012 | 160009 | 159997 | 159981 | 159948 | 159701 | 159688 | 159671 | 159574 | 159562 | 159549 | 159520 | 159502 | 159489 | 159281 | 159264 | 159251 | 159039 | 159035 | 159028 | 158982 | 158977 | 158972 | 158846 | 158843 | 158841 | 158774 | 158773 | 158772 | 158768 | 158766 | 158734 | 158727 | 158719 | 158603 | 158601 | 158599 | 158548 | 158527 | 158524 | 158521 | 158441 | 158437 | 158434 | 158369 | 158365 | 158364 | 158363 | 158325 | 158306 | 158295 | 158286 | 158108 | 158077 | 158062 | 157926 | 157906 | 157845 | 157122 | 157116 | 157091 | 157075 | 157040 | 157015 | 156992 | 156964 | 155590 | 155576 | 155564 | 155471 | 155458 | 155444 | 155425 | 155413 | 155401 | 155343 | 155322 | 155309 | 155111 | 155108 | 155104 | 154995 | 154972 | 154952 | 154859 | 154843 | 154831 | 154544 | 154528 | 154515 | 154480 | 154463 | 154448 | 154143 | 154141 | 154136 | 154045 | 154041 | 154034 | 154005 | 154001 | 153997 | 153953 | 153951 | 153950 | 153948 | 153945 | 153944 | 153876 | 153868 | 153860 | 153803 | 153796 | 153789 | 153498 | 153461 | 153439 | 153386 | 153374 | 153357 | 153320 | 153303 | 153283 | 152914 | 152907 | 152895 | 152678 | 152673 | 152670 | 152510 | 152493 | 152474 | 152425 | 152407 | 152388 | 152020 | 152016 | 152013 | 151929 | 151928 | 151927 | 151926 | 151925 | 151924 | 151922 | 151920 | 151919 | 151899 | 151897 | 151893 | 151845 | 151843 | 151840 | 151733 | 151727 | 151718 | 151674 | 151666 | 151658 | 151497 | 151483 | 151470 | 151436 | 151424 | 151393 | 151067 | 151053 | 151036 | 151021 | 151007 | 150994 | 150959 | 150946 | 150934 | 150908 | 150898 | 150882 | 150841 | 150830 | 150817 | 150616 | 150614 | 150611 | 150604 | 150600 | 150597
393 | Logging Interval T1 |  | 53537 | 53535 | 53534 | 53527 | 53526 | 53525 | 53512 | 53511 | 53511 | 53509 | 53509 | 53508 | 53507 | 53507 | 53506 | 53502 | 53502 | 53502 | 53502 | 53502 | 53502 | 53502 | 53501 | 53501 | 53497 | 53497 | 53496 | 53493 | 53493 | 53493 | 53482 | 53481 | 53480 | 53468 | 53467 | 53466 | 53448 | 53440 | 53440 | 53439 | 53432 | 53432 | 53430 | 53427 | 53421 | 53378 | 53376 | 53373 | 53355 | 53353 | 53351 | 53346 | 53342 | 53340 | 53305 | 53302 | 53299 | 53262 | 53261 | 53260 | 53253 | 53252 | 53251 | 53232 | 53231 | 53231 | 53222 | 53222 | 53222 | 53222 | 53222 | 53221 | 53220 | 53219 | 53200 | 53200 | 53199 | 53191 | 53187 | 53187 | 53186 | 53173 | 53173 | 53172 | 53162 | 53162 | 53162 | 53162 | 53161 | 53157 | 53155 | 53154 | 53123 | 53117 | 53114 | 53090 | 53086 | 53075 | 52950 | 52949 | 52945 | 52942 | 52936 | 52931 | 52927 | 52922 | 52683 | 52681 | 52678 | 52662 | 52660 | 52657 | 52654 | 52651 | 52649 | 52639 | 52635 | 52633 | 52599 | 52599 | 52598 | 52582 | 52577 | 52574 | 52557 | 52554 | 52552 | 52501 | 52498 | 52496 | 52490 | 52487 | 52484 | 52432 | 52431 | 52431 | 52417 | 52416 | 52415 | 52410 | 52409 | 52409 | 52402 | 52402 | 52402 | 52402 | 52402 | 52402 | 52396 | 52394 | 52393 | 52384 | 52383 | 52382 | 52336 | 52330 | 52326 | 52317 | 52314 | 52312 | 52305 | 52302 | 52298 | 52235 | 52234 | 52232 | 52196 | 52195 | 52194 | 52170 | 52167 | 52164 | 52155 | 52152 | 52148 | 52085 | 52084 | 52084 | 52071 | 52071 | 52071 | 52071 | 52071 | 52071 | 52071 | 52071 | 52071 | 52071 | 52070 | 52070 | 52062 | 52062 | 52061 | 52044 | 52043 | 52041 | 52034 | 52033 | 52031 | 52006 | 52004 | 52001 | 51995 | 51993 | 51987 | 51930 | 51928 | 51925 | 51922 | 51919 | 51917 | 51911 | 51908 | 51906 | 51902 | 51900 | 51897 | 51890 | 51888 | 51885 | 51851 | 51850 | 51850 | 51849 | 51848 | 51848
394 | Logging Interval T2 |  | 49.945 | 49.9392 | 49.9397 | 49.9102 | 50.0631 | 50.0327 | 50.0306 | 49.9723 | 49.9556 | 50.0876 | 49.9798 | 50.1305 | 50.0809 | 50.0327 | 49.9785 | 49.9705 | 49.9765 | 49.955 | 49.9433 | 49.9928 | 50.0868 | 49.926 | 49.9431 | 49.9604 | 49.8776 | 49.9252 | 49.9871 | 50.0405 | 50.0211 | 50.0631 | 50.0717 | 50.0511 | 50.0466 | 49.9605 | 49.9962 | 49.9993 | 50.0326 | 50.125 | 50.1317 | 50.0952 | 50.0735 | 50.0325 | 50.029 | 49.9764 | 50.0032 | 50.0087 | 50.0111 | 50.0476 | 49.9611 | 50.0178 | 50.0507 | 50.0536 | 49.9935 | 50.004 | 49.9297 | 50.0601 | 50.024 | 50.0575 | 50.0123 | 50.1775 | 50.108 | 50.0719 | 50.073 | 49.9657 | 49.961 | 50.0151 | 49.9395 | 49.9556 | 49.9676 | 49.948 | 49.8984 | 49.8999 | 49.8783 | 49.8943 | 50.0758 | 50.0657 | 50.0702 | 49.9924 | 50.0805 | 50.0579 | 50.0693 | 49.9713 | 49.9505 | 49.915 | 49.9437 | 49.9621 | 49.98 | 49.9866 | 50.112 | 50.1316 | 50.1773 | 50.1568 | 50.1493 | 50.1049 | 49.9818 | 49.9969 | 49.998 | 50.0716 | 49.9889 | 49.9143 | 49.9113 | 49.9202 | 49.942 | 49.9816 | 49.9231 | 50.0247 | 49.9589 | 50.0579 | 49.9014 | 50.1222 | 50.0678 | 50.1 | 50.087 | 50.0778 | 50.1147 | 49.9431 | 49.9257 | 49.9474 | 50.0748 | 50.0952 | 50.0442 | 49.9403 | 49.9936 | 49.981 | 50.0087 | 49.9202 | 49.926 | 50.0725 | 50.0518 | 50.0421 | 50.041 | 50.0088 | 50.0214 | 50.1845 | 50.1506 | 50.0839 | 50.0539 | 50.0693 | 50.0828 | 50.0186 | 50.1223 | 49.985 | 50.0648 | 50.0385 | 50.0368 | 49.9596 | 49.9304 | 49.9603 | 49.9857 | 49.9625 | 49.9219 | 49.9219 | 49.9521 | 49.8836 | 49.9773 | 50.0042 | 50.0267 | 49.9339 | 50.0298 | 49.9564 | 49.9121 | 49.9334 | 50.0116 | 49.9703 | 49.982 | 49.9802 | 49.948 | 50.0155 | 49.9794 | 50.0346 | 50.0662 | 50.0362 | 49.9878 | 50.0324 | 50.0491 | 50.1113 | 50.1294 | 50.1185 | 49.9954 | 50.0314 | 50.0429 | 49.9882 | 50.0369 | 50.0485 | 50.03 | 50.0481 | 50.0839 | 49.9332 | 49.9226 | 49.9453 | 50.0773 | 50.051 | 50.0067 | 50.0476 | 50.0158 | 50.0189 | 49.9512 | 50.0132 | 50.0495 | 50.0109 | 49.9134 | 49.858 | 49.9596 | 49.9528 | 49.8659 | 50.0627 | 50.0535 | 50.0911 | 50.0692 | 50.084 | 49.9586 | 49.9795 | 49.9591 | 49.9431 | 50.0596 | 49.9825 | 49.9975 | 49.9474 | 49.9906 | 49.9671 | 49.9524 | 49.9908 | 49.955 | 49.9652 | 49.99 | 49.9985
395 | V L1-2 |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
396 | V L2-3 |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
397 | V L3-1 |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
398 | V1 |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
399 | V2 |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
400 | V3 |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
401 | A1 |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
402 | A2 |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
403 | A3 |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
404 | kW Sum |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
405 | kVA Sum |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
406 | kVAR Sum |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
407 | PF Average |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
408 | kWHr |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
409 | kVAHr |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
410 | Hz |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
411 | T1 |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
412 | T2 |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
413 | T3 |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
414 | T4 |  | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1
415 | T5 |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
416 | T6 |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
417 | T7 |  | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2
418 | T8 |  | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2
419 | T9 |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
420 | T10 |  | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1
421 | T11 |  | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2
422 | T12 |  | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2
423 | T13 |  | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2
424 | T14 |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
425 | T15 |  | 69.993 | 69.994 | 70.005 | 74.997 | 74.996 | 75.004 | 45.003 | 45.005 | 44.995 | 40.006 | 39.997 | 40.002 | 40.001 | 40.006 | 39.999 | 18.997 | 18.997 | 19.005 | 19.992 | 19.993 | 20.009 | 40.004 | 39.998 | 39.999 | 42.993 | 43.003 | 43.004 | 43.007 | 42.997 | 42.998 | 70.998 | 70.993 | 70.998 | 74.999 | 74.999 | 74.998 | 74 | 110 | 110 | 110 | 110 | 109.99 | 110 | 110 | 110.01 | 120 | 120 | 120.01 | 120.01 | 120 | 120.02 | 120 | 120 | 119.99 | 120.01 | 120 | 120 | 69.002 | 68.984 | 68.991 | 69.999 | 69.989 | 70 | 40.004 | 40.002 | 40.001 | 18.997 | 19 | 18.995 | 20.01 | 20 | 75 | 75.002 | 74.99 | 43.004 | 43.001 | 43.003 | 42.992 | 45.002 | 44.999 | 45.005 | 45 | 44.99 | 44.995 | 20.008 | 20.006 | 19.997 | 19.996 | 110 | 110 | 110.02 | 110.02 | 120 | 120 | 120 | 119.99 | 120 | 120 | 119.99 | 120.01 | 119.98 | 119.99 | 119.99 | 120 | 120 | 120 | 120 | 119.99 | 120.01 | 120.01 | 120 | 120 | 120.01 | 119.99 | 119.99 | 109.98 | 110 | 110 | 45.005 | 45.001 | 44.994 | 119.99 | 120.01 | 120.01 | 120.01 | 120 | 120 | 120 | 120 | 120 | 110.01 | 110 | 110 | 44.998 | 45.006 | 45.002 | 43.001 | 43 | 43.001 | 40 | 40.003 | 39.993 | 18.996 | 18.999 | 19.004 | 19.996 | 19.998 | 20.01 | 71 | 70.999 | 71 | 76.007 | 75.996 | 76.004 | 119.99 | 120.01 | 120 | 120.01 | 120 | 120.01 | 120 | 120 | 119.99 | 110.01 | 110.01 | 110 | 44.999 | 45.002 | 44.998 | 119.99 | 120 | 119.98 | 119.99 | 120 | 119.99 | 45.003 | 44.996 | 45.003 | 20.001 | 20.004 | 20.007 | 19.003 | 19.01 | 18.997 | 20.001 | 20.002 | 20.003 | 43 | 42.998 | 43.001 | 40.001 | 39.996 | 40.007 | 70.003 | 70.002 | 69.007 | 76.001 | 75.998 | 76.003 | 120.03 | 119.99 | 120 | 120.01 | 119.99 | 120 | 120 | 120.01 | 120 | 120.01 | 120.01 | 119.99 | 119.99 | 119.99 | 120 | 120.03 | 120 | 120 | 109.99 | 110 | 109.99 | 44.994 | 44.996 | 44.997 | 45 | 45.003 | 44.998
426 | T16 |  | 397.07 | 396.68 | 395.72 | 399.43 | 402.02 | 402.04 | 380.08 | 380.06 | 379.53 | 375.37 | 375.14 | 375.2 | 375.34 | 374.29 | 374.84 | 366.73 | 366.64 | 366.36 | 366.48 | 367.47 | 368.28 | 375.57 | 375.42 | 375.81 | 380.71 | 380.98 | 380.91 | 380.24 | 380.24 | 380.39 | 398.54 | 398.69 | 397.98 | 399.55 | 399.79 | 399.18 | 395.85 | 415.28 | 415.6 | 415.22 | 416.74 | 416.63 | 415.52 | 415.83 | 415.04 | 416.94 | 417.68 | 418.1 | 418.5 | 418.55 | 419.62 | 420.09 | 419.13 | 418.15 | 417.29 | 421.52 | 424.77 | 395.03 | 393.65 | 396.71 | 398.4 | 397.09 | 396.85 | 375.47 | 376.16 | 376.4 | 366.38 | 365.6 | 365.15 | 366.46 | 366.47 | 401.36 | 401.08 | 401.12 | 376.8 | 377.11 | 377.5 | 376.75 | 377.54 | 377.97 | 377.59 | 375.59 | 374.73 | 374.75 | 366.14 | 366.12 | 366.03 | 366.07 | 421.89 | 421.88 | 421.83 | 421.51 | 422.29 | 421.1 | 420.51 | 418.92 | 418.82 | 417.74 | 422.34 | 422.44 | 423.18 | 422.41 | 422.82 | 422.76 | 421.91 | 422.92 | 418 | 419.15 | 417.2 | 416.53 | 416.21 | 416.94 | 417.33 | 416.71 | 416.35 | 416.12 | 413.41 | 415.12 | 379.43 | 380.31 | 379.95 | 419.52 | 420.04 | 416.83 | 422.87 | 421.94 | 421.77 | 419.56 | 419.21 | 418.83 | 417.78 | 417.92 | 417.91 | 382.22 | 381.59 | 381.71 | 378.83 | 378.27 | 378.63 | 375.5 | 376.01 | 376.75 | 373.47 | 372.14 | 373.17 | 374.04 | 373.48 | 373.59 | 399.19 | 397.74 | 398.02 | 400 | 399.62 | 399.92 | 417.86 | 419.37 | 418.5 | 417.91 | 418.99 | 418.64 | 414.64 | 414.85 | 414.87 | 422.5 | 422.98 | 421.71 | 382.83 | 383.44 | 383.11 | 417.99 | 418.84 | 419.4 | 418.92 | 418.72 | 419.58 | 383.98 | 384.54 | 384.08 | 370.21 | 370.73 | 370.99 | 370.09 | 370.28 | 370.76 | 370.84 | 371.38 | 370.7 | 381.22 | 380.85 | 381.91 | 378.44 | 378.04 | 377.74 | 397.72 | 397.22 | 396.66 | 400.87 | 401.31 | 401.81 | 421.99 | 421.85 | 421.28 | 421.09 | 421.49 | 421.11 | 415.55 | 416.1 | 416.51 | 416.34 | 416.69 | 415.87 | 415.83 | 415.94 | 415.11 | 416.11 | 415.9 | 415.45 | 415.73 | 415.55 | 415.58 | 379.45 | 378.69 | 379.06 | 379.14 | 379.62 | 379.04
427 | T17 |  | 397.6 | 397.21 | 396.3 | 399.92 | 402.44 | 402.51 | 380.42 | 380.44 | 379.93 | 375.65 | 375.42 | 375.46 | 375.66 | 374.57 | 375.15 | 366.47 | 366.45 | 366.09 | 366.34 | 367.21 | 367.95 | 375.79 | 375.69 | 376.2 | 381.05 | 381.33 | 381.23 | 380.65 | 380.55 | 380.9 | 399.05 | 399.19 | 398.49 | 399.99 | 400.33 | 399.65 | 396.35 | 415.5 | 415.82 | 415.41 | 416.94 | 416.84 | 415.71 | 416.02 | 415.25 | 417.43 | 417.96 | 418.53 | 418.86 | 418.95 | 420.09 | 420.51 | 419.43 | 418.45 | 417.75 | 421.92 | 425.17 | 395.63 | 394.22 | 397.32 | 398.98 | 397.66 | 397.48 | 375.86 | 376.42 | 376.77 | 366.13 | 365.46 | 364.91 | 366.28 | 366.26 | 401.84 | 401.62 | 401.54 | 377.17 | 377.52 | 377.88 | 377.11 | 378 | 378.4 | 378.03 | 376.02 | 375.14 | 375.18 | 365.94 | 365.93 | 365.85 | 365.9 | 422.09 | 422.11 | 422.07 | 421.69 | 422.61 | 421.52 | 420.99 | 419.41 | 419.26 | 418.13 | 422.81 | 422.86 | 423.64 | 422.8 | 423.32 | 423.14 | 422.32 | 423.29 | 418.41 | 419.61 | 417.65 | 416.89 | 416.63 | 417.38 | 417.72 | 417.17 | 416.77 | 416.42 | 413.68 | 415.39 | 379.83 | 380.74 | 380.4 | 419.92 | 420.46 | 417.29 | 423.31 | 422.25 | 422.26 | 420.03 | 419.59 | 419.18 | 417.97 | 418.1 | 418.11 | 382.66 | 381.98 | 382.12 | 379.26 | 378.68 | 379 | 375.8 | 376.31 | 377.14 | 373.14 | 372.03 | 373.06 | 373.88 | 373.22 | 373.38 | 399.79 | 398.31 | 398.54 | 400.45 | 400.13 | 400.45 | 418.21 | 419.76 | 418.8 | 418.31 | 419.38 | 419.02 | 415.04 | 415.14 | 415.19 | 422.63 | 423.08 | 421.86 | 383.21 | 383.77 | 383.47 | 418.36 | 419.19 | 419.74 | 419.29 | 418.99 | 419.81 | 384.28 | 384.9 | 384.4 | 369.88 | 370.45 | 370.84 | 369.82 | 369.97 | 370.5 | 370.49 | 371.19 | 370.28 | 381.48 | 381.18 | 382.24 | 378.7 | 378.32 | 378.02 | 398.17 | 397.68 | 397.12 | 401.2 | 401.6 | 402.07 | 422.27 | 422.13 | 421.6 | 421.35 | 421.89 | 421.44 | 415.88 | 416.35 | 416.77 | 416.54 | 417.11 | 416.18 | 416.16 | 416.2 | 415.39 | 416.39 | 416.21 | 415.74 | 415.87 | 415.63 | 415.73 | 379.76 | 379.04 | 379.24 | 379.36 | 379.85 | 379.34
428 | T18 |  | 397.04 | 396.69 | 395.73 | 399.34 | 401.91 | 401.94 | 380.51 | 380.62 | 380.09 | 375.9 | 375.73 | 375.81 | 375.89 | 374.88 | 375.4 | 367.22 | 367.14 | 366.8 | 367.1 | 367.96 | 368.6 | 376.17 | 376 | 376.47 | 381.27 | 381.47 | 381.47 | 380.86 | 380.87 | 381.03 | 398.52 | 398.66 | 397.94 | 399.46 | 399.83 | 399.11 | 395.71 | 415.22 | 415.6 | 415.15 | 416.76 | 416.58 | 415.48 | 415.76 | 415 | 417.17 | 417.84 | 418.31 | 418.63 | 418.62 | 419.78 | 420.23 | 419.29 | 418.26 | 417.48 | 421.71 | 424.98 | 395.06 | 393.77 | 396.78 | 398.4 | 397.13 | 396.88 | 376.13 | 376.76 | 377.03 | 366.82 | 366.12 | 365.6 | 367 | 366.94 | 401.37 | 401.07 | 401.09 | 377.27 | 377.57 | 378.04 | 377.21 | 378.11 | 378.52 | 378.13 | 376.17 | 375.36 | 375.29 | 366.65 | 366.6 | 366.5 | 366.61 | 421.88 | 421.93 | 421.88 | 421.51 | 422.42 | 421.33 | 420.69 | 419.18 | 419.01 | 417.89 | 422.52 | 422.61 | 423.31 | 422.61 | 423.02 | 422.93 | 422.13 | 423.06 | 418.18 | 419.39 | 417.37 | 416.67 | 416.34 | 417.06 | 417.51 | 416.93 | 416.6 | 416.15 | 413.42 | 415.11 | 380.02 | 380.81 | 380.45 | 419.61 | 420.22 | 416.96 | 422.98 | 422.04 | 421.93 | 419.7 | 419.32 | 418.89 | 417.7 | 417.82 | 417.85 | 382.67 | 382.11 | 382.1 | 379.36 | 378.86 | 379.06 | 376.04 | 376.59 | 377.35 | 373.93 | 372.64 | 373.77 | 374.48 | 373.86 | 374.03 | 399.16 | 397.68 | 397.94 | 399.82 | 399.54 | 399.84 | 417.96 | 419.48 | 418.61 | 418.08 | 419.1 | 418.84 | 414.81 | 414.97 | 415.07 | 422.51 | 422.97 | 421.69 | 383.28 | 383.89 | 383.56 | 418.22 | 418.94 | 419.47 | 419.07 | 418.89 | 419.65 | 384.47 | 385.16 | 384.48 | 370.68 | 371.28 | 371.56 | 370.61 | 370.83 | 371.25 | 371.33 | 371.83 | 371.22 | 381.66 | 381.5 | 382.5 | 379.04 | 378.64 | 378.33 | 397.79 | 397.24 | 396.65 | 400.75 | 401.23 | 401.64 | 422.18 | 422.01 | 421.4 | 421.26 | 421.69 | 421.24 | 415.7 | 416.24 | 416.54 | 416.46 | 416.88 | 416.02 | 415.96 | 416.09 | 415.27 | 416.23 | 416.09 | 415.55 | 415.7 | 415.48 | 415.57 | 379.94 | 379.3 | 379.55 | 379.64 | 380.1 | 379.59
429 | T19 |  | 229.35 | 229.13 | 228.58 | 230.69 | 232.17 | 232.19 | 219.59 | 219.61 | 219.31 | 216.88 | 216.76 | 216.79 | 216.87 | 216.26 | 216.58 | 211.78 | 211.74 | 211.55 | 211.68 | 212.2 | 212.62 | 216.99 | 216.91 | 217.18 | 219.98 | 220.12 | 220.09 | 219.73 | 219.71 | 219.84 | 230.19 | 230.27 | 229.86 | 230.75 | 230.93 | 230.54 | 228.61 | 239.79 | 239.99 | 239.75 | 240.65 | 240.57 | 239.93 | 240.1 | 239.66 | 240.86 | 241.23 | 241.51 | 241.72 | 241.74 | 242.39 | 242.65 | 242.07 | 241.5 | 241.05 | 243.48 | 245.36 | 228.19 | 227.41 | 229.17 | 230.13 | 229.38 | 229.25 | 216.98 | 217.34 | 217.51 | 211.57 | 211.15 | 210.86 | 211.64 | 211.63 | 231.82 | 231.66 | 231.66 | 217.71 | 217.89 | 218.13 | 217.67 | 218.17 | 218.41 | 218.19 | 217.04 | 216.55 | 216.55 | 211.45 | 211.43 | 211.38 | 211.42 | 243.61 | 243.63 | 243.6 | 243.39 | 243.9 | 243.25 | 242.91 | 242.01 | 241.93 | 241.29 | 243.96 | 244.01 | 244.44 | 243.99 | 244.25 | 244.19 | 243.71 | 244.27 | 241.44 | 242.13 | 240.99 | 240.58 | 240.4 | 240.83 | 241.06 | 240.72 | 240.51 | 240.31 | 238.74 | 239.72 | 219.25 | 219.75 | 219.55 | 242.3 | 242.63 | 240.77 | 244.25 | 243.69 | 243.64 | 242.35 | 242.12 | 241.89 | 241.23 | 241.3 | 241.31 | 220.85 | 220.49 | 220.53 | 218.9 | 218.59 | 218.76 | 216.96 | 217.26 | 217.71 | 215.65 | 214.93 | 215.54 | 216.01 | 215.65 | 215.74 | 230.58 | 229.73 | 229.88 | 230.99 | 230.8 | 230.98 | 241.34 | 242.22 | 241.7 | 241.39 | 242 | 241.81 | 239.5 | 239.59 | 239.63 | 243.96 | 244.23 | 243.5 | 221.19 | 221.53 | 221.34 | 241.44 | 241.9 | 242.22 | 241.97 | 241.83 | 242.3 | 221.84 | 222.2 | 221.89 | 213.77 | 214.09 | 214.27 | 213.72 | 213.83 | 214.1 | 214.13 | 214.47 | 214.05 | 220.23 | 220.07 | 220.67 | 218.66 | 218.43 | 218.26 | 229.72 | 229.43 | 229.1 | 231.48 | 231.74 | 232 | 243.73 | 243.64 | 243.31 | 243.2 | 243.46 | 243.22 | 240.01 | 240.31 | 240.53 | 240.44 | 240.69 | 240.19 | 240.17 | 240.22 | 239.75 | 240.32 | 240.22 | 239.94 | 240.04 | 239.92 | 239.96 | 219.23 | 218.82 | 218.98 | 219.03 | 219.31 | 219
430 | T20 |  | 337.85 | 336.88 | 337.2 | 340.71 | 341.66 | 340.97 | 260.48 | 261.61 | 260.84 | 265.1 | 266.05 | 266.21 | 266.33 | 265.73 | 265.05 | 205.05 | 205.08 | 203.97 | 205.12 | 206.19 | 205.71 | 259.37 | 259.47 | 259.07 | 260.82 | 259.68 | 260.89 | 271.05 | 270.26 | 270.55 | 341.17 | 340.56 | 340.12 | 343.2 | 343.04 | 342.72 | 341.91 | 424.11 | 424.16 | 424.25 | 423.92 | 424.15 | 424.09 | 424.32 | 424.2 | 434.26 | 433.94 | 432.75 | 434.42 | 433.78 | 432.61 | 429.64 | 429.29 | 429.28 | 428.58 | 427.98 | 426.52 | 334.85 | 334.79 | 335.29 | 335.56 | 335.52 | 334.95 | 256.21 | 257.08 | 256.29 | 203.18 | 203.79 | 204.36 | 205.94 | 204.46 | 338.9 | 338.45 | 339.27 | 258.45 | 258.37 | 258.23 | 259.1 | 260.93 | 260.71 | 260.62 | 264.22 | 264.57 | 264.2 | 205.97 | 206.24 | 204.94 | 204.52 | 417.5 | 418.76 | 419.13 | 418.87 | 428.51 | 428.57 | 428.39 | 424.21 | 424.67 | 425.67 | 427.7 | 428.5 | 427.34 | 427.38 | 424.87 | 425.77 | 425.16 | 424.05 | 428.55 | 428.17 | 428.79 | 432.89 | 431.71 | 431.26 | 426.76 | 425.87 | 426.58 | 422.14 | 419.32 | 420.45 | 261.03 | 260.58 | 259.01 | 429.05 | 428.58 | 429.19 | 426.03 | 426.09 | 425.37 | 428.91 | 430.06 | 430.47 | 418.54 | 417.9 | 418.1 | 257.66 | 258.34 | 256.3 | 257.56 | 256.88 | 257.13 | 255.45 | 254.78 | 255.31 | 203.87 | 204.08 | 203.94 | 205.94 | 204.9 | 204.53 | 332.28 | 331.41 | 331.01 | 334.89 | 334.7 | 333.93 | 427.55 | 425.88 | 427.66 | 429.23 | 428.52 | 427.86 | 426.52 | 426.04 | 425.68 | 418.32 | 416.62 | 416.23 | 257.27 | 259.74 | 257.14 | 428.32 | 428.29 | 427.72 | 431.62 | 433.17 | 433.79 | 258.33 | 258.3 | 258.1 | 206.31 | 206.16 | 206.03 | 203.66 | 206.92 | 206.7 | 206.8 | 205.98 | 205.17 | 258.07 | 258.14 | 256.59 | 256.89 | 257.04 | 256.68 | 334.59 | 334.06 | 332.02 | 338.64 | 338.18 | 337.97 | 429.26 | 428.59 | 428.96 | 429.6 | 428.82 | 428.63 | 428.74 | 428.16 | 429.3 | 428.4 | 426.55 | 428.34 | 431.7 | 431.38 | 432.05 | 433.07 | 433.32 | 433.22 | 419.59 | 419.9 | 419.35 | 257.79 | 258.29 | 258.43 | 259.1 | 258.53 | 257.7
431 | T21 |  | 355.99 | 355.28 | 355.53 | 358.2 | 357.75 | 357.82 | 273.22 | 273.27 | 272.46 | 275.93 | 276.87 | 277.18 | 277.1 | 276.52 | 276.29 | 204.21 | 203.97 | 202.92 | 204.1 | 205.21 | 204.71 | 269.37 | 270.33 | 269.46 | 271.41 | 272.59 | 271.97 | 282.46 | 282.44 | 282.52 | 359.09 | 358.35 | 358.02 | 359.82 | 360.22 | 358.84 | 359.88 | 436.56 | 436.19 | 436.54 | 436.29 | 436.77 | 436.25 | 436.69 | 436.51 | 448.17 | 446.47 | 446.1 | 447.96 | 447.28 | 446.8 | 443.56 | 441.76 | 441.3 | 442.44 | 441.3 | 439.5 | 352.83 | 352.52 | 353.37 | 353.3 | 353.18 | 353.18 | 266.3 | 267.27 | 266.76 | 202.44 | 202.58 | 203.55 | 204.79 | 203.24 | 355.07 | 355.22 | 355.14 | 270.63 | 270.72 | 270.52 | 270.76 | 272.36 | 272.06 | 272.26 | 275.76 | 274.95 | 275.59 | 205.69 | 204.98 | 204.8 | 203.47 | 429.75 | 430.91 | 431.43 | 430.91 | 441.35 | 441.46 | 442.64 | 437.79 | 438.35 | 438.43 | 440.89 | 441.3 | 440.32 | 440.28 | 438.48 | 438.85 | 438.04 | 436.74 | 441.66 | 441.84 | 442.25 | 445.67 | 444.36 | 445.13 | 439.95 | 439.67 | 439.88 | 434.17 | 431.74 | 432.62 | 271.95 | 272.25 | 270.94 | 442.23 | 441.98 | 443.5 | 439.79 | 438.66 | 439.07 | 442.47 | 443.14 | 443.31 | 430.37 | 429.77 | 430 | 269.27 | 269.1 | 268.19 | 270.31 | 267.84 | 269.82 | 265.68 | 265.08 | 265.5 | 203.13 | 203.08 | 202.79 | 205.05 | 204.3 | 203.87 | 349.63 | 348.75 | 348.13 | 350.88 | 350.64 | 349.89 | 440.28 | 439.13 | 439.72 | 442.42 | 442.08 | 440.62 | 440.24 | 437.94 | 437.79 | 430.1 | 428.09 | 428.28 | 270.03 | 272 | 269.93 | 441.61 | 441.52 | 440.95 | 445.16 | 445.86 | 446.23 | 270.86 | 270.22 | 271.13 | 206.12 | 205.77 | 205.5 | 203.13 | 205.88 | 205.95 | 206.13 | 204.95 | 204.6 | 270.96 | 269.32 | 269.96 | 268.24 | 267.41 | 268.09 | 352.24 | 352.09 | 350.32 | 355.2 | 354.3 | 354.24 | 441.86 | 441.34 | 441.75 | 442.04 | 442.17 | 441.59 | 441.79 | 440.2 | 441.35 | 440.1 | 440.56 | 441.46 | 445.14 | 443.8 | 444.6 | 445.4 | 446.13 | 446.24 | 431.63 | 431.47 | 431.29 | 270.29 | 269.02 | 269.75 | 270.33 | 270.15 | 269.09
432 | T22 |  | 345.05 | 344.43 | 345 | 346.95 | 347.36 | 346.59 | 275.23 | 275.64 | 274.96 | 280.37 | 281.37 | 281.3 | 281.31 | 280.77 | 280.52 | 211.73 | 211.61 | 210.64 | 211.89 | 213.17 | 212.17 | 274.04 | 274.84 | 274.35 | 274.89 | 274.9 | 274.58 | 284.88 | 285.22 | 286.49 | 348.2 | 347.42 | 347.2 | 348.29 | 348.91 | 348.03 | 347.93 | 426.33 | 426.64 | 426.36 | 426.56 | 426.7 | 426.29 | 426.37 | 426.44 | 438.68 | 437.78 | 437.38 | 438.31 | 437.12 | 436.87 | 433.57 | 433.19 | 432.69 | 432.8 | 432.04 | 430.83 | 342.3 | 341.99 | 343.01 | 342.62 | 342.68 | 342.09 | 271.1 | 271.65 | 271.26 | 209.89 | 210.16 | 210.5 | 212.7 | 211.22 | 344.74 | 343.6 | 344.59 | 272.59 | 273.19 | 272.7 | 274.15 | 274.55 | 274.19 | 273.98 | 278.87 | 279.02 | 278.94 | 213.32 | 212.62 | 211.58 | 211.17 | 419.99 | 421.62 | 421.85 | 421.33 | 432.21 | 432.59 | 432.48 | 428.8 | 428.54 | 429.55 | 431.31 | 432.13 | 431.12 | 431.3 | 428.75 | 429.44 | 429.29 | 427.83 | 432.3 | 432.41 | 432.13 | 436.23 | 434.84 | 434.84 | 430.54 | 430.26 | 430.91 | 424.35 | 421.51 | 422.26 | 274.62 | 275.07 | 273.47 | 432.22 | 432.78 | 433.25 | 430.24 | 429.68 | 429.26 | 432.44 | 433.69 | 433.66 | 420.47 | 420 | 420.26 | 271.84 | 271.85 | 269.82 | 272.55 | 271.37 | 271.71 | 269.75 | 268.75 | 269.63 | 209.83 | 210.01 | 210.17 | 212.82 | 212 | 211.33 | 338.96 | 337.81 | 337.36 | 339.56 | 339.77 | 339.06 | 430.53 | 429.25 | 430.68 | 432.72 | 432.05 | 431.48 | 430.51 | 428.85 | 429.64 | 420.68 | 419.1 | 418.81 | 271.05 | 272.66 | 270.76 | 432.62 | 431.54 | 431.19 | 435.33 | 436.85 | 436.39 | 272.04 | 271.95 | 272.27 | 213.84 | 213.43 | 212.94 | 210.32 | 213.3 | 213.11 | 213.57 | 212.61 | 212.39 | 272.3 | 272.62 | 271.29 | 271.72 | 271.58 | 271.3 | 341.54 | 341.29 | 339.36 | 343.46 | 342.87 | 342.47 | 432.97 | 432.11 | 432.38 | 433.11 | 432.64 | 431.74 | 432.5 | 431.3 | 431.63 | 431.75 | 430.84 | 431.74 | 434.89 | 434.65 | 435.23 | 436.06 | 436.76 | 436.27 | 421.4 | 421.62 | 421.32 | 271.59 | 271.28 | 271.52 | 271.85 | 271.88 | 271.46
433 | T23 |  | 346.3 | 345.53 | 345.91 | 348.62 | 348.93 | 348.46 | 269.64 | 270.17 | 269.42 | 273.8 | 274.77 | 274.9 | 274.91 | 274.34 | 273.95 | 207 | 206.89 | 205.84 | 207.04 | 208.19 | 207.53 | 267.59 | 268.21 | 267.63 | 269.04 | 269.06 | 269.15 | 279.46 | 279.31 | 279.86 | 349.49 | 348.77 | 348.45 | 350.43 | 350.72 | 349.87 | 349.9 | 429 | 429 | 429.05 | 428.92 | 429.21 | 428.88 | 429.13 | 429.05 | 440.37 | 439.4 | 438.75 | 440.23 | 439.39 | 438.76 | 435.59 | 434.75 | 434.42 | 434.61 | 433.77 | 432.28 | 343.33 | 343.1 | 343.89 | 343.83 | 343.8 | 343.41 | 264.54 | 265.33 | 264.77 | 205.17 | 205.51 | 206.14 | 207.81 | 206.31 | 346.23 | 345.75 | 346.33 | 267.22 | 267.43 | 267.15 | 268 | 269.28 | 268.99 | 268.95 | 272.95 | 272.85 | 272.91 | 208.33 | 207.95 | 207.11 | 206.39 | 422.41 | 423.77 | 424.14 | 423.7 | 434.03 | 434.21 | 434.5 | 430.26 | 430.52 | 431.22 | 433.3 | 433.97 | 432.93 | 432.99 | 430.7 | 431.35 | 430.83 | 429.54 | 434.17 | 434.14 | 434.39 | 438.26 | 436.97 | 437.08 | 432.42 | 431.93 | 432.46 | 426.88 | 424.19 | 425.11 | 269.2 | 269.3 | 267.81 | 434.5 | 434.45 | 435.31 | 432.02 | 431.48 | 431.23 | 434.61 | 435.63 | 435.81 | 423.13 | 422.55 | 422.79 | 266.25 | 266.43 | 264.77 | 266.8 | 265.36 | 266.22 | 263.62 | 262.87 | 263.48 | 205.61 | 205.72 | 205.63 | 207.93 | 207.07 | 206.57 | 340.29 | 339.32 | 338.83 | 341.78 | 341.7 | 340.96 | 432.79 | 431.42 | 432.69 | 434.79 | 434.22 | 433.32 | 432.42 | 430.94 | 431.04 | 423.04 | 421.27 | 421.11 | 266.12 | 268.13 | 265.95 | 434.18 | 433.78 | 433.29 | 437.37 | 438.63 | 438.8 | 267.08 | 266.83 | 267.17 | 208.76 | 208.45 | 208.16 | 205.7 | 208.7 | 208.58 | 208.84 | 207.85 | 207.39 | 267.11 | 266.69 | 265.94 | 265.62 | 265.34 | 265.35 | 342.79 | 342.48 | 340.57 | 345.77 | 345.12 | 344.9 | 434.7 | 434.01 | 434.37 | 434.92 | 434.54 | 433.99 | 434.34 | 433.22 | 434.09 | 433.42 | 432.65 | 433.85 | 437.24 | 436.61 | 437.29 | 438.18 | 438.74 | 438.58 | 424.21 | 424.33 | 423.99 | 266.56 | 266.2 | 266.57 | 267.09 | 266.85 | 266.08
434 | T24 |  | 0.89893 | 0.89871 | 0.89888 | 0.89943 | 0.89949 | 0.89937 | 0.87144 | 0.87174 | 0.87128 | 0.87733 | 0.87786 | 0.87793 | 0.87801 | 0.87763 | 0.87745 | 0.84896 | 0.8488 | 0.84754 | 0.84611 | 0.8473 | 0.84673 | 0.87335 | 0.87375 | 0.87336 | 0.87227 | 0.87226 | 0.87237 | 0.87865 | 0.87879 | 0.87891 | 0.8999 | 0.89966 | 0.89961 | 0.89984 | 0.89999 | 0.89982 | 0.89986 | 0.91353 | 0.91349 | 0.91351 | 0.91355 | 0.91359 | 0.91347 | 0.91349 | 0.91358 | 0.91736 | 0.91706 | 0.91695 | 0.91679 | 0.91662 | 0.91628 | 0.91582 | 0.91606 | 0.91629 | 0.91677 | 0.91543 | 0.91436 | 0.89819 | 0.89821 | 0.89846 | 0.89846 | 0.89845 | 0.89835 | 0.87177 | 0.8723 | 0.8718 | 0.8466 | 0.84703 | 0.848 | 0.84714 | 0.84494 | 0.89883 | 0.89873 | 0.89891 | 0.87121 | 0.87139 | 0.87122 | 0.87178 | 0.87128 | 0.87116 | 0.87109 | 0.8737 | 0.8738 | 0.87381 | 0.84753 | 0.84695 | 0.84575 | 0.84533 | 0.9128 | 0.91301 | 0.91309 | 0.91297 | 0.91508 | 0.91539 | 0.91555 | 0.91549 | 0.91561 | 0.91606 | 0.91496 | 0.91496 | 0.91467 | 0.91484 | 0.91449 | 0.91458 | 0.91483 | 0.91432 | 0.91631 | 0.916 | 0.91662 | 0.91701 | 0.91702 | 0.91678 | 0.91624 | 0.91646 | 0.91652 | 0.91309 | 0.91268 | 0.91274 | 0.87143 | 0.87129 | 0.87031 | 0.91604 | 0.91584 | 0.91687 | 0.91465 | 0.91485 | 0.91487 | 0.91586 | 0.91604 | 0.91617 | 0.91271 | 0.91267 | 0.91269 | 0.86953 | 0.86962 | 0.86864 | 0.87111 | 0.87023 | 0.87066 | 0.87106 | 0.87046 | 0.87079 | 0.84762 | 0.84738 | 0.84747 | 0.84714 | 0.84589 | 0.8457 | 0.89721 | 0.89685 | 0.89678 | 0.8975 | 0.89758 | 0.89737 | 0.91628 | 0.91563 | 0.91598 | 0.91631 | 0.916 | 0.91595 | 0.91708 | 0.91689 | 0.91693 | 0.91274 | 0.9125 | 0.91247 | 0.86921 | 0.87062 | 0.8691 | 0.91614 | 0.91594 | 0.91565 | 0.9162 | 0.91644 | 0.91614 | 0.86974 | 0.86967 | 0.87003 | 0.8482 | 0.84819 | 0.84762 | 0.84774 | 0.85122 | 0.85126 | 0.84849 | 0.84719 | 0.84669 | 0.87105 | 0.87095 | 0.87029 | 0.87221 | 0.87194 | 0.87204 | 0.8979 | 0.89768 | 0.89712 | 0.89861 | 0.89843 | 0.89837 | 0.91521 | 0.91513 | 0.91545 | 0.91551 | 0.91531 | 0.91537 | 0.91692 | 0.91668 | 0.91664 | 0.91669 | 0.91639 | 0.91684 | 0.91712 | 0.91701 | 0.9173 | 0.91713 | 0.9172 | 0.91734 | 0.91269 | 0.91264 | 0.91261 | 0.86946 | 0.86933 | 0.86944 | 0.86998 | 0.86955 | 0.86921
435 | T25 |  | 0.89893 | 0.89871 | 0.89888 | 0.89943 | 0.89949 | 0.89937 | 0.87144 | 0.87174 | 0.87128 | 0.87733 | 0.87786 | 0.87793 | 0.87801 | 0.87763 | 0.87745 | 0.84896 | 0.8488 | 0.84754 | 0.84611 | 0.8473 | 0.84673 | 0.87335 | 0.87375 | 0.87336 | 0.87227 | 0.87226 | 0.87237 | 0.87865 | 0.87879 | 0.87891 | 0.8999 | 0.89966 | 0.89961 | 0.89984 | 0.89999 | 0.89982 | 0.89986 | 0.91353 | 0.91349 | 0.91351 | 0.91355 | 0.91359 | 0.91347 | 0.91349 | 0.91358 | 0.91736 | 0.91706 | 0.91695 | 0.91679 | 0.91662 | 0.91628 | 0.91582 | 0.91606 | 0.91629 | 0.91677 | 0.91543 | 0.91436 | 0.89819 | 0.89821 | 0.89846 | 0.89846 | 0.89845 | 0.89835 | 0.87177 | 0.8723 | 0.8718 | 0.8466 | 0.84703 | 0.848 | 0.84714 | 0.84494 | 0.89883 | 0.89873 | 0.89891 | 0.87121 | 0.87139 | 0.87122 | 0.87178 | 0.87128 | 0.87116 | 0.87109 | 0.8737 | 0.8738 | 0.87381 | 0.84753 | 0.84695 | 0.84575 | 0.84533 | 0.9128 | 0.91301 | 0.91309 | 0.91297 | 0.91508 | 0.91539 | 0.91555 | 0.91549 | 0.91561 | 0.91606 | 0.91496 | 0.91496 | 0.91467 | 0.91484 | 0.91449 | 0.91458 | 0.91476 | 0.91432 | 0.91631 | 0.916 | 0.91662 | 0.91701 | 0.91702 | 0.91678 | 0.91624 | 0.91646 | 0.91652 | 0.91309 | 0.91268 | 0.91274 | 0.87143 | 0.87129 | 0.87031 | 0.91604 | 0.91584 | 0.91687 | 0.91465 | 0.91485 | 0.91487 | 0.91586 | 0.91604 | 0.91617 | 0.91271 | 0.91267 | 0.91269 | 0.86953 | 0.86962 | 0.86864 | 0.87111 | 0.87023 | 0.87066 | 0.87106 | 0.87046 | 0.87079 | 0.84762 | 0.84738 | 0.84747 | 0.84714 | 0.84589 | 0.8457 | 0.89721 | 0.89685 | 0.89678 | 0.8975 | 0.89758 | 0.89737 | 0.91628 | 0.91563 | 0.91598 | 0.91631 | 0.916 | 0.91595 | 0.91708 | 0.91689 | 0.91693 | 0.91274 | 0.9125 | 0.91247 | 0.86921 | 0.87062 | 0.8691 | 0.91614 | 0.91594 | 0.91565 | 0.9162 | 0.91644 | 0.91614 | 0.86974 | 0.86967 | 0.87003 | 0.8482 | 0.84819 | 0.84762 | 0.84774 | 0.85122 | 0.85126 | 0.84849 | 0.84719 | 0.84669 | 0.87105 | 0.87095 | 0.87029 | 0.87221 | 0.87194 | 0.87204 | 0.8979 | 0.89768 | 0.89712 | 0.89861 | 0.89843 | 0.89837 | 0.91521 | 0.91513 | 0.91545 | 0.91551 | 0.91531 | 0.91537 | 0.91692 | 0.91668 | 0.91664 | 0.91669 | 0.91639 | 0.91684 | 0.91712 | 0.91701 | 0.9173 | 0.91713 | 0.9172 | 0.91734 | 0.91269 | 0.91264 | 0.91261 | 0.86946 | 0.86933 | 0.86944 | 0.86998 | 0.86955 | 0.86921
436 | T26 |  | 0.48813 | 0.48881 | 0.49001 | 0.51873 | 0.51559 | 0.51502 | 0.32316 | 0.32325 | 0.32357 | 0.29348 | 0.29384 | 0.29381 | 0.2937 | 0.2944 | 0.29391 | 0.13891 | 0.1389 | 0.13885 | 0.14596 | 0.14579 | 0.14542 | 0.2919 | 0.29212 | 0.29164 | 0.30873 | 0.30851 | 0.30859 | 0.31123 | 0.31129 | 0.31116 | 0.49307 | 0.49293 | 0.49378 | 0.5177 | 0.51747 | 0.51871 | 0.51619 | 0.73012 | 0.72937 | 0.73024 | 0.72754 | 0.72794 | 0.72966 | 0.72916 | 0.73062 | 0.78624 | 0.78552 | 0.78489 | 0.78451 | 0.78428 | 0.78298 | 0.78204 | 0.78307 | 0.78416 | 0.78541 | 0.78051 | 0.77635 | 0.48308 | 0.4849 | 0.4813 | 0.48615 | 0.48761 | 0.48765 | 0.29145 | 0.29114 | 0.29075 | 0.13862 | 0.13892 | 0.13923 | 0.14607 | 0.14577 | 0.51505 | 0.51539 | 0.51535 | 0.31152 | 0.31134 | 0.31096 | 0.31174 | 0.32495 | 0.32458 | 0.3248 | 0.32743 | 0.32824 | 0.32822 | 0.14625 | 0.14617 | 0.14603 | 0.14595 | 0.71841 | 0.71865 | 0.71882 | 0.71923 | 0.77973 | 0.78106 | 0.78171 | 0.7828 | 0.78298 | 0.78441 | 0.77932 | 0.77932 | 0.77823 | 0.77917 | 0.77824 | 0.77847 | 0.77937 | 0.77796 | 0.78398 | 0.78283 | 0.78491 | 0.78608 | 0.7863 | 0.78543 | 0.78442 | 0.78513 | 0.78552 | 0.72823 | 0.73249 | 0.72943 | 0.32343 | 0.32265 | 0.3226 | 0.78259 | 0.7818 | 0.78546 | 0.77803 | 0.77915 | 0.77922 | 0.78217 | 0.78272 | 0.78322 | 0.72498 | 0.72465 | 0.72472 | 0.32042 | 0.32094 | 0.32049 | 0.30982 | 0.30998 | 0.3099 | 0.29123 | 0.29068 | 0.29021 | 0.13628 | 0.13668 | 0.13635 | 0.14329 | 0.14333 | 0.14329 | 0.49122 | 0.49274 | 0.4923 | 0.52287 | 0.5235 | 0.5229 | 0.78418 | 0.78225 | 0.78338 | 0.78421 | 0.78295 | 0.78316 | 0.78729 | 0.78689 | 0.78693 | 0.71707 | 0.71601 | 0.7181 | 0.32007 | 0.3201 | 0.3198 | 0.78384 | 0.7829 | 0.78227 | 0.78322 | 0.78368 | 0.7826 | 0.31932 | 0.31883 | 0.31935 | 0.14494 | 0.14475 | 0.14454 | 0.13756 | 0.13794 | 0.13778 | 0.14477 | 0.14437 | 0.14458 | 0.30812 | 0.30832 | 0.30723 | 0.2895 | 0.28971 | 0.28997 | 0.48661 | 0.48685 | 0.48057 | 0.52241 | 0.52183 | 0.52106 | 0.77965 | 0.77959 | 0.78044 | 0.78064 | 0.7801 | 0.78052 | 0.78665 | 0.78584 | 0.78566 | 0.7858 | 0.78502 | 0.78622 | 0.78666 | 0.78651 | 0.7874 | 0.78645 | 0.78664 | 0.78724 | 0.72865 | 0.7289 | 0.72875 | 0.32284 | 0.32339 | 0.32322 | 0.32332 | 0.3228 | 0.3231
437 | T27 |  | 112800 | 112610 | 112760 | 121660 | 121760 | 121460 | 54722 | 54858 | 54684 | 49866 | 50086 | 50114 | 50116 | 49991 | 49902 | 17263 | 17249 | 17136 | 18116 | 18245 | 18173 | 48450 | 48588 | 48451 | 52225 | 52223 | 52252 | 54734 | 54710 | 54830 | 115480 | 115250 | 115140 | 122080 | 122230 | 122030 | 120440 | 222320 | 222270 | 222340 | 222260 | 222470 | 222250 | 222370 | 222360 | 247410 | 247000 | 246710 | 247630 | 247110 | 246970 | 245130 | 244430 | 244010 | 244060 | 244430 | 244080 | 110070 | 110060 | 110300 | 111870 | 111860 | 111670 | 47780 | 47956 | 47821 | 17043 | 17080 | 17150 | 18194 | 18016 | 120480 | 120310 | 120500 | 51803 | 51858 | 51790 | 51990 | 54611 | 54542 | 54522 | 55546 | 55541 | 55551 | 18255 | 18208 | 18109 | 18034 | 218670 | 219470 | 219690 | 219410 | 244720 | 244610 | 244670 | 241720 | 241850 | 242070 | 244260 | 244690 | 244150 | 244050 | 242710 | 243090 | 242580 | 241980 | 243770 | 244060 | 243740 | 245890 | 245060 | 245270 | 242530 | 242150 | 242360 | 221070 | 219570 | 220000 | 54614 | 54620 | 54245 | 244360 | 244390 | 244210 | 243410 | 242910 | 242730 | 244320 | 244840 | 244890 | 218970 | 218630 | 218780 | 53852 | 53893 | 53477 | 51709 | 51373 | 51572 | 47569 | 47398 | 47529 | 17107 | 17111 | 17106 | 18214 | 18109 | 18063 | 112130 | 111760 | 111560 | 120380 | 120400 | 120080 | 242910 | 242400 | 242980 | 244100 | 244010 | 243370 | 241890 | 241020 | 241110 | 218860 | 217850 | 217770 | 53806 | 54319 | 53757 | 243700 | 243640 | 243470 | 245850 | 246570 | 246780 | 54045 | 53995 | 54082 | 18313 | 18287 | 18249 | 17122 | 17445 | 17437 | 18328 | 18210 | 18162 | 51776 | 51688 | 51489 | 48010 | 47946 | 47953 | 111460 | 111000 | 109000 | 121940 | 121700 | 121570 | 244920 | 244420 | 244570 | 244840 | 244700 | 244270 | 243280 | 242690 | 243330 | 242900 | 242450 | 243040 | 245060 | 244730 | 244910 | 245690 | 245940 | 245780 | 219580 | 219600 | 219400 | 53925 | 53850 | 53935 | 54076 | 54003 | 53819
438 | T28 |  | 116300 | 116100 | 116230 | 125150 | 125300 | 125010 | 57401 | 57537 | 57354 | 52279 | 52499 | 52527 | 52530 | 52400 | 52315 | 18268 | 18253 | 18139 | 19190 | 19322 | 19250 | 50848 | 50985 | 50851 | 54814 | 54813 | 54839 | 57333 | 57308 | 57429 | 119000 | 118770 | 118650 | 125590 | 125730 | 125520 | 123870 | 225320 | 225270 | 225350 | 225290 | 225490 | 225240 | 225380 | 225370 | 250180 | 249780 | 249500 | 250440 | 249910 | 249810 | 247960 | 247230 | 246800 | 246840 | 247290 | 247020 | 113540 | 113500 | 113790 | 115400 | 115360 | 115170 | 50186 | 50368 | 50231 | 18052 | 18085 | 18155 | 19272 | 19094 | 124020 | 123840 | 124040 | 54369 | 54425 | 54360 | 54556 | 57271 | 57206 | 57180 | 58192 | 58181 | 58192 | 19328 | 19280 | 19179 | 19105 | 221780 | 222580 | 222800 | 222510 | 247610 | 247480 | 247510 | 244530 | 244650 | 244840 | 247140 | 247570 | 247060 | 246940 | 245600 | 245980 | 245470 | 244880 | 246550 | 246870 | 246500 | 248640 | 247800 | 248020 | 245290 | 244890 | 245100 | 224110 | 222530 | 223000 | 57269 | 57281 | 56903 | 247170 | 247220 | 246970 | 246290 | 245770 | 245600 | 247150 | 247670 | 247700 | 221990 | 221660 | 221810 | 56523 | 56558 | 56140 | 54283 | 53940 | 54142 | 49970 | 49803 | 49940 | 18127 | 18130 | 18130 | 19307 | 19201 | 19157 | 115630 | 115230 | 115040 | 123840 | 123860 | 123540 | 245710 | 245230 | 245770 | 246910 | 246810 | 246180 | 244600 | 243740 | 243840 | 222010 | 221000 | 220900 | 56519 | 57040 | 56475 | 246500 | 246450 | 246300 | 248660 | 249380 | 249620 | 56757 | 56709 | 56794 | 19404 | 19380 | 19340 | 18143 | 18466 | 18459 | 19421 | 19306 | 19253 | 54375 | 54286 | 54090 | 50442 | 50373 | 50379 | 114960 | 114760 | 112490 | 125440 | 125200 | 125080 | 247800 | 247300 | 247440 | 247700 | 247580 | 247150 | 246010 | 245430 | 246090 | 245660 | 245240 | 245780 | 247820 | 247470 | 247650 | 248440 | 248710 | 248520 | 222590 | 222610 | 222430 | 56596 | 56511 | 56600 | 56744 | 56674 | 56482
439 | T29 |  | 215.38 | 215.41 | 215.4 | 230.59 | 230.6 | 230.59 | 138.48 | 138.51 | 138.53 | 122.84 | 122.84 | 122.85 | 122.83 | 122.84 | 122.83 | 57.542 | 57.541 | 57.542 | 60.665 | 60.664 | 60.673 | 122.84 | 122.81 | 122.81 | 132.19 | 132.15 | 132.2 | 132.16 | 132.12 | 132.12 | 218.31 | 218.3 | 218.32 | 230.47 | 230.46 | 230.48 | 227.42 | 335.97 | 335.96 | 336.02 | 335.89 | 335.92 | 335.97 | 335.99 | 335.98 | 362.09 | 362.48 | 362.61 | 362.78 | 362.86 | 363.28 | 363.52 | 363.11 | 362.7 | 362.31 | 364.23 | 365.57 | 212.26 | 212.27 | 212.24 | 215.28 | 215.27 | 215.26 | 122.8 | 122.81 | 122.79 | 57.504 | 57.51 | 57.501 | 60.629 | 60.635 | 230.48 | 230.48 | 230.49 | 132.16 | 132.15 | 132.16 | 132.13 | 138.43 | 138.43 | 138.42 | 138.38 | 138.4 | 138.38 | 60.615 | 60.622 | 60.63 | 60.622 | 335.97 | 335.94 | 335.93 | 335.98 | 364.63 | 364.12 | 363.83 | 363.16 | 363.1 | 362.61 | 364.66 | 364.71 | 364.99 | 364.7 | 364.86 | 364.84 | 364.54 | 364.9 | 362.54 | 363.02 | 362.15 | 361.87 | 361.7 | 361.98 | 362.18 | 361.89 | 361.72 | 335.97 | 336.06 | 336.03 | 138.43 | 138.41 | 138.42 | 363.16 | 363.36 | 361.86 | 364.56 | 364.21 | 364.14 | 363.14 | 362.97 | 362.82 | 335.94 | 335.93 | 335.93 | 138.38 | 138.4 | 138.4 | 132.11 | 132.14 | 132.14 | 122.79 | 122.8 | 122.8 | 57.509 | 57.511 | 57.501 | 60.634 | 60.629 | 60.64 | 218.34 | 218.36 | 218.36 | 233.49 | 233.48 | 233.47 | 362.48 | 363.19 | 362.84 | 362.49 | 362.96 | 362.85 | 360.91 | 361.08 | 361.03 | 335.84 | 335.85 | 335.87 | 138.43 | 138.44 | 138.43 | 362.46 | 362.85 | 363.09 | 362.88 | 362.78 | 363.21 | 138.46 | 138.46 | 138.45 | 60.626 | 60.634 | 60.642 | 57.518 | 57.504 | 57.506 | 60.644 | 60.639 | 60.654 | 132.17 | 132.18 | 132.15 | 122.82 | 122.82 | 122.81 | 215.28 | 215.03 | 212.27 | 233.42 | 233.42 | 233.43 | 364.27 | 364.21 | 363.94 | 363.88 | 364.05 | 363.89 | 361.32 | 361.61 | 361.82 | 361.71 | 361.81 | 361.45 | 361.4 | 361.52 | 361.12 | 361.59 | 361.45 | 361.25 | 335.99 | 336.01 | 335.97 | 138.41 | 138.45 | 138.44 | 138.44 | 138.43 | 138.43
440 | T30 |  | 216.13 | 216.17 | 216.16 | 231.32 | 231.26 | 231.29 | 139.02 | 138.98 | 139 | 123.27 | 123.28 | 123.27 | 123.26 | 123.27 | 123.28 | 57.584 | 57.574 | 57.582 | 60.707 | 60.712 | 60.709 | 123.23 | 123.25 | 123.24 | 132.62 | 132.68 | 132.64 | 132.59 | 132.61 | 132.6 | 219.03 | 219.03 | 219.05 | 231.14 | 231.18 | 231.12 | 228.17 | 336.44 | 336.4 | 336.46 | 336.36 | 336.4 | 336.41 | 336.44 | 336.43 | 362.78 | 363.02 | 363.25 | 363.43 | 363.49 | 364 | 364.2 | 363.67 | 363.21 | 363 | 364.88 | 366.19 | 213 | 213 | 212.99 | 216 | 216 | 216.02 | 123.22 | 123.22 | 123.23 | 57.553 | 57.543 | 57.54 | 60.667 | 60.683 | 231.14 | 231.19 | 231.13 | 132.65 | 132.66 | 132.66 | 132.62 | 138.9 | 138.9 | 138.89 | 138.88 | 138.84 | 138.88 | 60.675 | 60.662 | 60.684 | 60.669 | 336.42 | 336.39 | 336.4 | 336.41 | 365.2 | 364.72 | 364.55 | 363.83 | 363.76 | 363.2 | 365.28 | 365.29 | 365.59 | 365.28 | 365.52 | 365.45 | 365.07 | 365.49 | 363.16 | 363.7 | 362.79 | 362.41 | 362.26 | 362.65 | 362.8 | 362.59 | 362.35 | 336.45 | 336.55 | 336.48 | 138.9 | 138.9 | 138.93 | 363.78 | 364.01 | 362.6 | 365.25 | 364.77 | 364.82 | 363.81 | 363.57 | 363.39 | 336.38 | 336.37 | 336.37 | 138.89 | 138.86 | 138.9 | 132.64 | 132.61 | 132.65 | 123.21 | 123.22 | 123.22 | 57.552 | 57.545 | 57.548 | 60.683 | 60.684 | 60.696 | 219.06 | 219.07 | 219.07 | 234.16 | 234.15 | 234.15 | 363.06 | 363.81 | 363.34 | 363.11 | 363.62 | 363.44 | 361.59 | 361.59 | 361.57 | 336.26 | 336.25 | 336.33 | 138.95 | 138.93 | 138.94 | 363.11 | 363.51 | 363.75 | 363.54 | 363.35 | 363.74 | 138.97 | 138.96 | 138.97 | 60.694 | 60.696 | 60.697 | 57.569 | 57.542 | 57.549 | 60.69 | 60.69 | 60.7 | 132.69 | 132.65 | 132.69 | 123.27 | 123.25 | 123.27 | 216.03 | 215.79 | 213.03 | 234.11 | 234.09 | 234.1 | 364.86 | 364.79 | 364.55 | 364.44 | 364.71 | 364.53 | 361.95 | 362.15 | 362.35 | 362.2 | 362.52 | 362.1 | 362.07 | 362.07 | 361.68 | 362.13 | 362.04 | 361.87 | 336.46 | 336.44 | 336.45 | 138.94 | 138.89 | 138.91 | 138.89 | 138.92 | 138.91
441 | Frequency |  | 215.59 | 215.63 | 215.64 | 230.76 | 230.76 | 230.73 | 139.01 | 139.02 | 139.05 | 123.37 | 123.38 | 123.37 | 123.35 | 123.36 | 123.36 | 57.742 | 57.736 | 57.746 | 60.878 | 60.88 | 60.878 | 123.35 | 123.34 | 123.35 | 132.69 | 132.68 | 132.68 | 132.64 | 132.65 | 132.69 | 218.51 | 218.49 | 218.52 | 230.59 | 230.63 | 230.63 | 227.58 | 336.14 | 336.18 | 336.18 | 336.14 | 336.13 | 336.16 | 336.16 | 336.17 | 362.55 | 362.89 | 363.11 | 363.18 | 363.2 | 363.72 | 363.92 | 363.53 | 363.07 | 362.75 | 364.66 | 366.02 | 212.48 | 212.49 | 212.46 | 215.47 | 215.48 | 215.47 | 123.33 | 123.32 | 123.32 | 57.708 | 57.704 | 57.69 | 60.844 | 60.855 | 230.65 | 230.6 | 230.64 | 132.66 | 132.67 | 132.67 | 132.68 | 138.93 | 138.93 | 138.91 | 138.94 | 138.96 | 138.95 | 60.838 | 60.834 | 60.83 | 60.843 | 336.19 | 336.18 | 336.17 | 336.19 | 365.01 | 364.57 | 364.25 | 363.65 | 363.51 | 363.03 | 365.05 | 365.1 | 365.38 | 365.1 | 365.27 | 365.22 | 364.88 | 365.3 | 362.95 | 363.49 | 362.51 | 362.21 | 362.05 | 362.35 | 362.6 | 362.34 | 362.2 | 336.17 | 336.26 | 336.2 | 138.95 | 138.95 | 138.96 | 363.51 | 363.81 | 362.3 | 365 | 364.6 | 364.55 | 363.52 | 363.36 | 363.16 | 336.12 | 336.12 | 336.12 | 138.93 | 138.92 | 138.9 | 132.65 | 132.68 | 132.65 | 123.3 | 123.31 | 123.31 | 57.695 | 57.695 | 57.723 | 60.853 | 60.854 | 60.853 | 218.55 | 218.53 | 218.55 | 233.61 | 233.63 | 233.63 | 362.81 | 363.54 | 363.17 | 362.86 | 363.33 | 363.24 | 361.33 | 361.41 | 361.49 | 336.06 | 336.07 | 336.09 | 138.93 | 138.9 | 138.92 | 362.93 | 363.21 | 363.48 | 363.28 | 363.19 | 363.5 | 138.95 | 138.97 | 138.95 | 60.852 | 60.869 | 60.868 | 57.724 | 57.706 | 57.707 | 60.866 | 60.859 | 60.874 | 132.67 | 132.71 | 132.67 | 123.33 | 123.34 | 123.31 | 215.5 | 215.02 | 212.48 | 233.55 | 233.55 | 233.52 | 364.7 | 364.6 | 364.34 | 364.26 | 364.49 | 364.25 | 361.76 | 362 | 362.11 | 362.1 | 362.27 | 361.86 | 361.77 | 361.9 | 361.48 | 361.95 | 361.86 | 361.6 | 336.17 | 336.18 | 336.19 | 138.93 | 138.94 | 138.94 | 138.91 | 138.94 | 138.95
442
443 | COP - BASED ON POWER METER (Takes into account econ) - FUND |  | 4.795 | 4.7927 | 4.7849 | 4.7643 | 4.7562 | 4.7601 | 7.1986 | 7.1878 | 7.1993 | 6.9027 | 6.9011 | 6.9407 | 6.9414 | 6.9254 | 6.9508 | 9.4029 | 9.4012 | 9.4766 | 9.6068 | 9.5628 | 9.7335 | 7.1198 | 7.1053 | 7.1397 | 7.0834 | 7.0983 | 7.1108 | 6.7654 | 6.7874 | 6.7693 | 4.7494 | 4.7466 | 4.7461 | 4.7166 | 4.7038 | 4.6977 | 4.7347 | 3.257 | 3.2653 | 3.2611 | 3.2629 | 3.2563 | 3.2594 | 3.5299 | 3.535 | 2.8434 | 2.8506 | 2.8487 | 3.1513 | 3.1668 | 3.1603 | 3.2175 | 3.2259 | 3.2312 | 2.827 | 2.8238 | 2.8283 | 4.74 | 4.7199 | 4.7044 | 4.7616 | 4.7773 | 4.7704 | 7.0139 | 6.9929 | 6.9989 | 8.629 | 8.7885 | 8.1704 | 8.8946 | 9.0394 | 4.6898 | 4.6916 | 4.6963 | 6.9936 | 6.9812 | 7.0086 | 6.984 | 7.0084 | 7.0546 | 7.0384 | 6.5098 | 6.5138 | 6.5327 | 8.6171 | 8.9369 | 8.7807 | 9.0985 | 3.3934 | 3.3947 | 3.4051 | 3.3997 | 3.131 | 3.1526 | 3.1544 | 3.2208 | 3.2289 | 3.2403 | 3.2911 | 3.2949 | 3.2986 | 3.2992 | 3.3335 | 3.3281 | 3.3338 | 3.3573 | 2.9682 | 2.9667 | 2.9707 | 3.2626 | 3.2676 | 3.273 | 3.3367 | 3.3428 | 3.3456 | 3.6436 | 3.6653 | 3.6728 | 7.1768 | 7.182 | 7.2335 | 2.9434 | 2.9397 | 2.9466 | 3.3183 | 3.3047 | 3.3052 | 3.2865 | 3.2777 | 3.2994 | 3.6874 | 3.6907 | 3.691 | 7.2787 | 7.3 | 7.3772 | 7.1657 | 7.2253 | 7.1859 | 7.2591 | 7.2616 | 7.2467 | 8.704 | 8.7702 | 9.2724 | 9.3217 | 9.1718 | 9.2698 | 4.9061 | 4.946 | 4.952 | 4.8799 | 4.8825 | 4.8958 | 2.9448 | 2.9468 | 2.9209 | 3.2418 | 3.2451 | 3.2523 | 3.294 | 3.3091 | 3.3003 | 3.6568 | 3.6892 | 3.674 | 7.2558 | 7.1488 | 7.274 | 3.297 | 3.2941 | 3.291 | 3.2499 | 3.2445 | 3.2332 | 7.2522 | 7.2096 | 7.2646 | 9.0873 | 9.1695 | 9.2929 | 9.2149 | 8.8602 | 8.8929 | 9.0126 | 9.177 | 9.2354 | 7.1549 | 7.1601 | 7.1705 | 7.1268 | 7.1204 | 7.1104 | 4.902 | 4.8895 | 4.9278 | 4.827 | 4.8239 | 4.8277 | 2.9107 | 2.9268 | 2.9304 | 2.9315 | 2.9275 | 2.9189 | 3.2837 | 3.3015 | 3.2865 | 3.2894 | 3.2895 | 3.296 | 3.244 | 3.2412 | 3.2383 | 3.2209 | 3.2214 | 3.219 | 3.6027 | 3.5799 | 3.602 | 7.2807 | 7.2966 | 7.307 | 7.2627 | 7.2934 | 7.3072
444 | IE POWER - BASED ON POWER METER (FUND) |  | 72.2986 | 72.2402 | 72.3194 | 71.3078 | 71.5054 | 71.4501 | 73.1857 | 73.1704 | 73.0871 | 69.8429 | 69.802 | 70.2584 | 70.2458 | 70.2158 | 70.1503 | 72.4945 | 72.5901 | 72.7926 | 73.5479 | 73.5341 | 74.5974 | 71.9992 | 71.9539 | 72.1602 | 71.701 | 71.7563 | 71.7667 | 68.3969 | 68.7337 | 68.4714 | 71.5593 | 71.5749 | 71.5473 | 71.0031 | 70.8501 | 70.7857 | 71.2236 | 67.7684 | 67.9178 | 67.9343 | 67.891 | 67.7025 | 67.7401 | 67.8981 | 67.8721 | 65.1032 | 65.2168 | 65.2939 | 65.7435 | 65.8016 | 65.6566 | 65.9179 | 65.8944 | 65.8266 | 64.7561 | 64.801 | 64.8016 | 71.2308 | 71.0176 | 71.1218 | 71.5327 | 71.768 | 71.6527 | 70.6291 | 70.6725 | 70.6551 | 66.3373 | 67.6988 | 62.9357 | 69.0056 | 69.5628 | 70.5406 | 70.4879 | 70.6274 | 70.6383 | 70.4493 | 70.8481 | 70.7075 | 70.9212 | 71.182 | 70.9994 | 70.3543 | 70.6167 | 70.6107 | 67.8687 | 69.6948 | 68.0992 | 70.1978 | 67.1868 | 67.2252 | 67.3349 | 67.2979 | 65.4111 | 65.4702 | 65.3205 | 65.7072 | 65.8729 | 65.8972 | 67.779 | 67.8664 | 67.9455 | 67.9798 | 67.8773 | 67.9244 | 67.9664 | 67.9551 | 67.958 | 67.8101 | 68.0918 | 67.8938 | 67.806 | 67.9055 | 68.2527 | 68.2228 | 68.2765 | 69.6534 | 69.8588 | 69.9508 | 72.9891 | 73.0301 | 73.1751 | 67.6545 | 67.5848 | 67.6242 | 68.0147 | 67.7141 | 67.766 | 68.3757 | 68.0996 | 68.5147 | 70.1726 | 70.1617 | 70.1192 | 74.2344 | 74.388 | 74.6801 | 72.9008 | 73.0406 | 73.081 | 73.2307 | 73.0589 | 73.1397 | 66.8532 | 67.3622 | 70.7057 | 72.0637 | 70.7423 | 71.3913 | 74.0948 | 74.1684 | 74.3085 | 73.1635 | 73.3096 | 73.2676 | 67.6578 | 67.7008 | 67.4117 | 67.6734 | 67.8304 | 67.884 | 67.7472 | 67.7096 | 67.7784 | 70.3313 | 70.85 | 70.3421 | 73.2872 | 72.941 | 73.4042 | 67.5221 | 67.5713 | 67.5274 | 67.7359 | 67.7838 | 67.7569 | 73.3791 | 72.9196 | 73.614 | 70.8613 | 71.4404 | 72.0857 | 70.3802 | 70.0866 | 70.3993 | 70.7086 | 71.5974 | 71.9235 | 72.4875 | 72.4025 | 72.354 | 72.3749 | 72.203 | 72.1473 | 73.9311 | 73.6437 | 73.6628 | 72.5152 | 72.4673 | 72.5182 | 66.9383 | 66.8721 | 66.9474 | 67.0381 | 67.0354 | 66.777 | 67.0467 | 67.2242 | 67.1109 | 67.1413 | 67.0185 | 67.1297 | 67.2963 | 67.2438 | 67.2436 | 67.2981 | 67.3177 | 67.2934 | 69.4325 | 69.3415 | 69.394 | 73.6143 | 73.8085 | 73.905 | 73.4799 | 73.8629 | 73.6956
445 | % of TABLE IE - BASED ON POWER METER |  | 100.4652 | 100.3763 | 100.4454 | 99.1904 | 99.3866 | 99.3298 | 112.4351 | 112.3851 | 112.351 | 107.4782 | 107.471 | 108.1453 | 108.1457 | 108.0085 | 108.0745 | 124.4308 | 124.5029 | 125.1068 | 126.619 | 126.361 | 128.3617 | 110.8562 | 110.7552 | 111.1377 | 110.3496 | 110.4884 | 110.5841 | 105.328 | 105.7805 | 105.4382 | 99.4388 | 99.4399 | 99.4003 | 98.6711 | 98.4565 | 98.3548 | 98.9906 | 91.6544 | 91.8567 | 91.8785 | 91.8202 | 91.5657 | 91.6167 | 91.8311 | 91.7964 | 88.2917 | 88.4471 | 88.5583 | 88.9151 | 88.9949 | 88.7988 | 89.1606 | 89.1316 | 89.0432 | 87.8208 | 87.8897 | 87.8854 | 99.02 | 98.6996 | 98.7665 | 99.4424 | 99.7651 | 99.6042 | 108.9046 | 108.8372 | 108.8466 | 113.9663 | 116.2036 | 108.0667 | 118.1183 | 119.4699 | 98.0539 | 97.9996 | 98.188 | 108.8033 | 108.5557 | 109.1029 | 108.8497 | 109.1758 | 109.6922 | 109.4179 | 105.6362 | 105.9116 | 106.0234 | 115.3079 | 119.0089 | 116.5654 | 120.4426 | 90.8674 | 90.919 | 91.0676 | 91.0173 | 88.4654 | 88.5468 | 88.3457 | 88.8756 | 89.0995 | 89.1375 | 91.6702 | 91.7887 | 91.8951 | 91.9413 | 91.8114 | 91.8735 | 91.9307 | 91.9234 | 92.166 | 91.9572 | 92.3551 | 91.8244 | 91.7063 | 91.8408 | 92.3193 | 92.2804 | 92.3535 | 94.2034 | 94.4821 | 94.6062 | 112.1716 | 112.2446 | 112.6287 | 91.769 | 91.6739 | 91.7166 | 91.9983 | 91.5914 | 91.661 | 92.4755 | 92.1029 | 92.6645 | 94.9068 | 94.8922 | 94.8345 | 113.9564 | 114.249 | 114.9301 | 112.015 | 112.4677 | 112.2861 | 112.8426 | 112.673 | 112.678 | 114.9292 | 115.8046 | 121.99 | 123.5139 | 121.3725 | 122.5599 | 102.9208 | 103.1472 | 103.3264 | 101.7529 | 101.9328 | 101.9311 | 91.7765 | 91.8326 | 91.4569 | 91.5254 | 91.7375 | 91.8101 | 91.6329 | 91.5868 | 91.6759 | 95.1201 | 95.8218 | 95.1364 | 112.8603 | 111.9463 | 113.0938 | 91.3306 | 91.3954 | 91.3351 | 91.6097 | 91.6742 | 91.6377 | 112.9653 | 112.2489 | 113.2532 | 120.9605 | 121.9916 | 123.3431 | 121.3305 | 118.7641 | 119.2463 | 120.2965 | 122.0949 | 122.724 | 111.5487 | 111.487 | 111.4664 | 111.2756 | 111.0464 | 110.934 | 102.7252 | 102.3466 | 102.4913 | 100.8145 | 100.7415 | 100.8083 | 90.8059 | 90.683 | 90.7822 | 90.908 | 90.9111 | 90.5581 | 90.6924 | 90.9354 | 90.7789 | 90.8202 | 90.6557 | 90.8072 | 91.0171 | 90.9458 | 90.9454 | 91.0173 | 91.044 | 91.011 | 93.9058 | 93.7808 | 93.8533 | 113.3398 | 113.5962 | 113.7622 | 113.1224 | 113.6572 | 113.5664
446 | Frequency Based on POWER METER |  | 69.993 | 69.994 | 70.005 | 74.997 | 74.996 | 75.004 | 45.003 | 45.005 | 44.995 | 40.006 | 39.997 | 40.002 | 40.001 | 40.006 | 39.999 | 18.997 | 18.997 | 19.005 | 19.992 | 19.993 | 20.009 | 40.004 | 39.998 | 39.999 | 42.993 | 43.003 | 43.004 | 43.007 | 42.997 | 42.998 | 70.998 | 70.993 | 70.998 | 74.999 | 74.999 | 74.998 | 74 | 110 | 110 | 110 | 110 | 109.99 | 110 | 110 | 110.01 | 120 | 120 | 120.01 | 120.01 | 120 | 120.02 | 120 | 120 | 119.99 | 120.01 | 120 | 120 | 69.002 | 68.984 | 68.991 | 69.999 | 69.989 | 70 | 40.004 | 40.002 | 40.001 | 18.997 | 19 | 18.995 | 20.01 | 20 | 75 | 75.002 | 74.99 | 43.004 | 43.001 | 43.003 | 42.992 | 45.002 | 44.999 | 45.005 | 45 | 44.99 | 44.995 | 20.008 | 20.006 | 19.997 | 19.996 | 110 | 110 | 110.02 | 110.02 | 120 | 120 | 120 | 119.99 | 120 | 120 | 119.99 | 120.01 | 119.98 | 119.99 | 119.99 | 120 | 120 | 120 | 120 | 119.99 | 120.01 | 120.01 | 120 | 120 | 120.01 | 119.99 | 119.99 | 109.98 | 110 | 110 | 45.005 | 45.001 | 44.994 | 119.99 | 120.01 | 120.01 | 120.01 | 120 | 120 | 120 | 120 | 120 | 110.01 | 110 | 110 | 44.998 | 45.006 | 45.002 | 43.001 | 43 | 43.001 | 40 | 40.003 | 39.993 | 18.996 | 18.999 | 19.004 | 19.996 | 19.998 | 20.01 | 71 | 70.999 | 71 | 76.007 | 75.996 | 76.004 | 119.99 | 120.01 | 120 | 120.01 | 120 | 120.01 | 120 | 120 | 119.99 | 110.01 | 110.01 | 110 | 44.999 | 45.002 | 44.998 | 119.99 | 120 | 119.98 | 119.99 | 120 | 119.99 | 45.003 | 44.996 | 45.003 | 20.001 | 20.004 | 20.007 | 19.003 | 19.01 | 18.997 | 20.001 | 20.002 | 20.003 | 43 | 42.998 | 43.001 | 40.001 | 39.996 | 40.007 | 70.003 | 70.002 | 69.007 | 76.001 | 75.998 | 76.003 | 120.03 | 119.99 | 120 | 120.01 | 119.99 | 120 | 120 | 120.01 | 120 | 120.01 | 120.01 | 119.99 | 119.99 | 119.99 | 120 | 120.03 | 120 | 120 | 109.99 | 110 | 109.99 | 44.994 | 44.996 | 44.997 | 45 | 45.003 | 44.998
447 | Corrected Swept Vol for Hz |  | 765.4714 | 765.4824 | 765.6027 | 820.1972 | 820.1863 | 820.2737 | 492.1708 | 492.1927 | 492.0833 | 437.5216 | 437.4232 | 437.4779 | 437.4669 | 437.5216 | 437.4451 | 207.7588 | 207.7588 | 207.8463 | 218.6405 | 218.6514 | 218.8264 | 437.4997 | 437.4341 | 437.4451 | 470.1886 | 470.298 | 470.3089 | 470.3418 | 470.2324 | 470.2433 | 776.4625 | 776.4078 | 776.4625 | 820.2191 | 820.2191 | 820.2081 | 809.2936 | 1203.004 | 1203.004 | 1203.004 | 1203.004 | 1202.8946 | 1203.004 | 1203.004 | 1203.1134 | 1312.368 | 1312.368 | 1312.4774 | 1312.4774 | 1312.368 | 1312.5867 | 1312.368 | 1312.368 | 1312.2586 | 1312.4774 | 1312.368 | 1312.368 | 754.6335 | 754.4366 | 754.5132 | 765.5371 | 765.4277 | 765.548 | 437.4997 | 437.4779 | 437.4669 | 207.7588 | 207.7916 | 207.7369 | 218.8374 | 218.728 | 820.23 | 820.2519 | 820.1206 | 470.3089 | 470.2761 | 470.298 | 470.1777 | 492.1599 | 492.1271 | 492.1927 | 492.138 | 492.0286 | 492.0833 | 218.8155 | 218.7936 | 218.6952 | 218.6843 | 1203.004 | 1203.004 | 1203.2227 | 1203.2227 | 1312.368 | 1312.368 | 1312.368 | 1312.2586 | 1312.368 | 1312.368 | 1312.2586 | 1312.4774 | 1312.1493 | 1312.2586 | 1312.2586 | 1312.368 | 1312.368 | 1312.368 | 1312.368 | 1312.2586 | 1312.4774 | 1312.4774 | 1312.368 | 1312.368 | 1312.4774 | 1312.2586 | 1312.2586 | 1202.7853 | 1203.004 | 1203.004 | 492.1927 | 492.1489 | 492.0724 | 1312.2586 | 1312.4774 | 1312.4774 | 1312.4774 | 1312.368 | 1312.368 | 1312.368 | 1312.368 | 1312.368 | 1203.1134 | 1203.004 | 1203.004 | 492.1161 | 492.2036 | 492.1599 | 470.2761 | 470.2652 | 470.2761 | 437.456 | 437.4888 | 437.3794 | 207.7479 | 207.7807 | 207.8353 | 218.6843 | 218.7061 | 218.8374 | 776.4844 | 776.4735 | 776.4844 | 831.243 | 831.1227 | 831.2101 | 1312.2586 | 1312.4774 | 1312.368 | 1312.4774 | 1312.368 | 1312.4774 | 1312.368 | 1312.368 | 1312.2586 | 1203.1134 | 1203.1134 | 1203.004 | 492.1271 | 492.1599 | 492.1161 | 1312.2586 | 1312.368 | 1312.1493 | 1312.2586 | 1312.368 | 1312.2586 | 492.1708 | 492.0943 | 492.1708 | 218.7389 | 218.7717 | 218.8046 | 207.8244 | 207.901 | 207.7588 | 218.7389 | 218.7499 | 218.7608 | 470.2652 | 470.2433 | 470.2761 | 437.4669 | 437.4123 | 437.5326 | 765.5808 | 765.5699 | 754.6882 | 831.1773 | 831.1445 | 831.1992 | 1312.6961 | 1312.2586 | 1312.368 | 1312.4774 | 1312.2586 | 1312.368 | 1312.368 | 1312.4774 | 1312.368 | 1312.4774 | 1312.4774 | 1312.2586 | 1312.2586 | 1312.2586 | 1312.368 | 1312.6961 | 1312.368 | 1312.368 | 1202.8946 | 1203.004 | 1202.8946 | 492.0724 | 492.0943 | 492.1052 | 492.138 | 492.1708 | 492.1161
448 | Corrected VE% Based on Swept Hz above |  | 95.6138 | 95.5759 | 95.5841 | 95.1706 | 95.3599 | 95.2629 | 94.6687 | 94.5708 | 94.5086 | 93.0692 | 93.0628 | 93.6619 | 93.6028 | 93.404 | 93.5311 | 87.0653 | 87.0511 | 87.3277 | 88.7089 | 88.8757 | 90.1312 | 93.0763 | 93.0323 | 93.2858 | 93.1204 | 93.2297 | 93.2317 | 92.9557 | 93.3423 | 93.078 | 95.3279 | 95.2846 | 95.3216 | 95.0044 | 94.7955 | 94.6975 | 95.2262 | 94.7324 | 94.8868 | 94.9415 | 94.8658 | 94.6885 | 94.6221 | 94.9078 | 94.8339 | 93.0018 | 93.1605 | 93.2593 | 93.6538 | 93.7235 | 93.5102 | 93.9455 | 93.8835 | 93.7546 | 91.4575 | 91.5305 | 91.5329 | 93.3393 | 93.1032 | 93.1911 | 93.9157 | 94.3062 | 94.0483 | 90.2491 | 90.3324 | 90.1362 | 79.1147 | 80.7385 | 75.1317 | 82.4048 | 83.1243 | 93.2508 | 93.1331 | 93.3341 | 90.9786 | 90.8152 | 91.1208 | 91.0485 | 91.8273 | 92.201 | 91.9572 | 91.7495 | 92.0616 | 92.018 | 80.8852 | 83.0009 | 81.1238 | 83.6378 | 92.8795 | 92.894 | 92.976 | 92.974 | 92.3383 | 92.2948 | 92.1274 | 92.3788 | 92.5992 | 92.5817 | 95.1821 | 95.294 | 95.5025 | 95.5004 | 95.4101 | 95.3973 | 95.4721 | 95.5802 | 95.772 | 95.6607 | 95.9082 | 96.1706 | 96.1108 | 96.159 | 96.437 | 96.4757 | 96.4977 | 96.6747 | 96.7502 | 96.8656 | 94.0195 | 94.0829 | 94.3488 | 95.436 | 95.313 | 95.3545 | 96.2325 | 95.8601 | 95.9635 | 96.4336 | 96.1592 | 96.7221 | 96.8044 | 96.7931 | 96.8775 | 94.3812 | 94.4654 | 94.8659 | 93.0313 | 93.0994 | 93.1 | 92.9725 | 92.7447 | 92.9139 | 79.9064 | 80.5134 | 84.7357 | 86.7045 | 84.8064 | 85.4846 | 96.1085 | 96.2286 | 96.2804 | 95.3313 | 95.4848 | 95.4423 | 94.7408 | 94.8839 | 94.6602 | 95.0519 | 95.2797 | 95.3688 | 95.3185 | 95.3008 | 95.3035 | 96.327 | 96.8995 | 96.3799 | 93.7126 | 93.375 | 93.7167 | 95.7342 | 95.7837 | 95.7527 | 95.8601 | 95.9113 | 95.9675 | 93.9741 | 93.5624 | 94.3853 | 85.234 | 85.8953 | 86.7501 | 84.3838 | 84.2862 | 84.6735 | 85.2042 | 86.2392 | 86.7063 | 92.9164 | 92.8234 | 92.7767 | 92.4526 | 92.4079 | 92.3044 | 96.4462 | 95.7986 | 96.0178 | 95.5828 | 95.5162 | 95.6043 | 94.7136 | 94.6826 | 94.7568 | 94.8841 | 94.9096 | 94.6166 | 95.0637 | 95.3399 | 95.144 | 95.2061 | 95.0717 | 95.3139 | 95.3223 | 95.2604 | 95.2506 | 95.2644 | 95.3394 | 95.2583 | 95.9634 | 95.7826 | 95.8968 | 94.25 | 94.5519 | 94.7123 | 94.1376 | 94.568 | 94.2739
449 | IE% based on total power | % | 70.1228 | 70.0686 | 70.1604 | 69.3193 | 69.4852 | 69.4211 | 69.77 | 69.7634 | 69.6846 | 66.6192 | 66.5937 | 67.0309 | 67.0176 | 66.9878 | 66.9147 | 68.5063 | 68.5973 | 68.7675 | 69.4316 | 69.4353 | 70.4238 | 68.6037 | 68.5711 | 68.7545 | 68.3144 | 68.3657 | 68.3812 | 65.2963 | 65.6178 | 65.3727 | 69.4426 | 69.4536 | 69.4307 | 69.0187 | 68.8778 | 68.8175 | 69.2514 | 66.8661 | 67.0133 | 67.0269 | 66.9779 | 66.7957 | 66.8409 | 66.9913 | 66.9656 | 64.3824 | 64.4909 | 64.5638 | 65.0058 | 65.0644 | 64.9102 | 65.1656 | 65.1481 | 65.0824 | 64.0268 | 64.0516 | 64.0304 | 69.0539 | 68.8651 | 68.9405 | 69.3446 | 69.5906 | 69.4751 | 67.243 | 67.2882 | 67.2652 | 62.6294 | 63.9367 | 59.4518 | 65.1457 | 65.6354 | 68.5271 | 68.4787 | 68.6117 | 67.3044 | 67.1265 | 67.4986 | 67.3818 | 67.6272 | 67.8672 | 67.699 | 67.1552 | 67.4125 | 67.4061 | 64.101 | 65.8197 | 64.3 | 66.2626 | 66.2446 | 66.2859 | 66.395 | 66.3603 | 64.6477 | 64.7109 | 64.5709 | 64.9521 | 65.119 | 65.1517 | 66.9892 | 67.0769 | 67.1452 | 67.1842 | 67.0786 | 67.1264 | 67.1662 | 67.1503 | 67.1918 | 67.0382 | 67.3294 | 67.1429 | 67.0563 | 67.1525 | 67.4847 | 67.4594 | 67.5133 | 68.7086 | 68.9296 | 69.0098 | 69.6053 | 69.6375 | 69.757 | 66.8854 | 66.8111 | 66.8684 | 67.2194 | 66.9261 | 66.9741 | 67.5928 | 67.3215 | 67.7374 | 69.218 | 69.2026 | 69.1613 | 70.7265 | 70.8829 | 71.1376 | 69.4439 | 69.5646 | 69.612 | 69.712 | 69.5309 | 69.6086 | 63.0914 | 63.5761 | 66.7122 | 67.984 | 66.719 | 67.3143 | 71.852 | 71.9349 | 72.0606 | 71.1194 | 71.2617 | 71.2156 | 66.8868 | 66.9195 | 66.6465 | 66.9032 | 67.0609 | 67.1092 | 66.9966 | 66.954 | 67.0195 | 69.3334 | 69.8402 | 69.3454 | 69.7693 | 69.4615 | 69.8714 | 66.7551 | 66.8009 | 66.7515 | 66.9705 | 67.02 | 66.986 | 69.8729 | 69.4298 | 70.0988 | 66.8771 | 67.4113 | 68.0192 | 66.4196 | 66.2115 | 66.5016 | 66.7291 | 67.5328 | 67.8479 | 69.0227 | 68.9375 | 68.8748 | 68.8854 | 68.7243 | 68.6731 | 71.6802 | 71.2308 | 71.3775 | 70.4919 | 70.4415 | 70.4832 | 66.1604 | 66.0933 | 66.1709 | 66.2641 | 66.2556 | 65.9989 | 66.3027 | 66.4737 | 66.3582 | 66.387 | 66.2561 | 66.3814 | 66.5468 | 66.4993 | 66.4996 | 66.5531 | 66.568 | 66.5515 | 68.4936 | 68.4039 | 68.4487 | 70.1401 | 70.333 | 70.4252 | 70.025 | 70.3818 | 70.221
450 | Oil Flowmeter (m3/hr) | m3/hr | 3.3203 | 3.1158 | 2.9665 | 3.3055 | 3.3343 | 3.4 | 1.2898 | -0.087323 | -0.087149 | -0.08721 | -0.087407 | -0.087445 | -0.087371 | -0.087287 | -0.087356 | -0.087435 | -0.08743 | -0.087407 | 1.1153 | 1.3586 | 0.95133 | 1.7877 | 1.7826 | 1.7745 | 1.8736 | 1.8327 | 1.798 | 1.7297 | 1.7758 | 1.8303 | 3.2635 | 2.9657 | 2.9667 | 3.4473 | 3.4487 | 3.4911 | 3.1709 | 3.5254 | 3.4988 | 3.4647 | 3.4244 | 3.5817 | 3.4874 | 3.396 | 3.5166 | 3.3631 | 3.4401 | 3.409 | 3.3709 | 3.4555 | 3.4289 | 3.3061 | 3.3695 | 3.2814 | 3.1415 | 3.227 | 3.4368 | 2.4513 | 2.8303 | 2.3925 | 2.7399 | 2.8007 | 2.6863 | 1.7121 | 1.6289 | 1.7105 | 0.95405 | 0.96186 | 0.9611 | 0.95635 | 0.94654 | 3.3347 | 3.225 | 2.9106 | 1.7246 | 1.6962 | 1.815 | 1.7036 | 1.7167 | 1.6121 | 1.6906 | 1.0886 | 0.97593 | 0.76148 | -0.087224 | 1.2108 | 1.632 | 1.2297 | 3.438 | 3.3868 | 3.4775 | 3.4096 | 3.4376 | 3.3661 | 3.1758 | 3.3718 | 3.434 | 3.3974 | 3.0165 | 3.2518 | 3.4668 | 3.1946 | 3.0268 | 3.0704 | 3.4377 | 2.8544 | 2.4486 | 2.4486 | 2.4395 | 2.2385 | 2.3954 | 2.4339 | 2.3551 | 2.33 | 2.3509 | 2.3829 | 2.6506 | 2.1368 | 1.0563 | 1.0465 | 1.0489 | 2.4192 | 2.4118 | 2.4414 | 2.8753 | 3.1463 | 2.9777 | 2.8234 | 2.9772 | 2.7899 | 2.4674 | 2.4217 | 2.4947 | 1.6339 | 1.7331 | 1.6461 | 1.087 | 1.0489 | 1.0594 | 1.0384 | 1.1851 | 0.99594 | -0.087317 | 0.63614 | -0.087444 | 0.64103 | -0.087417 | 1.1103 | 2.1786 | 2.1492 | 1.986 | 2.4165 | 2.3444 | 2.5862 | 2.5215 | 2.5056 | 2.6371 | 2.8738 | 3.0474 | 3.0115 | 2.8429 | 3.0321 | 3.1359 | 2.8283 | 3.2098 | 2.9735 | 1.668 | 1.7092 | 1.7219 | 3.1612 | 3.2919 | 3.3233 | 3.0149 | 3.2999 | 3.008 | 1.7411 | 1.7201 | 1.5864 | 1.4902 | 0.91062 | 0.83756 | 0.83674 | 0.85483 | 0.87748 | 0.83415 | 0.842 | 0.82669 | 1.7246 | 1.7393 | 1.6357 | 1.6306 | 1.4592 | 1.3668 | 2.3871 | 2.5857 | 2.1973 | 2.8468 | 2.9008 | 2.8286 | 3.3881 | 3.2277 | 2.8084 | 2.9125 | 3.2939 | 3.1877 | 3.342 | 3.4541 | 3.4921 | 3.445 | 3.6332 | 3.3433 | 3.49 | 3.3309 | 3.5313 | 3.6822 | 3.4381 | 3.2007 | 3.5994 | 3.4482 | 3.5546 | 1.6782 | 1.6647 | 1.668 | 1.6664 | 1.7121 | 1.795
451 | Pressure Differential meter NRV (AI6) | bar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.000872 | 0.00049 | 0.000292 | 0.000411 | 0.000514 | 0.000865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001686 | 0.001747 | 0.001749 | 0.004556 | 0.004408 | 0.004838 | 0.033904 | 0.033879 | 0.033606 | 0.033046 | 0.032879 | 0.032334 | 0.033953 | 0.034027 | 0.033877 | 0.041266 | 0.041124 | 0.041046 | 0.040974 | 0.040934 | 0.040899 | 0.040901 | 0.040729 | 0.040796 | 0.039796 | 0.039696 | 0.039438 | 0.037649 | 0.037352 | 0.036136 | 0.033378 | 0.032985 | 0.033044 | 0.032201 | 0.031702 | 0.031407 | 0.039343 | 0.039133 | 0.039123 | 0.03901 | 0.038883 | 0.03896 | 0.034662 | 0.034282 | 0.034295 | 0.033896 | 0.033598 | 0.033616 | 0.033506 | 0.033137 | 0.033145 | 0.032846 | 0.032999 | 0.032469 | 0.031778 | 0.031405 | 0.031229 | 0.030181 | 0.029864 | 0.029526 | 0.027817 | 0.028934 | 0.028416
452 | COP - based on total (not incl. econ) |  | 4.6507 | 4.6486 | 4.6421 | 4.6314 | 4.6218 | 4.6249 | 6.8626 | 6.8531 | 6.8641 | 6.5841 | 6.5839 | 6.6218 | 6.6224 | 6.607 | 6.6302 | 8.8856 | 8.8841 | 8.9526 | 9.0691 | 9.0298 | 9.1889 | 6.784 | 6.7712 | 6.8027 | 6.7489 | 6.7629 | 6.7754 | 6.4587 | 6.4797 | 6.463 | 4.609 | 4.6059 | 4.6057 | 4.5848 | 4.5729 | 4.5671 | 4.6036 | 3.2137 | 3.2218 | 3.2175 | 3.219 | 3.2127 | 3.2161 | 3.2287 | 3.2304 | 2.8119 | 2.8188 | 2.8169 | 3.1159 | 3.1313 | 3.1244 | 3.1808 | 3.1893 | 3.1947 | 2.7952 | 2.7912 | 2.7946 | 4.5952 | 4.5768 | 4.5601 | 4.616 | 4.6324 | 4.6255 | 6.6777 | 6.658 | 6.6631 | 8.1467 | 8.3001 | 7.7181 | 8.3971 | 8.529 | 4.5559 | 4.5579 | 4.5622 | 6.6636 | 6.6519 | 6.6773 | 6.6555 | 6.6829 | 6.7261 | 6.7112 | 6.2138 | 6.2182 | 6.2362 | 8.1388 | 8.44 | 8.2908 | 8.5884 | 3.1836 | 3.1779 | 3.1856 | 3.1826 | 3.0945 | 3.116 | 3.1182 | 3.1838 | 3.1919 | 3.2036 | 3.2527 | 3.2566 | 3.2597 | 3.2606 | 3.2942 | 3.289 | 3.2945 | 3.3176 | 2.9347 | 2.9329 | 2.9375 | 3.2265 | 3.2315 | 3.2367 | 3.2992 | 3.3054 | 3.3082 | 3.2923 | 3.3176 | 3.315 | 6.8441 | 6.8484 | 6.8956 | 2.9099 | 2.9061 | 2.9137 | 3.2795 | 3.2662 | 3.2666 | 3.2488 | 3.2402 | 3.2619 | 3.3306 | 3.3333 | 3.3309 | 6.9348 | 6.956 | 7.0273 | 6.8259 | 6.8815 | 6.8448 | 6.9103 | 6.9109 | 6.8968 | 8.2142 | 8.2773 | 8.7487 | 8.794 | 8.6502 | 8.7404 | 4.7576 | 4.7971 | 4.8022 | 4.7436 | 4.7461 | 4.7587 | 2.9112 | 2.9128 | 2.8877 | 3.2049 | 3.2083 | 3.2152 | 3.2575 | 3.2722 | 3.2633 | 3.3226 | 3.3578 | 3.3443 | 6.9075 | 6.8077 | 6.924 | 3.2595 | 3.2565 | 3.2532 | 3.2132 | 3.2079 | 3.1964 | 6.9057 | 6.8646 | 6.9177 | 8.5764 | 8.6523 | 8.7687 | 8.6963 | 8.3703 | 8.4006 | 8.5054 | 8.656 | 8.7121 | 6.8129 | 6.8174 | 6.8257 | 6.7832 | 6.7773 | 6.768 | 4.7528 | 4.7293 | 4.7749 | 4.6923 | 4.6891 | 4.6922 | 2.8768 | 2.8927 | 2.8964 | 2.8976 | 2.8934 | 2.8849 | 3.2473 | 3.2647 | 3.2496 | 3.2524 | 3.252 | 3.2593 | 3.2078 | 3.2053 | 3.2024 | 3.1853 | 3.1855 | 3.1835 | 3.2984 | 3.2714 | 3.2922 | 6.9371 | 6.953 | 6.963 | 6.9212 | 6.9497 | 6.9626
453 | Pressure at Top cover | bar | 3.5798 | 3.567 | 3.575 | 3.5759 | 3.5734 | 3.5665 | 3.8059 | 3.8116 | 3.81 | 3.8056 | 3.827 | 3.8273 | 3.8268 | 3.8206 | 3.813 | 3.8961 | 3.8905 | 3.8809 | 3.8893 | 3.8891 | 3.8912 | 3.8148 | 3.8216 | 3.8204 | 3.7982 | 3.8022 | 3.8117 | 3.8091 | 3.8085 | 3.8143 | 3.5859 | 3.5774 | 3.5644 | 3.5645 | 3.563 | 3.5632 | 3.5722 | 3.2969 | 3.2947 | 3.2965 | 3.2945 | 3.298 | 3.2999 | 3.302 | 3.2996 | 3.0253 | 3.0155 | 3.0169 | 3.2761 | 3.2791 | 3.2746 | 3.2772 | 3.2738 | 3.2787 | 3.0509 | 3.0612 | 3.0566 | 3.615 | 3.6165 | 3.6147 | 3.6195 | 3.6167 | 3.6139 | 3.857 | 3.8573 | 3.8551 | 3.9037 | 3.9039 | 3.9191 | 3.9232 | 3.9108 | 3.6102 | 3.6055 | 3.612 | 3.8473 | 3.8507 | 3.8489 | 3.8593 | 3.848 | 3.8529 | 3.8478 | 3.6488 | 3.6403 | 3.6508 | 3.9001 | 3.9299 | 3.9273 | 3.9264 | 3.3013 | 3.3117 | 3.3208 | 3.3101 | 3.2948 | 3.3079 | 3.3151 | 3.3108 | 3.3044 | 3.323 | 3.3086 | 3.3161 | 3.3031 | 3.3001 | 3.3069 | 3.3158 | 3.3023 | 3.3106 | 3.0252 | 3.0297 | 3.022 | 3.2826 | 3.2704 | 3.2766 | 3.2753 | 3.2706 | 3.2747 | 3.2952 | 3.2884 | 3.2974 | 3.8214 | 3.8161 | 3.8061 | 3.0326 | 3.0296 | 3.0293 | 3.2909 | 3.2824 | 3.2766 | 3.2771 | 3.2836 | 3.2825 | 3.308 | 3.2994 | 3.299 | 3.8098 | 3.8165 | 3.812 | 3.8222 | 3.8266 | 3.8157 | 3.8278 | 3.821 | 3.8192 | 3.8866 | 3.8834 | 3.9027 | 3.8822 | 3.8821 | 3.8775 | 3.5885 | 3.5935 | 3.5907 | 3.5868 | 3.5886 | 3.5929 | 3.0255 | 3.0168 | 3.0161 | 3.2754 | 3.2728 | 3.2658 | 3.2744 | 3.2737 | 3.2674 | 3.3097 | 3.2977 | 3.3042 | 3.8025 | 3.799 | 3.8026 | 3.2695 | 3.2732 | 3.266 | 3.267 | 3.276 | 3.2666 | 3.811 | 3.8003 | 3.8042 | 3.8564 | 3.8532 | 3.8537 | 3.8781 | 3.8098 | 3.8065 | 3.8234 | 3.8191 | 3.8104 | 3.8142 | 3.8123 | 3.7979 | 3.7959 | 3.7892 | 3.792 | 3.5809 | 3.5801 | 3.5786 | 3.5701 | 3.5635 | 3.561 | 3.022 | 3.0261 | 3.0301 | 3.0294 | 3.0273 | 3.022 | 3.2862 | 3.2834 | 3.2836 | 3.2829 | 3.2768 | 3.2829 | 3.2771 | 3.2709 | 3.2774 | 3.273 | 3.2772 | 3.2706 | 3.3064 | 3.2989 | 3.3023 | 3.8254 | 3.8128 | 3.8211 | 3.8309 | 3.827 | 3.8247
454 | Gauge at Top cover | ºC | 5.678 | 5.5744 | 5.6397 | 5.6466 | 5.6264 | 5.5711 | 7.4625 | 7.5062 | 7.4941 | 7.4598 | 7.6245 | 7.6271 | 7.6236 | 7.5758 | 7.5173 | 8.1519 | 8.1091 | 8.0366 | 8.0999 | 8.0989 | 8.1143 | 7.5309 | 7.5837 | 7.5741 | 7.4032 | 7.4343 | 7.5071 | 7.4871 | 7.4827 | 7.5274 | 5.7274 | 5.659 | 5.554 | 5.5549 | 5.5424 | 5.5441 | 5.6172 | 3.3202 | 3.3013 | 3.3168 | 3.2997 | 3.3297 | 3.3457 | 3.3639 | 3.3433 | 0.90512 | 0.8148 | 0.82843 | 3.1407 | 3.1663 | 3.1278 | 3.1499 | 3.1205 | 3.163 | 1.14 | 1.2341 | 1.1915 | 5.9616 | 5.9733 | 5.9596 | 5.9975 | 5.9749 | 5.9531 | 7.8542 | 7.8568 | 7.8399 | 8.2089 | 8.2106 | 8.3253 | 8.3561 | 8.2626 | 5.9229 | 5.8853 | 5.9374 | 7.7804 | 7.8067 | 7.7928 | 7.8723 | 7.7858 | 7.8233 | 7.7843 | 6.2319 | 6.164 | 6.2475 | 8.1819 | 8.4066 | 8.3875 | 8.3808 | 3.3583 | 3.4474 | 3.5254 | 3.4335 | 3.302 | 3.4145 | 3.4765 | 3.4398 | 3.3844 | 3.5445 | 3.4208 | 3.4847 | 3.3735 | 3.3473 | 3.4066 | 3.4822 | 3.3669 | 3.438 | 0.90454 | 0.94593 | 0.87548 | 3.1966 | 3.0913 | 3.1452 | 3.1338 | 3.0931 | 3.129 | 3.3053 | 3.2472 | 3.3247 | 7.5821 | 7.5413 | 7.4644 | 0.97224 | 0.94497 | 0.94239 | 3.2687 | 3.1955 | 3.145 | 3.149 | 3.2054 | 3.1957 | 3.4153 | 3.3421 | 3.3384 | 7.4922 | 7.5443 | 7.5095 | 7.5882 | 7.622 | 7.5378 | 7.6312 | 7.579 | 7.5652 | 8.0797 | 8.0554 | 8.2013 | 8.0466 | 8.0454 | 8.0105 | 5.7488 | 5.789 | 5.7664 | 5.735 | 5.7495 | 5.7842 | 0.90676 | 0.82742 | 0.82048 | 3.1347 | 3.1122 | 3.0518 | 3.1262 | 3.1198 | 3.0655 | 3.4305 | 3.3272 | 3.3833 | 7.4363 | 7.4093 | 7.437 | 3.0834 | 3.1159 | 3.053 | 3.0616 | 3.1399 | 3.0585 | 7.5014 | 7.4194 | 7.4494 | 7.8496 | 7.8254 | 7.8291 | 8.0154 | 7.4923 | 7.4673 | 7.5974 | 7.564 | 7.4969 | 7.5262 | 7.5119 | 7.4009 | 7.3854 | 7.3338 | 7.3552 | 5.687 | 5.6811 | 5.6686 | 5.6001 | 5.5461 | 5.5263 | 0.87524 | 0.91269 | 0.94961 | 0.94347 | 0.92353 | 0.87493 | 3.2276 | 3.2035 | 3.2053 | 3.1992 | 3.1472 | 3.1995 | 3.1497 | 3.0958 | 3.1523 | 3.1144 | 3.1504 | 3.0931 | 3.4016 | 3.3375 | 3.367 | 7.6125 | 7.5159 | 7.5794 | 7.6547 | 7.6249 | 7.6073
455 | Temp after motor | ºC | 23.1507 | 23.0822 | 23.0314 | 22.6296 | 22.5849 | 22.537 | 21.5798 | 21.5382 | 21.4427 | 21.2781 | 21.225 | 21.1688 | 21.0591 | 20.9891 | 20.9295 | 20.0619 | 20.0102 | 19.9554 | 19.0473 | 18.7823 | 18.5746 | 22.5989 | 22.592 | 22.5856 | 22.5851 | 22.5704 | 22.5848 | 22.6203 | 22.6256 | 22.6394 | 22.9762 | 22.9477 | 22.9516 | 22.8491 | 22.8037 | 22.8399 | 22.9652 | 22.8799 | 22.8507 | 22.8429 | 22.7172 | 22.6382 | 22.5915 | 22.5228 | 22.4003 | 21.0526 | 20.9714 | 20.8422 | 20.0663 | 19.939 | 19.8323 | 19.5084 | 19.2777 | 19.1276 | 21.8241 | 21.7414 | 21.6717 | 20.7673 | 20.7147 | 20.6736 | 20.5433 | 20.5384 | 20.5088 | 19.4722 | 19.3873 | 19.3536 | 17.6604 | 17.5894 | 17.5609 | 17.3494 | 17.2473 | 21.2418 | 21.231 | 21.199 | 19.9991 | 19.9789 | 19.937 | 19.643 | 19.5493 | 19.5242 | 19.5208 | 19.0131 | 18.9861 | 18.9567 | 17.6915 | 17.5855 | 17.5831 | 17.5389 | 24.9401 | 24.8996 | 24.9012 | 24.8546 | 24.6722 | 24.6053 | 24.5658 | 24.0188 | 23.912 | 23.5293 | 23.4345 | 23.3864 | 23.3561 | 23.3411 | 23.2462 | 23.1835 | 23.1491 | 23.0527 | 21.7648 | 21.674 | 21.6298 | 21.111 | 21.0415 | 20.9985 | 20.8925 | 20.8325 | 20.7531 | 20.3791 | 20.2051 | 20.0522 | 18.3873 | 18.2884 | 18.2317 | 21.7326 | 21.6181 | 21.5173 | 21.0421 | 20.9607 | 20.882 | 19.942 | 19.887 | 19.8199 | 19.6187 | 19.536 | 19.4589 | 16.7604 | 16.6981 | 16.6225 | 18.2066 | 18.0843 | 18.0152 | 17.3168 | 17.2251 | 17.104 | 19.3907 | 19.3829 | 19.4077 | 19.353 | 19.3431 | 19.3408 | 20.2704 | 20.2346 | 20.2482 | 19.8033 | 19.7573 | 19.7239 | 21.517 | 21.3045 | 21.12 | 20.798 | 20.6835 | 20.5372 | 20.2806 | 20.1086 | 19.9581 | 21.5806 | 21.4833 | 21.4326 | 19.787 | 19.6938 | 19.6292 | 21.7639 | 21.6537 | 21.5465 | 21.1886 | 21.0316 | 20.9139 | 20.3771 | 20.3161 | 20.2994 | 20.8031 | 20.8062 | 20.7471 | 20.8171 | 20.78 | 20.7574 | 20.7338 | 20.727 | 20.6975 | 20.4312 | 20.4336 | 20.3804 | 20.3029 | 20.2559 | 20.2711 | 19.4516 | 19.409 | 19.31 | 18.6886 | 18.5514 | 18.4786 | 22.8618 | 22.823 | 22.775 | 22.7056 | 22.67 | 22.5483 | 21.1121 | 21.1138 | 21.0166 | 20.9721 | 20.8944 | 20.8311 | 20.6277 | 20.5479 | 20.4465 | 20.304 | 20.2152 | 20.1339 | 19.8873 | 19.7832 | 19.736 | 18.0277 | 17.9877 | 18.0087 | 17.9228 | 17.8538 | 17.7851
456 | Pressure after strainer | barA | 3.5968 | 3.5873 | 3.5884 | 3.6017 | 3.5943 | 3.5891 | 3.7889 | 3.7995 | 3.794 | 3.7862 | 3.8072 | 3.807 | 3.811 | 3.7996 | 3.7987 | 3.8575 | 3.8547 | 3.8411 | 3.8506 | 3.8567 | 3.8494 | 3.799 | 3.8079 | 3.8029 | 3.7896 | 3.7916 | 3.8008 | 3.7998 | 3.7963 | 3.8064 | 3.6017 | 3.5936 | 3.5869 | 3.5897 | 3.5944 | 3.587 | 3.594 | 3.3789 | 3.3815 | 3.3771 | 3.3791 | 3.3818 | 3.3835 | 3.3868 | 3.3888 | 3.1203 | 3.1137 | 3.1083 | 3.3788 | 3.3818 | 3.3794 | 3.38 | 3.378 | 3.3809 | 3.1144 | 3.1155 | 3.1128 | 3.5974 | 3.5923 | 3.5883 | 3.5973 | 3.5935 | 3.5906 | 3.8027 | 3.8042 | 3.8035 | 3.8404 | 3.8418 | 3.8577 | 3.8611 | 3.8468 | 3.5918 | 3.5918 | 3.5974 | 3.7965 | 3.8012 | 3.7992 | 3.8079 | 3.7993 | 3.8028 | 3.8017 | 3.6002 | 3.591 | 3.6037 | 3.8266 | 3.857 | 3.8543 | 3.8554 | 3.3572 | 3.3671 | 3.3747 | 3.365 | 3.3672 | 3.383 | 3.3887 | 3.3732 | 3.3736 | 3.3916 | 3.3847 | 3.3921 | 3.3787 | 3.3781 | 3.3858 | 3.3898 | 3.3829 | 3.3872 | 3.1149 | 3.1188 | 3.1122 | 3.384 | 3.3732 | 3.3782 | 3.3736 | 3.369 | 3.3743 | 3.3834 | 3.3709 | 3.3776 | 3.803 | 3.8043 | 3.788 | 3.1147 | 3.116 | 3.1191 | 3.3869 | 3.3778 | 3.3733 | 3.37 | 3.3797 | 3.3825 | 3.3777 | 3.373 | 3.3691 | 3.79 | 3.8016 | 3.7897 | 3.8016 | 3.8004 | 3.7965 | 3.8041 | 3.7984 | 3.7979 | 3.852 | 3.8523 | 3.8661 | 3.8482 | 3.8472 | 3.844 | 3.5865 | 3.5939 | 3.5897 | 3.6003 | 3.5993 | 3.5985 | 3.1162 | 3.1087 | 3.1058 | 3.3819 | 3.3775 | 3.3687 | 3.3765 | 3.3746 | 3.3702 | 3.3889 | 3.3777 | 3.381 | 3.792 | 3.7928 | 3.7994 | 3.378 | 3.3731 | 3.3674 | 3.374 | 3.3809 | 3.3759 | 3.8014 | 3.7902 | 3.7934 | 3.8394 | 3.8376 | 3.8404 | 3.8626 | 3.794 | 3.7913 | 3.8104 | 3.8042 | 3.7946 | 3.8043 | 3.8029 | 3.7912 | 3.7974 | 3.788 | 3.7866 | 3.6 | 3.5988 | 3.5962 | 3.599 | 3.5911 | 3.5855 | 3.1069 | 3.1137 | 3.118 | 3.1204 | 3.1154 | 3.1086 | 3.3846 | 3.3807 | 3.385 | 3.3785 | 3.3734 | 3.3813 | 3.3765 | 3.37 | 3.3721 | 3.3698 | 3.3726 | 3.3709 | 3.3801 | 3.3639 | 3.375 | 3.7952 | 3.7838 | 3.7898 | 3.8022 | 3.7946 | 3.7985
457 | Pressure before suction strainer (H30+Pressure differential) | barA | 3.5968 | 3.5873 | 3.5884 | 3.6017 | 3.5943 | 3.5891 | 3.7889 | 3.7995 | 3.794 | 3.7862 | 3.8072 | 3.807 | 3.811 | 3.7996 | 3.7987 | 3.8575 | 3.8547 | 3.8411 | 3.8506 | 3.8567 | 3.8494 | 3.799 | 3.8079 | 3.8029 | 3.7896 | 3.7916 | 3.8008 | 3.7998 | 3.7963 | 3.8064 | 3.6017 | 3.5936 | 3.5869 | 3.5897 | 3.5944 | 3.587 | 3.594 | 3.3789 | 3.3815 | 3.3771 | 3.3791 | 3.3818 | 3.3835 | 3.3868 | 3.3888 | 3.1203 | 3.1137 | 3.1083 | 3.3788 | 3.3818 | 3.3794 | 3.38 | 3.378 | 3.3809 | 3.1144 | 3.1155 | 3.1128 | 3.5974 | 3.5923 | 3.5883 | 3.5973 | 3.5935 | 3.5906 | 3.8027 | 3.8042 | 3.8035 | 3.8404 | 3.8418 | 3.8577 | 3.8611 | 3.8468 | 3.5918 | 3.5918 | 3.5974 | 3.7965 | 3.8012 | 3.7992 | 3.8079 | 3.7993 | 3.8028 | 3.8017 | 3.6002 | 3.591 | 3.6037 | 3.8266 | 3.857 | 3.8543 | 3.8554 | 3.3572 | 3.3671 | 3.3747 | 3.365 | 3.3672 | 3.383 | 3.3887 | 3.3732 | 3.3736 | 3.3916 | 3.3847 | 3.3921 | 3.3787 | 3.3781 | 3.3858 | 3.3898 | 3.3829 | 3.3872 | 3.1149 | 3.1188 | 3.1122 | 3.384 | 3.3732 | 3.3782 | 3.3736 | 3.369 | 3.3743 | 3.3834 | 3.3709 | 3.3776 | 3.803 | 3.8043 | 3.788 | 3.1147 | 3.116 | 3.1191 | 3.3869 | 3.3778 | 3.3733 | 3.37 | 3.3797 | 3.3825 | 3.3777 | 3.373 | 3.3691 | 3.79 | 3.8016 | 3.7897 | 3.8016 | 3.8004 | 3.7965 | 3.8041 | 3.7984 | 3.7979 | 3.8529 | 3.8528 | 3.8664 | 3.8487 | 3.8477 | 3.8448 | 3.5865 | 3.5939 | 3.5897 | 3.6003 | 3.5993 | 3.5985 | 3.1162 | 3.1087 | 3.1058 | 3.3819 | 3.3775 | 3.3687 | 3.3765 | 3.3746 | 3.3702 | 3.3906 | 3.3795 | 3.3828 | 3.7966 | 3.7972 | 3.8042 | 3.4119 | 3.4069 | 3.401 | 3.407 | 3.4137 | 3.4083 | 3.8353 | 3.8242 | 3.8273 | 3.8806 | 3.8787 | 3.8815 | 3.9036 | 3.835 | 3.8322 | 3.8513 | 3.8449 | 3.8354 | 3.8441 | 3.8426 | 3.8306 | 3.835 | 3.8254 | 3.8227 | 3.6334 | 3.6318 | 3.6292 | 3.6312 | 3.6228 | 3.6169 | 3.1462 | 3.1528 | 3.1572 | 3.1594 | 3.1543 | 3.1475 | 3.4192 | 3.415 | 3.4193 | 3.4124 | 3.407 | 3.415 | 3.41 | 3.4031 | 3.4053 | 3.4026 | 3.4056 | 3.4034 | 3.4119 | 3.3953 | 3.4062 | 3.8254 | 3.8137 | 3.8193 | 3.8301 | 3.8235 | 3.8269
458 | Gauge at suction before strainer | ºC | 5.8159 | 5.7387 | 5.7481 | 5.855 | 5.795 | 5.7536 | 7.3309 | 7.4129 | 7.3707 | 7.3106 | 7.4729 | 7.4713 | 7.5019 | 7.4136 | 7.4071 | 7.8581 | 7.8367 | 7.733 | 7.8054 | 7.8525 | 7.7967 | 7.4091 | 7.4779 | 7.4393 | 7.337 | 7.3518 | 7.4234 | 7.4157 | 7.3881 | 7.4661 | 5.8551 | 5.79 | 5.7359 | 5.7585 | 5.7962 | 5.7363 | 5.7931 | 4.0191 | 4.041 | 4.0037 | 4.0212 | 4.044 | 4.0581 | 4.0857 | 4.1028 | 1.7679 | 1.7087 | 1.6604 | 4.018 | 4.0439 | 4.0237 | 4.0281 | 4.0116 | 4.0364 | 1.7149 | 1.7248 | 1.7011 | 5.8199 | 5.7791 | 5.747 | 5.8193 | 5.7885 | 5.7659 | 7.4376 | 7.4492 | 7.4441 | 7.7278 | 7.7381 | 7.86 | 7.8858 | 7.7763 | 5.7751 | 5.7756 | 5.8203 | 7.3896 | 7.4265 | 7.411 | 7.4778 | 7.4116 | 7.4388 | 7.4301 | 5.8425 | 5.7689 | 5.8709 | 7.6214 | 7.8545 | 7.8336 | 7.8419 | 3.8356 | 3.9195 | 3.9838 | 3.9014 | 3.9206 | 4.0538 | 4.1016 | 3.971 | 3.9743 | 4.1267 | 4.068 | 4.1303 | 4.0176 | 4.0123 | 4.0773 | 4.1109 | 4.0527 | 4.0896 | 1.7195 | 1.7552 | 1.6955 | 4.0623 | 3.9712 | 4.013 | 3.9743 | 3.9357 | 3.9807 | 4.0571 | 3.9514 | 4.0081 | 7.4402 | 7.4504 | 7.3242 | 1.7182 | 1.7293 | 1.7573 | 4.0871 | 4.0095 | 3.9715 | 3.9439 | 4.0261 | 4.0498 | 4.0094 | 3.9691 | 3.9364 | 7.34 | 7.4291 | 7.3371 | 7.4293 | 7.4202 | 7.3903 | 7.4488 | 7.4048 | 7.4005 | 7.823 | 7.822 | 7.9264 | 7.7907 | 7.7835 | 7.7616 | 5.7321 | 5.7925 | 5.7584 | 5.844 | 5.8357 | 5.8295 | 1.7314 | 1.6637 | 1.6382 | 4.0446 | 4.0075 | 3.9326 | 3.9987 | 3.9832 | 3.9456 | 4.1175 | 4.024 | 4.0519 | 7.3907 | 7.3954 | 7.4493 | 4.2966 | 4.2551 | 4.2054 | 4.2559 | 4.3122 | 4.2664 | 7.6886 | 7.6032 | 7.6271 | 8.0343 | 8.0196 | 8.0408 | 8.2085 | 7.686 | 7.6646 | 7.811 | 7.7619 | 7.6896 | 7.7557 | 7.7446 | 7.6527 | 7.6862 | 7.6123 | 7.5921 | 6.1091 | 6.096 | 6.0754 | 6.0911 | 6.0241 | 5.9769 | 2.0003 | 2.0588 | 2.0977 | 2.1176 | 2.072 | 2.012 | 4.3582 | 4.3229 | 4.3587 | 4.3009 | 4.2559 | 4.3225 | 4.2811 | 4.2231 | 4.2411 | 4.2192 | 4.2438 | 4.2251 | 4.2965 | 4.1578 | 4.2492 | 7.6125 | 7.5224 | 7.5658 | 7.6482 | 7.5979 | 7.6239
459 | Gauge after strainer | ºC | 5.8159 | 5.7387 | 5.7481 | 5.855 | 5.795 | 5.7536 | 7.3309 | 7.4129 | 7.3707 | 7.3106 | 7.4729 | 7.4713 | 7.5019 | 7.4136 | 7.4071 | 7.8581 | 7.8367 | 7.733 | 7.8054 | 7.8525 | 7.7967 | 7.4091 | 7.4779 | 7.4393 | 7.337 | 7.3518 | 7.4234 | 7.4157 | 7.3881 | 7.4661 | 5.8551 | 5.79 | 5.7359 | 5.7585 | 5.7962 | 5.7363 | 5.7931 | 4.0191 | 4.041 | 4.0037 | 4.0212 | 4.044 | 4.0581 | 4.0857 | 4.1028 | 1.7679 | 1.7087 | 1.6604 | 4.018 | 4.0439 | 4.0237 | 4.0281 | 4.0116 | 4.0364 | 1.7149 | 1.7248 | 1.7011 | 5.8199 | 5.7791 | 5.747 | 5.8193 | 5.7885 | 5.7659 | 7.4376 | 7.4492 | 7.4441 | 7.7278 | 7.7381 | 7.86 | 7.8858 | 7.7763 | 5.7751 | 5.7756 | 5.8203 | 7.3896 | 7.4265 | 7.411 | 7.4778 | 7.4116 | 7.4388 | 7.4301 | 5.8425 | 5.7689 | 5.8709 | 7.6214 | 7.8545 | 7.8336 | 7.8419 | 3.8356 | 3.9195 | 3.9838 | 3.9014 | 3.9206 | 4.0538 | 4.1016 | 3.971 | 3.9743 | 4.1267 | 4.068 | 4.1303 | 4.0176 | 4.0123 | 4.0773 | 4.1109 | 4.0527 | 4.0896 | 1.7195 | 1.7552 | 1.6955 | 4.0623 | 3.9712 | 4.013 | 3.9743 | 3.9357 | 3.9807 | 4.0571 | 3.9514 | 4.0081 | 7.4402 | 7.4504 | 7.3242 | 1.7182 | 1.7293 | 1.7573 | 4.0871 | 4.0095 | 3.9715 | 3.9439 | 4.0261 | 4.0498 | 4.0094 | 3.9691 | 3.9364 | 7.34 | 7.4291 | 7.3371 | 7.4293 | 7.4202 | 7.3903 | 7.4488 | 7.4048 | 7.4005 | 7.8163 | 7.8183 | 7.9242 | 7.7876 | 7.7795 | 7.755 | 5.7321 | 5.7925 | 5.7584 | 5.844 | 5.8357 | 5.8295 | 1.7314 | 1.6637 | 1.6382 | 4.0446 | 4.0075 | 3.9326 | 3.9987 | 3.9832 | 3.9456 | 4.1033 | 4.0092 | 4.0372 | 7.3554 | 7.3613 | 7.412 | 4.0114 | 3.9698 | 3.9219 | 3.9776 | 4.0357 | 3.9942 | 7.4275 | 7.341 | 7.3661 | 7.7196 | 7.7059 | 7.7278 | 7.8975 | 7.3709 | 7.3497 | 7.4973 | 7.449 | 7.3756 | 7.4501 | 7.4396 | 7.349 | 7.3966 | 7.3244 | 7.3135 | 5.8415 | 5.8315 | 5.8103 | 5.8329 | 5.7695 | 5.7243 | 1.6477 | 1.7087 | 1.748 | 1.7692 | 1.7242 | 1.663 | 4.067 | 4.0347 | 4.0707 | 4.0158 | 3.9729 | 4.0398 | 3.999 | 3.9438 | 3.9618 | 3.9423 | 3.9658 | 3.9515 | 4.0292 | 3.8926 | 3.9862 | 7.38 | 7.2918 | 7.3381 | 7.4342 | 7.375 | 7.4052
460 | Differential pressure Suction [keller 1bar] | bar | 0.011424 | 0.011271 | 0.011116 | 0.026736 | 0.026879 | 0.030243 | 0.02356 | 0.023876 | 0.023433 | 0.019441 | 0.019332 | 0.01955 | 0.019676 | 0.019435 | 0.019145 | -0.041105 | -0.039229 | -0.040285 | -0.033653 | -0.032236 | -0.031732 | -0.044268 | -0.044165 | -0.044208 | -0.041311 | -0.042226 | -0.040987 | -0.041779 | -0.041886 | -0.041437 | -0.011722 | -0.01326 | -0.012592 | -0.0074391 | -0.0085503 | -0.0078958 | -0.010759 | 0.04613 | 0.049175 | 0.051204 | 0.053992 | 0.054408 | 0.052598 | 0.050972 | 0.050516 | 0.053287 | 0.054379 | 0.055519 | 0.07417 | 0.075738 | 0.073887 | 0.075876 | 0.074013 | 0.074297 | 0.063156 | 0.056516 | 0.060244 | -0.012123 | -0.0091849 | -0.011245 | -0.0094513 | -0.0092282 | -0.009319 | -0.042132 | -0.042051 | -0.041508 | -0.051278 | -0.051217 | -0.050828 | -0.051235 | -0.051498 | -0.005309 | -0.0049317 | -0.006027 | -0.037466 | -0.037391 | -0.038116 | -0.0377 | -0.035203 | -0.035145 | -0.035172 | -0.037871 | -0.037969 | -0.03892 | -0.049294 | -0.051488 | -0.052001 | -0.052269 | 0.049699 | 0.050022 | 0.051557 | 0.047706 | 0.068098 | 0.066953 | 0.068172 | 0.06664 | 0.068436 | 0.068001 | 0.079025 | 0.080172 | 0.078024 | 0.07736 | 0.077534 | 0.079187 | 0.079776 | 0.078635 | 0.075592 | 0.077649 | 0.076962 | 0.10702 | 0.10494 | 0.10941 | 0.10827 | 0.10492 | 0.11045 | 0.087841 | 0.089428 | 0.089254 | 0.014405 | 0.01487 | 0.014473 | 0.073074 | 0.073338 | 0.072753 | 0.10212 | 0.099822 | 0.1014 | 0.08201 | 0.088667 | 0.095284 | 0.08453 | 0.08339 | 0.082702 | 0.021499 | 0.021084 | 0.019599 | 0.013034 | 0.012872 | 0.014285 | 0.017987 | 0.017652 | 0.016662 | -0.037548 | -0.036868 | -0.036811 | -0.037746 | -0.037722 | -0.036952 | 0.045826 | 0.04415 | 0.046213 | 0.053161 | 0.053688 | 0.052377 | 0.058628 | 0.063911 | 0.074017 | 0.055086 | 0.057583 | 0.060476 | 0.066768 | 0.067516 | 0.06301 | 0.10767 | 0.10781 | 0.10605 | -0.0072758 | -0.0098827 | -0.0073511 | 0.065007 | 0.068452 | 0.066994 | 0.074807 | 0.067693 | 0.06868 | 0.019697 | 0.020227 | 0.019597 | -0.023863 | -0.022656 | -0.024659 | -0.022513 | -0.025336 | -0.024071 | -0.022332 | -0.022666 | -0.023935 | 0.0050029 | 0.0047886 | 0.0047424 | -0.0046137 | -0.0045518 | -0.0032092 | 0.043979 | 0.042719 | 0.043068 | 0.054124 | 0.053324 | 0.054154 | 0.063219 | 0.062752 | 0.066639 | 0.067605 | 0.06976 | 0.071298 | 0.067211 | 0.068851 | 0.064801 | 0.077124 | 0.075562 | 0.078849 | 0.094239 | 0.091579 | 0.093534 | 0.096018 | 0.099852 | 0.10022 | 0.088829 | 0.086801 | 0.086928 | 0.016402 | 0.018098 | 0.017616 | 0.016747 | 0.018025 | 0.019697
461 | Differential pressure Oil Separator [omega 2bar] | bar | 0.079863 | 0.079262 | 0.079651 | 0.089567 | 0.08907 | 0.088998 | 0.031016 | 0.030582 | 0.030904 | 0.022918 | 0.022818 | 0.023015 | 0.023185 | 0.023005 | 0.022678 | 0.0016981 | 0.0016955 | 0.0018036 | 0.0027025 | 0.0026085 | 0.0027387 | 0.023398 | 0.023484 | 0.023436 | 0.027789 | 0.027768 | 0.028393 | 0.028208 | 0.027901 | 0.028014 | 0.081762 | 0.082045 | 0.081817 | 0.09126 | 0.089749 | 0.089825 | 0.086746 | 0.17904 | 0.17958 | 0.17966 | 0.18097 | 0.17921 | 0.17967 | 0.17922 | 0.18065 | 0.19176 | 0.19159 | 0.19111 | 0.20957 | 0.20968 | 0.21107 | 0.21054 | 0.21022 | 0.2115 | 0.18396 | 0.18493 | 0.18412 | 0.074105 | 0.074336 | 0.074255 | 0.07561 | 0.075639 | 0.076194 | 0.021554 | 0.021333 | 0.021153 | 0.0012244 | 0.0014253 | 0.0013989 | 0.0017453 | 0.0020865 | 0.086221 | 0.085483 | 0.085645 | 0.025934 | 0.026416 | 0.026411 | 0.026438 | 0.029858 | 0.029769 | 0.029679 | 0.027337 | 0.027139 | 0.027514 | 0.0019117 | 0.0018941 | 0.0018606 | 0.0018466 | 0.17038 | 0.1719 | 0.17107 | 0.1716 | 0.20131 | 0.20261 | 0.20184 | 0.20029 | 0.20097 | 0.20151 | 0.20079 | 0.20185 | 0.20004 | 0.20063 | 0.19994 | 0.20165 | 0.20022 | 0.20135 | 0.19257 | 0.19219 | 0.19262 | 0.21408 | 0.21142 | 0.21182 | 0.21075 | 0.21111 | 0.21014 | 0.17984 | 0.17894 | 0.18153 | 0.030596 | 0.030531 | 0.030928 | 0.19432 | 0.19486 | 0.19527 | 0.21522 | 0.2135 | 0.21448 | 0.21383 | 0.21327 | 0.21385 | 0.18204 | 0.18091 | 0.18098 | 0.031274 | 0.031083 | 0.031643 | 0.028206 | 0.027669 | 0.027566 | 0.023554 | 0.022908 | 0.02324 | 0.0012654 | 0.0012836 | 0.00155 | 0.0018736 | 0.0020917 | 0.0021546 | 0.082704 | 0.082116 | 0.081489 | 0.091912 | 0.092317 | 0.091985 | 0.19493 | 0.1956 | 0.19647 | 0.21511 | 0.21617 | 0.21435 | 0.21443 | 0.21521 | 0.21436 | 0.18122 | 0.18015 | 0.18176 | 0.031309 | 0.03091 | 0.031361 | 0.21342 | 0.21279 | 0.21132 | 0.21239 | 0.21243 | 0.21278 | 0.032235 | 0.031828 | 0.031943 | 0.0020602 | 0.0019208 | 0.0019973 | 0.0013927 | 0.0012309 | 0.0013608 | 0.0019755 | 0.0020032 | 0.0019889 | 0.028218 | 0.027754 | 0.027892 | 0.023406 | 0.023429 | 0.023137 | 0.081471 | 0.081341 | 0.079118 | 0.093389 | 0.093145 | 0.093069 | 0.19743 | 0.19683 | 0.19836 | 0.19866 | 0.19975 | 0.19846 | 0.21937 | 0.21772 | 0.21727 | 0.21678 | 0.21679 | 0.21623 | 0.21745 | 0.21602 | 0.21573 | 0.21641 | 0.21674 | 0.21587 | 0.1843 | 0.18413 | 0.18511 | 0.031765 | 0.031882 | 0.032136 | 0.032057 | 0.031905 | 0.031973
462 | Oil Sump pressure | bar | 10.8801 | 10.8738 | 10.8964 | 10.8731 | 10.8853 | 10.8626 | 8.5692 | 8.5965 | 8.5772 | 8.5126 | 8.5586 | 8.5617 | 8.5665 | 8.5467 | 8.5287 | 7.3289 | 7.3305 | 7.287 | 7.2915 | 7.3183 | 7.2947 | 8.5406 | 8.5672 | 8.5365 | 8.5182 | 8.5203 | 8.5334 | 8.5412 | 8.542 | 8.5545 | 10.9645 | 10.9414 | 10.9327 | 10.9217 | 10.9291 | 10.9154 | 10.8961 | 13.7476 | 13.7561 | 13.7515 | 13.7525 | 13.7483 | 13.7416 | 13.7401 | 13.7381 | 14.1037 | 14.0787 | 14.0572 | 13.7728 | 13.7389 | 13.7222 | 13.5669 | 13.495 | 13.4872 | 13.9727 | 14.0051 | 14.0048 | 10.8588 | 10.8619 | 10.8836 | 10.8684 | 10.8587 | 10.8422 | 8.5148 | 8.5378 | 8.5269 | 7.2868 | 7.296 | 7.3226 | 7.3509 | 7.2995 | 10.8503 | 10.8239 | 10.8426 | 8.5272 | 8.5365 | 8.5307 | 8.5663 | 8.5572 | 8.5504 | 8.5481 | 8.5207 | 8.5199 | 8.525 | 7.3547 | 7.3694 | 7.3389 | 7.3258 | 13.5813 | 13.6297 | 13.651 | 13.638 | 13.6866 | 13.6796 | 13.6613 | 13.4842 | 13.4951 | 13.4864 | 13.6402 | 13.6635 | 13.6254 | 13.6329 | 13.5068 | 13.5369 | 13.4986 | 13.44 | 13.9733 | 14.0262 | 13.997 | 13.7762 | 13.7379 | 13.7303 | 13.513 | 13.5169 | 13.5334 | 13.7843 | 13.674 | 13.7188 | 8.5555 | 8.5596 | 8.4999 | 14.0165 | 14.0118 | 13.9882 | 13.512 | 13.4938 | 13.4706 | 13.6528 | 13.68 | 13.6575 | 13.6103 | 13.5785 | 13.5891 | 8.5403 | 8.5559 | 8.5039 | 8.5765 | 8.5417 | 8.5639 | 8.5333 | 8.5087 | 8.5188 | 7.2956 | 7.3009 | 7.2995 | 7.3229 | 7.3083 | 7.2952 | 10.8717 | 10.8204 | 10.8167 | 10.8627 | 10.8632 | 10.8306 | 14.0394 | 14.0159 | 14.0205 | 13.7144 | 13.6976 | 13.6893 | 13.5377 | 13.4648 | 13.4849 | 13.7127 | 13.6306 | 13.5994 | 8.5236 | 8.5925 | 8.5296 | 13.4781 | 13.5 | 13.4991 | 13.6896 | 13.7229 | 13.7414 | 8.5389 | 8.5135 | 8.5302 | 7.3354 | 7.3281 | 7.3191 | 7.3003 | 7.318 | 7.3174 | 7.3141 | 7.2812 | 7.2543 | 8.5659 | 8.5506 | 8.5165 | 8.5557 | 8.5281 | 8.5343 | 10.891 | 10.8729 | 10.8137 | 10.8827 | 10.8623 | 10.8365 | 14.0362 | 13.961 | 13.9599 | 14.0032 | 13.9909 | 13.9492 | 13.4784 | 13.4349 | 13.4776 | 13.463 | 13.425 | 13.472 | 13.6467 | 13.6215 | 13.6367 | 13.6915 | 13.7228 | 13.712 | 13.6163 | 13.6578 | 13.6104 | 8.5179 | 8.4986 | 8.5119 | 8.5379 | 8.5222 | 8.5072
463
464
465 | Economiser Calculations (Ignore if not running economised)
466 | Item
467 | Assumed Liq Approach @ Economiser | ºC | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
468 | Pressure @ Econ@Compressor | BarA | 8.4122 | 8.3863 | 8.3756 | 8.2964 | 8.2792 | 8.2753 | 8.102 | 8.0947 | 8.0819 | 8.0613 | 8.0515 | 8.0407 | 8.0219 | 8.0117 | 8.0032 | 7.8814 | 7.8635 | 7.8615 | 7.7608 | 7.7299 | 7.7267 | 8.3739 | 8.3785 | 8.3743 | 8.3887 | 8.3909 | 8.3951 | 8.4105 | 8.4154 | 8.4131 | 8.4665 | 8.4716 | 8.4632 | 8.4403 | 8.4471 | 8.4529 | 8.4622 | 8.437 | 8.4356 | 8.4334 | 8.4098 | 8.4042 | 8.3926 | 8.3812 | 8.3533 | 8.088 | 8.0736 | 8.0436 | 7.8913 | 7.8766 | 7.8545 | 7.7996 | 7.7697 | 7.7737 | 8.4721 | 8.4522 | 8.4436 | 8.234 | 8.2236 | 8.2227 | 8.1699 | 8.1704 | 8.1603 | 7.9611 | 7.9505 | 7.9479 | 7.7678 | 7.7624 | 7.7525 | 7.7264 | 7.718 | 8.3037 | 8.295 | 8.2789 | 8.0887 | 8.0956 | 8.0862 | 8.0374 | 8.024 | 8.0136 | 8.0114 | 7.8993 | 7.8961 | 7.8928 | 7.7666 | 7.7533 | 7.752 | 7.757 | 8.9966 | 8.9857 | 8.9795 | 8.9769 | 8.8824 | 8.8671 | 8.8562 | 8.7487 | 8.7354 | 8.6794 | 8.8807 | 8.8701 | 8.8601 | 8.8601 | 8.8366 | 8.8188 | 8.803 | 8.7805 | 8.4585 | 8.4446 | 8.4312 | 8.3059 | 8.2927 | 8.2723 | 8.2481 | 8.2316 | 8.2163 | 8.1345 | 8.0984 | 8.0683 | 7.744 | 7.7269 | 7.7258 | 8.4467 | 8.4234 | 8.4077 | 8.3 | 8.284 | 8.2754 | 8.1488 | 8.1331 | 8.1158 | 8.0749 | 8.0532 | 8.0264 | 7.5594 | 7.5504 | 7.5345 | 7.8341 | 7.8246 | 7.8102 | 7.7531 | 7.742 | 7.7261 | 8.0665 | 8.0632 | 8.0628 | 8.0669 | 8.0618 | 8.0629 | 8.1815 | 8.1701 | 8.1636 | 8.0727 | 8.0678 | 8.0516 | 8.4408 | 8.3876 | 8.3531 | 8.2698 | 8.2522 | 8.2204 | 8.1659 | 8.1342 | 8.0997 | 8.2913 | 8.2775 | 8.2599 | 7.9204 | 7.9024 | 7.8954 | 8.4482 | 8.4278 | 8.4046 | 8.3458 | 8.3168 | 8.2942 | 8.1616 | 8.1495 | 8.1422 | 8.3379 | 8.3332 | 8.3318 | 8.3273 | 8.3296 | 8.3259 | 8.322 | 8.3177 | 8.3136 | 8.2927 | 8.2925 | 8.2839 | 8.3122 | 8.3091 | 8.303 | 8.1599 | 8.14 | 8.124 | 8.0093 | 7.9911 | 7.9708 | 8.9502 | 8.9378 | 8.9224 | 8.883 | 8.8729 | 8.8346 | 8.6436 | 8.6335 | 8.6221 | 8.6043 | 8.5857 | 8.5756 | 8.5334 | 8.5211 | 8.5079 | 8.4785 | 8.4719 | 8.4505 | 8.4015 | 8.3824 | 8.363 | 8.0539 | 8.0467 | 8.0402 | 8.0186 | 8.0073 | 8.0011
469 | Gauge @ Econ@ Compressor | ºC | 33.1036 | 32.9939 | 32.9486 | 32.6113 | 32.5375 | 32.5212 | 31.773 | 31.7414 | 31.6856 | 31.5957 | 31.5529 | 31.5059 | 31.4236 | 31.3787 | 31.3413 | 30.8037 | 30.724 | 30.7152 | 30.2651 | 30.1259 | 30.1117 | 32.941 | 32.9605 | 32.943 | 33.0039 | 33.0134 | 33.0309 | 33.0964 | 33.1169 | 33.1072 | 33.3326 | 33.3538 | 33.3188 | 33.2222 | 33.2509 | 33.2754 | 33.3143 | 33.2082 | 33.2022 | 33.1929 | 33.0932 | 33.0697 | 33.0203 | 32.9723 | 32.8538 | 31.7125 | 31.6497 | 31.5184 | 30.8476 | 30.7822 | 30.6841 | 30.4392 | 30.3052 | 30.3232 | 33.3559 | 33.2723 | 33.2362 | 32.344 | 32.2993 | 32.2955 | 32.0675 | 32.0698 | 32.0259 | 31.1564 | 31.1095 | 31.0982 | 30.2964 | 30.2721 | 30.2276 | 30.1104 | 30.0725 | 32.6425 | 32.6054 | 32.5363 | 31.7152 | 31.7453 | 31.7046 | 31.4915 | 31.4329 | 31.387 | 31.3774 | 30.8831 | 30.8691 | 30.8544 | 30.2913 | 30.2314 | 30.2253 | 30.2481 | 35.5125 | 35.4688 | 35.4438 | 35.4332 | 35.0513 | 34.9891 | 34.9445 | 34.5054 | 34.4509 | 34.2201 | 35.0441 | 35.0012 | 34.9607 | 34.9607 | 34.8649 | 34.7922 | 34.7278 | 34.6358 | 33.2986 | 33.2404 | 33.1838 | 32.6518 | 32.5954 | 32.5083 | 32.4043 | 32.3334 | 32.2677 | 31.9142 | 31.7574 | 31.6262 | 30.1895 | 30.1124 | 30.1077 | 33.2493 | 33.1507 | 33.0846 | 32.6266 | 32.5584 | 32.5216 | 31.9763 | 31.9083 | 31.833 | 31.6552 | 31.5604 | 31.4431 | 29.3512 | 29.3101 | 29.237 | 30.5932 | 30.5508 | 30.4864 | 30.2306 | 30.1805 | 30.1087 | 31.6187 | 31.6043 | 31.6023 | 31.6202 | 31.598 | 31.6028 | 32.1179 | 32.0684 | 32.0402 | 31.6455 | 31.6244 | 31.5535 | 33.2244 | 32.9991 | 32.853 | 32.4976 | 32.4221 | 32.2856 | 32.0504 | 31.9129 | 31.7631 | 32.5895 | 32.5303 | 32.4551 | 30.9764 | 30.8971 | 30.8659 | 33.2555 | 33.1693 | 33.0714 | 32.8218 | 32.6984 | 32.6019 | 32.0315 | 31.9796 | 31.9478 | 32.7881 | 32.768 | 32.7623 | 32.7433 | 32.7529 | 32.7371 | 32.7204 | 32.7021 | 32.6849 | 32.5954 | 32.5946 | 32.5579 | 32.6789 | 32.6656 | 32.6396 | 32.0242 | 31.9382 | 31.8689 | 31.3684 | 31.2884 | 31.199 | 35.3256 | 35.2753 | 35.2134 | 35.0534 | 35.0124 | 34.8567 | 34.0717 | 34.0302 | 33.9828 | 33.9088 | 33.8316 | 33.7894 | 33.6131 | 33.5618 | 33.5065 | 33.3829 | 33.3553 | 33.2652 | 33.0582 | 32.9772 | 32.8951 | 31.5633 | 31.5323 | 31.5038 | 31.4092 | 31.3593 | 31.3323
470 | Temp Subcooled Liq from Econ@comp | ºC | 38.1036 | 37.9939 | 37.9486 | 37.6113 | 37.5375 | 37.5212 | 36.773 | 36.7414 | 36.6856 | 36.5957 | 36.5529 | 36.5059 | 36.4236 | 36.3787 | 36.3413 | 35.8037 | 35.724 | 35.7152 | 35.2651 | 35.1259 | 35.1117 | 37.941 | 37.9605 | 37.943 | 38.0039 | 38.0134 | 38.0309 | 38.0964 | 38.1169 | 38.1072 | 38.3326 | 38.3538 | 38.3188 | 38.2222 | 38.2509 | 38.2754 | 38.3143 | 38.2082 | 38.2022 | 38.1929 | 38.0932 | 38.0697 | 38.0203 | 37.9723 | 37.8538 | 36.7125 | 36.6497 | 36.5184 | 35.8476 | 35.7822 | 35.6841 | 35.4392 | 35.3052 | 35.3232 | 38.3559 | 38.2723 | 38.2362 | 37.344 | 37.2993 | 37.2955 | 37.0675 | 37.0698 | 37.0259 | 36.1564 | 36.1095 | 36.0982 | 35.2964 | 35.2721 | 35.2276 | 35.1104 | 35.0725 | 37.6425 | 37.6054 | 37.5363 | 36.7152 | 36.7453 | 36.7046 | 36.4915 | 36.4329 | 36.387 | 36.3774 | 35.8831 | 35.8691 | 35.8544 | 35.2913 | 35.2314 | 35.2253 | 35.2481 | 40.5125 | 40.4688 | 40.4438 | 40.4332 | 40.0513 | 39.9891 | 39.9445 | 39.5054 | 39.4509 | 39.2201 | 40.0441 | 40.0012 | 39.9607 | 39.9607 | 39.8649 | 39.7922 | 39.7278 | 39.6358 | 38.2986 | 38.2404 | 38.1838 | 37.6518 | 37.5954 | 37.5083 | 37.4043 | 37.3334 | 37.2677 | 36.9142 | 36.7574 | 36.6262 | 35.1895 | 35.1124 | 35.1077 | 38.2493 | 38.1507 | 38.0846 | 37.6266 | 37.5584 | 37.5216 | 36.9763 | 36.9083 | 36.833 | 36.6552 | 36.5604 | 36.4431 | 34.3512 | 34.3101 | 34.237 | 35.5932 | 35.5508 | 35.4864 | 35.2306 | 35.1805 | 35.1087 | 36.6187 | 36.6043 | 36.6023 | 36.6202 | 36.598 | 36.6028 | 37.1179 | 37.0684 | 37.0402 | 36.6455 | 36.6244 | 36.5535 | 38.2244 | 37.9991 | 37.853 | 37.4976 | 37.4221 | 37.2856 | 37.0504 | 36.9129 | 36.7631 | 37.5895 | 37.5303 | 37.4551 | 35.9764 | 35.8971 | 35.8659 | 38.2555 | 38.1693 | 38.0714 | 37.8218 | 37.6984 | 37.6019 | 37.0315 | 36.9796 | 36.9478 | 37.7881 | 37.768 | 37.7623 | 37.7433 | 37.7529 | 37.7371 | 37.7204 | 37.7021 | 37.6849 | 37.5954 | 37.5946 | 37.5579 | 37.6789 | 37.6656 | 37.6396 | 37.0242 | 36.9382 | 36.8689 | 36.3684 | 36.2884 | 36.199 | 40.3256 | 40.2753 | 40.2134 | 40.0534 | 40.0124 | 39.8567 | 39.0717 | 39.0302 | 38.9828 | 38.9088 | 38.8316 | 38.7894 | 38.6131 | 38.5618 | 38.5065 | 38.3829 | 38.3553 | 38.2652 | 38.0582 | 37.9772 | 37.8951 | 36.5633 | 36.5323 | 36.5038 | 36.4092 | 36.3593 | 36.3323
471 | Enthalphy @ SubC Liq from Econ@comp | ºC | 253.5869 | 253.4243 | 253.357 | 252.8573 | 252.7479 | 252.7238 | 251.6175 | 251.5709 | 251.4884 | 251.3557 | 251.2926 | 251.2231 | 251.1018 | 251.0355 | 250.9804 | 250.1883 | 250.071 | 250.058 | 249.3961 | 249.1916 | 249.1707 | 253.3458 | 253.3747 | 253.3488 | 253.439 | 253.4531 | 253.4791 | 253.5763 | 253.6067 | 253.5923 | 253.9267 | 253.9582 | 253.9062 | 253.7629 | 253.8054 | 253.8419 | 253.8996 | 253.7421 | 253.7332 | 253.7195 | 253.5715 | 253.5367 | 253.4634 | 253.3922 | 253.2165 | 251.5281 | 251.4354 | 251.2417 | 250.253 | 250.1567 | 250.0122 | 249.6521 | 249.455 | 249.4814 | 253.9613 | 253.8372 | 253.7836 | 252.4615 | 252.3954 | 252.3897 | 252.0526 | 252.056 | 251.9911 | 250.7077 | 250.6387 | 250.622 | 249.442 | 249.4063 | 249.3409 | 249.1687 | 249.1132 | 252.9034 | 252.8486 | 252.7462 | 251.5321 | 251.5766 | 251.5165 | 251.2019 | 251.1155 | 251.0478 | 251.0337 | 250.3052 | 250.2846 | 250.2628 | 249.4345 | 249.3466 | 249.3376 | 249.3712 | 257.1753 | 257.1098 | 257.0725 | 257.0565 | 256.4858 | 256.393 | 256.3265 | 255.6714 | 255.5901 | 255.2463 | 256.4752 | 256.4111 | 256.3506 | 256.3506 | 256.2076 | 256.0992 | 256.0029 | 255.8658 | 253.8763 | 253.7899 | 253.7059 | 252.9171 | 252.8336 | 252.7048 | 252.5508 | 252.4458 | 252.3487 | 251.8261 | 251.5944 | 251.4008 | 249.2851 | 249.1718 | 249.1649 | 253.8031 | 253.6568 | 253.5587 | 252.8799 | 252.7789 | 252.7243 | 251.9179 | 251.8174 | 251.7061 | 251.4436 | 251.3036 | 251.1306 | 248.055 | 247.9948 | 247.8878 | 249.8784 | 249.8161 | 249.7214 | 249.3454 | 249.2717 | 249.1663 | 251.3896 | 251.3685 | 251.3654 | 251.3919 | 251.3591 | 251.3662 | 252.1272 | 252.0539 | 252.0122 | 251.4291 | 251.398 | 251.2935 | 253.7661 | 253.4319 | 253.2153 | 252.6889 | 252.5772 | 252.3751 | 252.0274 | 251.8242 | 251.6028 | 252.8249 | 252.7373 | 252.6259 | 250.4426 | 250.3258 | 250.2798 | 253.8123 | 253.6844 | 253.5391 | 253.1691 | 252.9862 | 252.8432 | 251.9994 | 251.9227 | 251.8757 | 253.1191 | 253.0894 | 253.0809 | 253.0527 | 253.067 | 253.0436 | 253.0188 | 252.9918 | 252.9662 | 252.8336 | 252.8325 | 252.7781 | 252.9573 | 252.9376 | 252.8991 | 251.9886 | 251.8615 | 251.7591 | 251.0204 | 250.9023 | 250.7705 | 256.8957 | 256.8206 | 256.728 | 256.489 | 256.4277 | 256.1953 | 255.0254 | 254.9636 | 254.8931 | 254.783 | 254.6682 | 254.6055 | 254.3434 | 254.2671 | 254.185 | 254.0014 | 253.9605 | 253.8267 | 253.5196 | 253.3995 | 253.2777 | 251.3079 | 251.2621 | 251.2201 | 251.0805 | 251.007 | 250.967
472 | Measured Duty | kW | 535.6112 | 534.5778 | 535.096 | 575.9332 | 576.1901 | 574.839 | 366.2443 | 367.0384 | 366.3025 | 320.0279 | 321.9014 | 324.0861 | 324.4098 | 322.8472 | 323.2661 | 145.8013 | 145.7599 | 145.7209 | 157.0245 | 157.7342 | 159.779 | 316.7466 | 317.1455 | 317.5865 | 339.1284 | 339.7522 | 340.5906 | 339.3372 | 340.2333 | 340.2514 | 542.2657 | 540.5213 | 539.7824 | 569.1504 | 568.4215 | 566.3223 | 563.2824 | 779.595 | 781.5283 | 780.9635 | 781.6478 | 780.9613 | 781.2955 | 784.9356 | 786.0378 | 777.4702 | 777.8107 | 777.6258 | 859.6757 | 861.5819 | 859.8804 | 866.3691 | 866.1682 | 865.4049 | 750.519 | 752.0208 | 751.7233 | 520.0429 | 517.9577 | 517.9259 | 532.2875 | 533.8217 | 532.2234 | 312.7819 | 313.4231 | 312.8162 | 132.6045 | 135.4322 | 126.5993 | 146.506 | 147.1696 | 561.359 | 560.7958 | 562.9523 | 336.2688 | 335.9721 | 337.0229 | 338.0377 | 356.3516 | 358.2896 | 357.336 | 338.108 | 338.3261 | 339.5198 | 142.168 | 147.2795 | 143.7895 | 148.2225 | 742.0331 | 745.0422 | 748.0737 | 745.925 | 810.8357 | 815.9196 | 816.5062 | 821.6113 | 824.5786 | 830.4121 | 847.8718 | 851.2695 | 849.69 | 849.5426 | 851.4302 | 852.9516 | 852.2854 | 855.078 | 787.2941 | 788.0393 | 788.8548 | 868.8031 | 865.8954 | 869.0182 | 871.9533 | 871.6753 | 874.0589 | 805.4831 | 804.8007 | 808.0095 | 369.6438 | 370.2102 | 369.5724 | 784.2278 | 784.2737 | 785.754 | 870.3541 | 864.7612 | 864.4495 | 873.7675 | 874.2148 | 880.8346 | 807.4213 | 806.9046 | 807.5146 | 372.2224 | 373.9627 | 374.4374 | 348.2479 | 348.5775 | 348.6336 | 325.236 | 323.9818 | 324.5566 | 132.6938 | 133.7693 | 141.3747 | 151.4369 | 148.0857 | 149.2094 | 549.6542 | 551.7842 | 551.5222 | 589.0355 | 589.7337 | 589.5587 | 780.0139 | 780.1013 | 777.5005 | 859.0997 | 860.3626 | 859.9811 | 863.5574 | 863.8011 | 863.823 | 800.3355 | 803.6893 | 800.0833 | 364.995 | 363.9877 | 366.0042 | 859.5716 | 859.4268 | 858.4508 | 863.3998 | 866.7674 | 865.9582 | 363.0333 | 360.452 | 364.0886 | 146.932 | 148.0221 | 149.6357 | 139.1105 | 136.4022 | 136.8701 | 145.8034 | 147.3633 | 147.8306 | 341.5181 | 341.0331 | 339.9697 | 315.0908 | 314.1686 | 313.8598 | 546.814 | 543.3432 | 536.865 | 591.9918 | 590.5033 | 590.5383 | 761.3078 | 762.9096 | 765.0742 | 767.8807 | 766.7302 | 763.5292 | 847.6568 | 849.3938 | 849.331 | 848.5642 | 846.6905 | 851.2881 | 851.5134 | 849.5747 | 850.3477 | 851.2225 | 852.697 | 852.2296 | 791.0875 | 786.143 | 790.2697 | 365.0771 | 365.2368 | 366.57 | 365.9328 | 367.0517 | 366.4178
473 | COP (Based on Fund. Power) |  | 4.7483 | 4.7472 | 4.7454 | 4.734 | 4.7322 | 4.7327 | 6.6928 | 6.6907 | 6.6985 | 6.4178 | 6.427 | 6.467 | 6.4732 | 6.4581 | 6.478 | 8.4459 | 8.4503 | 8.5038 | 8.6677 | 8.6453 | 8.7921 | 6.5376 | 6.5272 | 6.5548 | 6.4936 | 6.5058 | 6.5182 | 6.1998 | 6.2189 | 6.2056 | 4.6958 | 4.69 | 4.6881 | 4.6621 | 4.6504 | 4.6408 | 4.6769 | 3.5066 | 3.5161 | 3.5125 | 3.5168 | 3.5104 | 3.5154 | 3.5299 | 3.535 | 3.1424 | 3.149 | 3.152 | 3.4716 | 3.4866 | 3.4817 | 3.5343 | 3.5436 | 3.5466 | 3.0751 | 3.0766 | 3.0798 | 4.7247 | 4.7061 | 4.6956 | 4.7581 | 4.7722 | 4.766 | 6.5463 | 6.5356 | 6.5414 | 7.7806 | 7.9293 | 7.3819 | 8.0524 | 8.1688 | 4.6594 | 4.6613 | 4.6718 | 6.4913 | 6.4787 | 6.5075 | 6.502 | 6.5253 | 6.5691 | 6.554 | 6.087 | 6.0915 | 6.1119 | 7.7879 | 8.0887 | 7.9402 | 8.2191 | 3.3934 | 3.3947 | 3.4051 | 3.3997 | 3.3133 | 3.3356 | 3.3372 | 3.399 | 3.4095 | 3.4305 | 3.4712 | 3.479 | 3.4802 | 3.481 | 3.508 | 3.5088 | 3.5134 | 3.5337 | 3.2297 | 3.2289 | 3.2365 | 3.5333 | 3.5334 | 3.5431 | 3.5952 | 3.5997 | 3.6064 | 3.6436 | 3.6653 | 3.6728 | 6.7683 | 6.7779 | 6.813 | 3.2093 | 3.2091 | 3.2175 | 3.5757 | 3.56 | 3.5614 | 3.5763 | 3.5706 | 3.5969 | 3.6874 | 3.6907 | 3.691 | 6.912 | 6.939 | 7.0018 | 6.7348 | 6.7852 | 6.7601 | 6.8371 | 6.8353 | 6.8286 | 7.7567 | 7.8177 | 8.2646 | 8.3143 | 8.1775 | 8.2605 | 4.9019 | 4.9372 | 4.9437 | 4.8931 | 4.8981 | 4.9097 | 3.2111 | 3.2182 | 3.1999 | 3.5195 | 3.5259 | 3.5336 | 3.57 | 3.5839 | 3.5827 | 3.6568 | 3.6892 | 3.674 | 6.7835 | 6.7009 | 6.8085 | 3.5272 | 3.5274 | 3.5259 | 3.5119 | 3.5153 | 3.509 | 6.7172 | 6.6757 | 6.7322 | 8.0234 | 8.0944 | 8.1997 | 8.1247 | 7.819 | 7.8494 | 7.9552 | 8.0924 | 8.1396 | 6.5961 | 6.5979 | 6.6028 | 6.563 | 6.5526 | 6.5452 | 4.9059 | 4.895 | 4.9254 | 4.8548 | 4.8521 | 4.8576 | 3.1084 | 3.1213 | 3.1282 | 3.1363 | 3.1333 | 3.1258 | 3.4843 | 3.4999 | 3.4904 | 3.4935 | 3.4922 | 3.5027 | 3.4747 | 3.4715 | 3.4721 | 3.4646 | 3.4671 | 3.4674 | 3.6027 | 3.5799 | 3.602 | 6.7701 | 6.7825 | 6.7965 | 6.767 | 6.7969 | 6.8083
474
475 | Pressure drop suction pipe to filter | kPa | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0872 | 0.049 | 0.0292 | 0.0411 | 0.0514 | 0.0865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1686 | 0.1747 | 0.1749 | 0.4556 | 0.4408 | 0.4838 | 3.3904 | 3.3879 | 3.3606 | 3.3046 | 3.2879 | 3.2334 | 3.3953 | 3.4027 | 3.3877 | 4.1266 | 4.1124 | 4.1046 | 4.0974 | 4.0934 | 4.0899 | 4.0901 | 4.0729 | 4.0796 | 3.9796 | 3.9696 | 3.9438 | 3.7649 | 3.7352 | 3.6136 | 3.3378 | 3.2985 | 3.3044 | 3.2201 | 3.1702 | 3.1407 | 3.9343 | 3.9133 | 3.9123 | 3.901 | 3.8883 | 3.896 | 3.4662 | 3.4282 | 3.4295 | 3.3896 | 3.3598 | 3.3616 | 3.3506 | 3.3137 | 3.3145 | 3.2846 | 3.2999 | 3.2469 | 3.1778 | 3.1405 | 3.1229 | 3.0181 | 2.9864 | 2.9526 | 2.7817 | 2.8934 | 2.8416
476 | Pressure drop filter to top cover | kPa | 9.3556 | 9.867 | 10.041 | 10.0932 | 11.4324 | 11.209 | 7.7079 | 7.1561 | 7.7607 | 6.2366 | 6.9865 | 5.6254 | 6.3103 | 7.8986 | 5.5828 | 0 | 0.082 | 0 | 0 | 0 | 0 | 3.1969 | 3.6495 | 3.4924 | 6.0112 | 5.3141 | 4.7325 | 0.4242 | 0.9007 | 1.3462 | 13.4567 | 12.8145 | 14.0343 | 9.0137 | 13.7328 | 9.5501 | 16.6797 | 24.3422 | 23.6794 | 24.947 | 25.9055 | 24.5853 | 25.553 | 24.3844 | 25.3375 | 37.7201 | 35.1299 | 38.186 | 42.5456 | 40.7081 | 41.3902 | 39.0902 | 38.8113 | 42.5121 | 49.3133 | 47.9484 | 46.151 | 15.7946 | 14.892 | 15.6729 | 12.3263 | 11.5221 | 12.2814 | 1.977 | 2.7919 | 2.9386 | 0.7061 | 0.4924 | 0.4827 | 0.1013 | 0.5646 | 12.5629 | 13.1617 | 12.7395 | 5.4923 | 5.9711 | 5.7888 | 6.5692 | 6.6983 | 6.3541 | 6.6146 | 7.618 | 7.4618 | 7.4094 | 1.8845 | 2.2384 | 2.1011 | 2.4074 | 23.6284 | 22.8935 | 21.9697 | 24.6406 | 45.0461 | 47.7008 | 47.0909 | 41.9282 | 41.3169 | 41.4869 | 30.5252 | 28.3615 | 28.7126 | 27.3807 | 27.1931 | 26.487 | 27.7559 | 26.8388 | 38.7864 | 40.3277 | 38.1956 | 30.5368 | 28.1018 | 39.0821 | 42.9934 | 29.0481 | 31.7378 | 25.4593 | 24.7524 | 24.9427 | 10.7971 | 10.809 | 10.7223 | 25.9915 | 35.2869 | 32.7173 | 37.6353 | 39.385 | 39.3113 | 35.3511 | 28.4517 | 29.4388 | 40.4273 | 59.5074 | 36.6139 | 7.4257 | 7.803 | 8.1209 | 5.1692 | 5.2651 | 4.3763 | 7.4811 | 7.4955 | 7.1221 | 0 | 0 | 0 | 0 | 0 | 0 | 11.7822 | 12.4837 | 13.0659 | 5.7835 | 6.8343 | 8.8266 | 27.6218 | 33.1093 | 30.4785 | 48.6195 | 46.3676 | 47.8737 | 39.7814 | 36.0791 | 39.341 | 26.5329 | 29.6682 | 26.6451 | 11.0688 | 10.6688 | 11.0033 | 43.112 | 41.1941 | 41.1255 | 41.8367 | 41.4384 | 39.4345 | 5.1946 | 5.2704 | 4.9291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.5463 | 7.2274 | 7.0567 | 0.9292 | 0 | 1.9728 | 11.6924 | 11.7298 | 12.5469 | 9.4608 | 9.6518 | 5.236 | 36.9177 | 39.6431 | 39.1354 | 39.645 | 39.3923 | 38.2789 | 42.4492 | 45.4854 | 41.3147 | 43.9512 | 44.3458 | 41.9624 | 41.3932 | 40.014 | 38.3734 | 41.2793 | 41.0078 | 41.4719 | 21.3416 | 19.7082 | 22.1678 | 10.1796 | 10.2948 | 10.2749 | 10.5401 | 10.4276 | 9.8099
477 | suction pressure | kPaG | 359.6849 | 358.7273 | 358.8434 | 360.1719 | 359.4261 | 358.9124 | 378.8857 | 379.9471 | 379.4009 | 378.6241 | 380.7248 | 380.7038 | 381.1009 | 379.9561 | 379.8721 | 385.7473 | 385.4673 | 384.1117 | 385.0573 | 385.6745 | 384.9444 | 379.8975 | 380.7896 | 380.2887 | 378.9643 | 379.1564 | 380.083 | 379.983 | 379.6258 | 380.6361 | 360.1724 | 359.3636 | 358.6933 | 358.973 | 359.4407 | 358.6972 | 359.4025 | 337.889 | 338.1478 | 337.7066 | 337.9142 | 338.1843 | 338.3507 | 338.6777 | 338.8808 | 312.0256 | 311.367 | 310.8297 | 337.8763 | 338.1821 | 337.9432 | 337.9959 | 337.7999 | 338.0941 | 311.4359 | 311.5452 | 311.2819 | 359.7353 | 359.2282 | 358.8301 | 359.7274 | 359.3458 | 359.0642 | 380.2666 | 380.4178 | 380.3512 | 384.0429 | 384.1782 | 385.7722 | 386.1108 | 384.6773 | 359.1791 | 359.1847 | 359.7407 | 379.645 | 380.1229 | 379.9231 | 380.788 | 379.9297 | 380.2826 | 380.1696 | 360.0161 | 359.1019 | 360.3694 | 382.6551 | 385.7011 | 385.427 | 385.5362 | 335.7212 | 336.7107 | 337.4706 | 336.4968 | 336.7241 | 338.2995 | 338.8673 | 337.3198 | 337.3585 | 339.165 | 338.4688 | 339.2078 | 337.8717 | 337.8089 | 338.579 | 338.9777 | 338.2865 | 338.7249 | 311.4866 | 311.8845 | 311.2193 | 338.4002 | 337.3218 | 337.8163 | 337.359 | 336.9022 | 337.4341 | 338.3397 | 337.0876 | 337.7584 | 380.3008 | 380.4337 | 378.7995 | 311.4728 | 311.5957 | 311.9075 | 338.6946 | 337.7758 | 337.3257 | 336.9997 | 337.9719 | 338.2524 | 337.774 | 337.2975 | 336.9111 | 379.0038 | 380.1573 | 378.9663 | 380.159 | 380.0419 | 379.6545 | 380.4125 | 379.8428 | 379.7868 | 385.2003 | 385.2262 | 386.6148 | 384.8247 | 384.7193 | 384.3981 | 358.6461 | 359.3946 | 358.9721 | 360.0346 | 359.931 | 359.8542 | 311.6193 | 310.866 | 310.5832 | 338.1907 | 337.7512 | 336.8657 | 337.6472 | 337.4635 | 337.0198 | 338.887 | 337.7717 | 338.1028 | 379.2034 | 379.2797 | 379.9354 | 337.7973 | 337.3051 | 336.7395 | 337.3976 | 338.0853 | 337.5939 | 380.1358 | 379.0163 | 379.3415 | 383.9362 | 383.7568 | 384.0437 | 386.2641 | 379.4038 | 379.129 | 381.0415 | 380.4152 | 379.4645 | 380.4286 | 380.2928 | 379.1196 | 379.7355 | 378.8014 | 378.6609 | 360.0036 | 359.8798 | 359.6157 | 359.8962 | 359.1089 | 358.549 | 310.6888 | 311.3664 | 311.804 | 312.0395 | 311.5394 | 310.8583 | 338.4565 | 338.0733 | 338.4999 | 337.8496 | 337.3418 | 338.1343 | 337.6515 | 336.9979 | 337.2106 | 336.9798 | 337.2578 | 337.0887 | 338.0084 | 336.3936 | 337.4997 | 379.5214 | 378.3807 | 378.9794 | 380.2234 | 379.4562 | 379.847
478
479
480 | Refrigerant Mass Flow (@ Suction) | Kg/s | 3.4113 | 3.3961 | 3.3989 | 3.6032 | 3.6028 | 3.5954 | 2.245 | 2.2506 | 2.2466 | 1.9719 | 1.9843 | 1.9989 | 2.0022 | 1.9923 | 1.9941 | 0.90279 | 0.90239 | 0.90339 | 0.95738 | 0.96313 | 0.97594 | 1.9955 | 2.0039 | 2.0079 | 2.1523 | 2.1567 | 2.1625 | 2.1544 | 2.1618 | 2.1624 | 3.4232 | 3.4153 | 3.4132 | 3.6009 | 3.6014 | 3.5939 | 3.5601 | 4.9802 | 4.9928 | 4.989 | 4.9863 | 4.9803 | 4.9786 | 4.9947 | 4.986 | 4.9395 | 4.9277 | 4.9444 | 5.3674 | 5.3761 | 5.3614 | 5.3669 | 5.3656 | 5.3682 | 4.872 | 4.8748 | 4.8678 | 3.2563 | 3.2448 | 3.2439 | 3.3194 | 3.3287 | 3.3173 | 1.9283 | 1.927 | 1.9185 | 0.81133 | 0.82824 | 0.77394 | 0.89741 | 0.9016 | 3.5591 | 3.5572 | 3.5789 | 2.0998 | 2.0996 | 2.1068 | 2.1139 | 2.2208 | 2.2316 | 2.2242 | 2.0907 | 2.0913 | 2.0981 | 0.87332 | 0.89993 | 0.87827 | 0.90689 | 4.8635 | 4.8719 | 4.8808 | 4.8639 | 5.295 | 5.2907 | 5.2826 | 5.1749 | 5.1771 | 5.2175 | 5.2843 | 5.3043 | 5.293 | 5.2932 | 5.3034 | 5.3113 | 5.3045 | 5.3194 | 5.076 | 5.0697 | 5.0724 | 5.5437 | 5.5157 | 5.5064 | 5.491 | 5.4786 | 5.4826 | 5.1164 | 5.0837 | 5.1154 | 2.2677 | 2.2716 | 2.2653 | 5.0749 | 5.0757 | 5.089 | 5.5529 | 5.5225 | 5.5315 | 5.5029 | 5.513 | 5.5463 | 5.1119 | 5.0984 | 5.0966 | 2.2775 | 2.2874 | 2.2923 | 2.136 | 2.1344 | 2.1239 | 1.9791 | 1.9755 | 1.9819 | 0.82416 | 0.8299 | 0.87659 | 0.93914 | 0.9198 | 0.92729 | 3.4629 | 3.4756 | 3.474 | 3.6779 | 3.6857 | 3.6916 | 5.0125 | 5.0357 | 5.0512 | 5.4851 | 5.4954 | 5.4851 | 5.4924 | 5.4956 | 5.4857 | 5.0671 | 5.0496 | 5.0464 | 2.2403 | 2.2349 | 2.2491 | 5.4632 | 5.4592 | 5.4415 | 5.4556 | 5.4714 | 5.4878 | 2.2689 | 2.2507 | 2.274 | 0.92179 | 0.92952 | 0.93996 | 0.87424 | 0.85589 | 0.85789 | 0.91385 | 0.92291 | 0.92444 | 2.1433 | 2.1403 | 2.1294 | 1.9858 | 1.9776 | 1.975 | 3.4291 | 3.4057 | 3.3592 | 3.6794 | 3.6723 | 3.6718 | 5.0149 | 5.0236 | 5.038 | 5.052 | 5.0508 | 5.0328 | 5.4704 | 5.4838 | 5.4722 | 5.4733 | 5.4556 | 5.4781 | 5.4703 | 5.4575 | 5.468 | 5.4615 | 5.4676 | 5.4607 | 5.0459 | 5.016 | 5.0417 | 2.2674 | 2.2661 | 2.2739 | 2.269 | 2.2731 | 2.2662
481 | Oil Density (User input) | Kg/m^3 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000
482 | Time @ condition (user input) | Secs | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600
483 | Oil Returned to Separator (user input) | Ltrs
484 | Convert above to Cubic Metre | m^3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
485 | Density*M^3 = Mass | Kg/m^3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
486 | Divide by time @ condition | Kg/s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
487 | % OIL CARRY OVER | % | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0