## Summary
| Conditions | Logs | f [Hz] | PR | VR | SG [°C] | DG [°C] | SSH [°C] | Duty [kW] | Flow rate [m3/h] | IE [%] | VE [%] | COP [-]
0 | 5.8 / 42.0 @ 70 Hz | 1343-1344-1345 | 70 | 3 | 2.6 | 5.7675 | 42.033 | 9.6185 | 540.0435 | 731.769 | 70.1173 | 95.5912 | 4.6471
1 | 5.8 / 41.9 @ 75 Hz | 1340-1341-1342 | 75 | 3 | 2.6 | 5.8012 | 41.9346 | 11.7019 | 578.9672 | 781.3772 | 69.4085 | 95.2645 | 4.6261
2 | 7.4 / 33.4 @ 45 Hz | 1337-1338-1339 | 45 | 2.2 | 1.6 | 7.3715 | 33.3538 | 12.8114 | 393.9711 | 465.4878 | 69.7394 | 94.5827 | 6.8599

## Test_log
| Log Number | Unnamed: 1 | 1406 | 1405 | 1404 | 1403 | 1402 | 1401 | 1400 | 1399 | 1398 | 1397 | 1396 | 1395 | 1394 | 1393 | 1392 | 1391 | 1390 | 1389 | 1388 | 1387 | 1386 | 1385 | 1384 | 1383 | 1382 | 1381 | 1380 | 1379 | 1378 | 1377 | 1376 | 1375 | 1374 | 1373 | 1372 | 1371 | 1370 | 1369 | 1368 | 1367 | 1366 | 1365 | 1364 | 1363 | 1362 | 1361 | 1360 | 1359 | 1358 | 1357 | 1356 | 1355 | 1354 | 1353 | 1352 | 1351 | 1350 | 1349 | 1348 | 1347 | 1346 | 1345 | 1344 | 1343 | 1342 | 1341 | 1340 | 1339 | 1338 | 1337 | 1336 | 1335 | 1334 | 1333 | 1332 | 1331 | 1330 | 1329 | 1328 | 1327 | 1326 | 1325 | 1324 | 1323 | 1322 | 1321 | 1320 | 1319 | 1318 | 1317 | 1316 | 1315 | 1314 | 1313 | 1312 | 1311 | 1310 | 1309 | 1308 | 1307 | 1306 | 1305 | 1304 | 1303 | 1302 | 1301 | 1300 | 1299 | 1298 | 1297 | 1296 | 1295 | 1294 | 1293 | 1292 | 1291 | 1290 | 1289 | 1288 | 1287 | 1286 | 1285 | 1284 | 1283 | 1282 | 1281 | 1280 | 1279 | 1278 | 1277 | 1276 | 1275 | 1274 | 1273 | 1272 | 1271 | 1270 | 1269 | 1268 | 1267 | 1266 | 1265 | 1264 | 1263 | 1262 | 1261 | 1260 | 1259 | 1258 | 1257 | 1256 | 1255 | 1254 | 1253 | 1252 | 1251 | 1250 | 1249 | 1248 | 1247 | 1246 | 1245 | 1244 | 1243 | 1242 | 1241 | 1240 | 1239 | 1238 | 1237 | 1236 | 1235 | 1234 | 1233 | 1232 | 1231 | 1230 | 1229 | 1228 | 1227 | 1226 | 1225 | 1224 | 1223 | 1222 | 1221 | 1220 | 1219 | 1218 | 1217 | 1216 | 1215 | 1214 | 1213 | 1212 | 1211 | 1210 | 1209 | 1208 | 1207 | 1206 | 1205 | 1204 | 1203 | 1202 | 1201 | 1200 | 1199 | 1198 | 1197 | 1196 | 1195 | 1194 | 1193 | 1192 | 1191 | 1190 | 1189 | 1188 | 1187 | 1186 | 1185 | 1184 | 1183 | 1182 | 1181 | 1180 | 1179 | 1178 | 1177 | 1176 | 1175 | 1174 | 1173 | 1172 | 1171
0 | Parameters | Units | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs | Labview Outputs
1 | Date |  | 2020-05-14 16:03 | 2020-05-14 16:00 | 2020-05-14 15:58 | 2020-05-14 15:27 | 2020-05-14 15:24 | 2020-05-14 15:18 | 2020-05-14 14:59 | 2020-05-14 14:54 | 2020-05-14 14:51 | 2020-05-14 14:26 | 2020-05-14 14:22 | 2020-05-14 14:19 | 2020-05-14 13:55 | 2020-05-14 13:54 | 2020-05-14 13:54 | 2020-05-14 12:06 | 2020-05-14 12:03 | 2020-05-14 11:59 | 2020-05-14 11:44 | 2020-05-14 11:40 | 2020-05-14 11:37 | 2020-05-13 11:41 | 2020-05-13 11:37 | 2020-05-13 11:32 | 2020-05-13 11:25 | 2020-05-13 11:21 | 2020-05-13 11:17 | 2020-05-12 16:12 | 2020-05-12 16:08 | 2020-05-12 16:04 | 2020-05-12 16:00 | 2020-05-12 15:57 | 2020-05-12 15:54 | 2020-05-12 15:37 | 2020-05-12 15:33 | 2020-05-12 15:30 | 2020-05-12 15:09 | 2020-05-12 15:04 | 2020-05-12 14:51 | 2020-05-12 14:38 | 2020-05-12 14:34 | 2020-05-12 14:31 | 2020-05-12 13:45 | 2020-05-12 13:42 | 2020-05-12 13:38 | 2020-05-12 13:31 | 2020-05-12 13:12 | 2020-05-12 13:08 | 2020-05-12 13:04 | 2020-05-12 12:08 | 2020-05-12 12:05 | 2020-05-12 11:55 | 2020-05-12 11:20 | 2020-05-12 11:16 | 2020-05-12 11:06 | 2020-05-12 10:45 | 2020-05-12 10:42 | 2020-05-12 10:39 | 2020-05-12 10:29 | 2020-05-12 10:24 | 2020-05-12 10:21 | 2020-05-07 14:39 | 2020-05-07 14:31 | 2020-05-07 14:27 | 2020-05-07 14:07 | 2020-05-07 14:03 | 2020-05-07 14:01 | 2020-05-07 13:17 | 2020-05-07 13:15 | 2020-05-07 13:11 | 2020-05-07 13:01 | 2020-05-07 12:58 | 2020-05-07 12:54 | 2020-05-07 12:49 | 2020-05-07 12:45 | 2020-05-07 12:42 | 2020-05-07 11:49 | 2020-05-07 11:46 | 2020-05-07 11:42 | 2020-05-07 10:53 | 2020-05-07 10:43 | 2020-05-07 10:33 | 2020-05-06 16:33 | 2020-05-06 16:30 | 2020-05-06 16:27 | 2020-05-06 16:04 | 2020-05-06 15:58 | 2020-05-06 15:55 | 2020-05-06 15:38 | 2020-05-06 15:35 | 2020-05-06 15:32 | 2020-05-06 14:32 | 2020-05-06 14:29 | 2020-05-06 14:26 | 2020-05-06 13:50 | 2020-05-06 13:47 | 2020-05-06 13:44 | 2020-05-06 12:51 | 2020-05-06 12:31 | 2020-05-06 12:30 | 2020-05-06 12:28 | 2020-05-06 12:19 | 2020-05-06 12:18 | 2020-05-06 12:15 | 2020-05-06 12:11 | 2020-05-06 12:02 | 2020-05-06 10:57 | 2020-05-06 10:54 | 2020-05-06 10:50 | 2020-05-06 10:27 | 2020-05-06 10:24 | 2020-05-06 10:21 | 2020-05-06 10:14 | 2020-05-06 10:10 | 2020-05-06 10:07 | 2020-05-01 15:06 | 2020-05-01 15:02 | 2020-05-01 14:59 | 2020-05-01 14:03 | 2020-05-01 14:01 | 2020-05-01 13:57 | 2020-05-01 13:34 | 2020-05-01 13:31 | 2020-05-01 13:29 | 2020-05-01 12:22 | 2020-05-01 12:19 | 2020-05-01 12:16 | 2020-05-01 10:58 | 2020-05-01 10:55 | 2020-05-01 10:52 | 2020-05-01 10:39 | 2020-05-01 10:34 | 2020-04-30 16:33 | 2020-04-30 16:30 | 2020-04-30 16:26 | 2020-04-30 15:21 | 2020-04-30 15:19 | 2020-04-30 15:17 | 2020-04-30 14:22 | 2020-04-30 14:01 | 2020-04-30 13:58 | 2020-04-30 13:54 | 2020-04-30 12:33 | 2020-04-30 12:29 | 2020-04-30 12:26 | 2020-04-30 11:18 | 2020-04-30 11:06 | 2020-04-30 11:03 | 2020-04-30 11:01 | 2020-04-29 16:20 | 2020-04-29 16:15 | 2020-04-29 16:12 | 2020-04-29 16:10 | 2020-04-29 15:22 | 2020-04-29 15:15 | 2020-04-29 15:11 | 2020-04-29 14:39 | 2020-04-29 14:34 | 2020-04-29 14:19 | 2020-04-28 16:38 | 2020-04-28 16:36 | 2020-04-28 16:30 | 2020-04-28 16:27 | 2020-04-28 16:18 | 2020-04-28 16:12 | 2020-04-28 16:07 | 2020-04-28 16:00 | 2020-04-22 13:14 | 2020-04-22 13:10 | 2020-04-22 13:07 | 2020-04-22 12:45 | 2020-04-22 12:42 | 2020-04-22 12:39 | 2020-04-22 12:34 | 2020-04-22 12:31 | 2020-04-22 12:28 | 2020-04-22 12:15 | 2020-04-22 12:09 | 2020-04-22 12:06 | 2020-04-22 11:03 | 2020-04-22 10:59 | 2020-04-22 10:56 | 2020-04-20 16:27 | 2020-04-20 16:21 | 2020-04-20 16:16 | 2020-04-20 15:54 | 2020-04-20 15:50 | 2020-04-20 15:47 | 2020-04-20 12:48 | 2020-04-20 12:44 | 2020-04-20 12:41 | 2020-04-20 12:32 | 2020-04-20 12:28 | 2020-04-20 12:24 | 2020-04-20 10:49 | 2020-04-20 10:46 | 2020-04-20 10:41 | 2020-04-17 10:56 | 2020-04-17 10:51 | 2020-04-17 10:44 | 2020-04-17 10:12 | 2020-04-17 10:07 | 2020-04-17 10:03 | 2020-04-16 16:15 | 2020-04-16 16:10 | 2020-04-16 16:06 | 2020-04-16 16:00 | 2020-04-16 15:50 | 2020-04-16 15:47 | 2020-04-16 12:26 | 2020-04-16 12:22 | 2020-04-16 12:18 | 2020-04-16 11:49 | 2020-04-16 11:46 | 2020-04-16 11:43 | 2020-04-15 11:35 | 2020-04-15 11:26 | 2020-04-15 11:21 | 2020-04-15 11:08 | 2020-04-15 11:05 | 2020-04-15 11:01 | 2020-04-15 10:52 | 2020-04-15 10:48 | 2020-04-15 10:43 | 2020-04-14 16:34 | 2020-04-14 16:32 | 2020-04-14 16:29 | 2020-04-14 15:19 | 2020-04-14 15:14 | 2020-04-14 15:11 | 2020-04-09 11:53 | 2020-04-09 11:48 | 2020-04-09 11:44 | 2020-04-09 11:32 | 2020-04-09 11:28 | 2020-04-09 11:24
2 | Time |  | 2020-05-14 | 2020-05-14 | 2020-05-14 | 2020-05-14 | 2020-05-14 | 2020-05-14 | 2020-05-14 | 2020-05-14 | 2020-05-14 | 2020-05-14 | 2020-05-14 | 2020-05-14 | 2020-05-14 | 2020-05-14 | 2020-05-14 | 2020-05-14 | 2020-05-14 | 2020-05-14 | 2020-05-14 | 2020-05-14 | 2020-05-14 | 2020-05-13 | 2020-05-13 | 2020-05-13 | 2020-05-13 | 2020-05-13 | 2020-05-13 | 2020-05-12 | 2020-05-12 | 2020-05-12 | 2020-05-12 | 2020-05-12 | 2020-05-12 | 2020-05-12 | 2020-05-12 | 2020-05-12 | 2020-05-12 | 2020-05-12 | 2020-05-12 | 2020-05-12 | 2020-05-12 | 2020-05-12 | 2020-05-12 | 2020-05-12 | 2020-05-12 | 2020-05-12 | 2020-05-12 | 2020-05-12 | 2020-05-12 | 2020-05-12 | 2020-05-12 | 2020-05-12 | 2020-05-12 | 2020-05-12 | 2020-05-12 | 2020-05-12 | 2020-05-12 | 2020-05-12 | 2020-05-12 | 2020-05-12 | 2020-05-12 | 2020-05-07 | 2020-05-07 | 2020-05-07 | 2020-05-07 | 2020-05-07 | 2020-05-07 | 2020-05-07 | 2020-05-07 | 2020-05-07 | 2020-05-07 | 2020-05-07 | 2020-05-07 | 2020-05-07 | 2020-05-07 | 2020-05-07 | 2020-05-07 | 2020-05-07 | 2020-05-07 | 2020-05-07 | 2020-05-07 | 2020-05-07 | 2020-05-06 | 2020-05-06 | 2020-05-06 | 2020-05-06 | 2020-05-06 | 2020-05-06 | 2020-05-06 | 2020-05-06 | 2020-05-06 | 2020-05-06 | 2020-05-06 | 2020-05-06 | 2020-05-06 | 2020-05-06 | 2020-05-06 | 2020-05-06 | 2020-05-06 | 2020-05-06 | 2020-05-06 | 2020-05-06 | 2020-05-06 | 2020-05-06 | 2020-05-06 | 2020-05-06 | 2020-05-06 | 2020-05-06 | 2020-05-06 | 2020-05-06 | 2020-05-06 | 2020-05-06 | 2020-05-06 | 2020-05-06 | 2020-05-06 | 2020-05-01 | 2020-05-01 | 2020-05-01 | 2020-05-01 | 2020-05-01 | 2020-05-01 | 2020-05-01 | 2020-05-01 | 2020-05-01 | 2020-05-01 | 2020-05-01 | 2020-05-01 | 2020-05-01 | 2020-05-01 | 2020-05-01 | 2020-05-01 | 2020-05-01 | 2020-04-30 | 2020-04-30 | 2020-04-30 | 2020-04-30 | 2020-04-30 | 2020-04-30 | 2020-04-30 | 2020-04-30 | 2020-04-30 | 2020-04-30 | 2020-04-30 | 2020-04-30 | 2020-04-30 | 2020-04-30 | 2020-04-30 | 2020-04-30 | 2020-04-30 | 2020-04-29 | 2020-04-29 | 2020-04-29 | 2020-04-29 | 2020-04-29 | 2020-04-29 | 2020-04-29 | 2020-04-29 | 2020-04-29 | 2020-04-29 | 2020-04-28 | 2020-04-28 | 2020-04-28 | 2020-04-28 | 2020-04-28 | 2020-04-28 | 2020-04-28 | 2020-04-28 | 2020-04-22 | 2020-04-22 | 2020-04-22 | 2020-04-22 | 2020-04-22 | 2020-04-22 | 2020-04-22 | 2020-04-22 | 2020-04-22 | 2020-04-22 | 2020-04-22 | 2020-04-22 | 2020-04-22 | 2020-04-22 | 2020-04-22 | 2020-04-20 | 2020-04-20 | 2020-04-20 | 2020-04-20 | 2020-04-20 | 2020-04-20 | 2020-04-20 | 2020-04-20 | 2020-04-20 | 2020-04-20 | 2020-04-20 | 2020-04-20 | 2020-04-20 | 2020-04-20 | 2020-04-20 | 2020-04-17 | 2020-04-17 | 2020-04-17 | 2020-04-17 | 2020-04-17 | 2020-04-17 | 2020-04-16 | 2020-04-16 | 2020-04-16 | 2020-04-16 | 2020-04-16 | 2020-04-16 | 2020-04-16 | 2020-04-16 | 2020-04-16 | 2020-04-16 | 2020-04-16 | 2020-04-16 | 2020-04-15 | 2020-04-15 | 2020-04-15 | 2020-04-15 | 2020-04-15 | 2020-04-15 | 2020-04-15 | 2020-04-15 | 2020-04-15 | 2020-04-14 | 2020-04-14 | 2020-04-14 | 2020-04-14 | 2020-04-14 | 2020-04-14 | 2020-04-09 | 2020-04-09 | 2020-04-09 | 2020-04-09 | 2020-04-09 | 2020-04-09
3 | Conditions |  | 15 / 51.6 ºC SH 10 ºC | 15 / 51.7 ºC SH 9.9 ºC | 14.9 / 51.6 ºC SH 9.8 ºC | 10 / 51.7 ºC SH 11.3 ºC | 10 / 51.7 ºC SH 10.8 ºC | 10 / 51.7 ºC SH 9.4 ºC | 4.9 / 51.7 ºC SH 11.4 ºC | 5 / 51.6 ºC SH 10.6 ºC | 5 / 51.6 ºC SH 10 ºC | 0 / 51.7 ºC SH 10.1 ºC | 0 / 51.7 ºC SH 10.5 ºC | 0 / 51.7 ºC SH 9.8 ºC | -5 / 51.7 ºC SH 12.3 ºC | -5 / 51.6 ºC SH 12.2 ºC | -5 / 51.6 ºC SH 12.1 ºC | 7.8 / 28 ºC SH 10.7 ºC | 7.8 / 28 ºC SH 10.8 ºC | 7.8 / 28 ºC SH 11.1 ºC | 7.8 / 28.1 ºC SH 10.8 ºC | 7.9 / 28 ºC SH 10.8 ºC | 7.8 / 27.9 ºC SH 10.8 ºC | 7.7 / 28 ºC SH 10.6 ºC | 7.7 / 28 ºC SH 10.9 ºC | 7.8 / 28 ºC SH 11 ºC | 7.8 / 28.1 ºC SH 10.9 ºC | 7.8 / 28 ºC SH 10.9 ºC | 7.8 / 27.9 ºC SH 10.9 ºC | 7.4 / 33.2 ºC SH 9.3 ºC | 7.4 / 33.2 ºC SH 9.5 ºC | 7.4 / 33.2 ºC SH 9.5 ºC | 7.5 / 33.3 ºC SH 9.3 ºC | 7.5 / 33.3 ºC SH 9.2 ºC | 7.5 / 33.3 ºC SH 9 ºC | 7.3 / 33.2 ºC SH 10.3 ºC | 7.4 / 33.4 ºC SH 10 ºC | 7.4 / 33.3 ºC SH 9.8 ºC | 7.4 / 33.2 ºC SH 8.4 ºC | 7.4 / 33.3 ºC SH 8 ºC | 7.4 / 33.3 ºC SH 8.1 ºC | 7.5 / 33.2 ºC SH 8.2 ºC | 7.4 / 33.4 ºC SH 8.5 ºC | 7.5 / 33.4 ºC SH 9 ºC | 5.8 / 42.1 ºC SH 9.2 ºC | 5.8 / 41.9 ºC SH 9.2 ºC | 5.8 / 42 ºC SH 9 ºC | 5.8 / 41.9 ºC SH 8.7 ºC | 5.8 / 42.2 ºC SH 9.1 ºC | 5.9 / 42.1 ºC SH 9 ºC | 5.9 / 42 ºC SH 8.9 ºC | 4 / 50.5 ºC SH 9.3 ºC | 4 / 50.5 ºC SH 9.3 ºC | 4 / 50.6 ºC SH 8.9 ºC | 1.7 / 51.8 ºC SH 10.1 ºC | 1.7 / 51.7 ºC SH 9.3 ºC | 1.7 / 51.7 ºC SH 10.5 ºC | 4 / 50.5 ºC SH 9.4 ºC | 4 / 50.6 ºC SH 9.5 ºC | 4 / 50.5 ºC SH 9.5 ºC | 3.9 / 50 ºC SH 9.6 ºC | 4 / 49.9 ºC SH 11 ºC | 4 / 50.1 ºC SH 11.8 ºC | 5.8 / 42.1 ºC SH 9.4 ºC | 5.7 / 42 ºC SH 9.7 ºC | 5.7 / 42.1 ºC SH 9.7 ºC | 5.9 / 41.9 ºC SH 11.7 ºC | 5.8 / 42 ºC SH 11.7 ºC | 5.8 / 41.9 ºC SH 11.7 ºC | 7.3 / 33.3 ºC SH 13 ºC | 7.4 / 33.4 ºC SH 12.8 ºC | 7.4 / 33.3 ºC SH 12.7 ºC | 7.3 / 33.2 ºC SH 11.8 ºC | 7.5 / 33.3 ºC SH 11.5 ºC | 7.5 / 33.4 ºC SH 11.3 ºC | 7.5 / 33.4 ºC SH 11.1 ºC | 7.4 / 33.3 ºC SH 11.1 ºC | 7.4 / 33.2 ºC SH 11.1 ºC | 7.9 / 28.1 ºC SH 9.3 ºC | 7.8 / 28.1 ºC SH 9.2 ºC | 7.7 / 27.9 ºC SH 9 ºC | 7.8 / 27.9 ºC SH 11.2 ºC | 7.9 / 28.1 ºC SH 10.7 ºC | 7.8 / 28 ºC SH 10.6 ºC | 7.4 / 33.3 ºC SH 10 ºC | 7.5 / 33.4 ºC SH 9.5 ºC | 7.4 / 33.3 ºC SH 9.4 ºC | 7.3 / 33.2 ºC SH 8.9 ºC | 7.4 / 33.2 ºC SH 8.8 ºC | 7.4 / 33.2 ºC SH 8.8 ºC | 7.4 / 33.3 ºC SH 8.9 ºC | 7.4 / 33.3 ºC SH 8.8 ºC | 7.5 / 33.3 ºC SH 8.7 ºC | 5.9 / 42.1 ºC SH 11.3 ºC | 5.8 / 42.1 ºC SH 11.2 ºC | 5.7 / 42 ºC SH 11.1 ºC | 5.8 / 42 ºC SH 10.8 ºC | 5.8 / 42 ºC SH 10.6 ºC | 5.7 / 42 ºC SH 10.4 ºC | 5.8 / 42 ºC SH 11.1 ºC | 4 / 50.6 ºC SH 10.3 ºC | 4 / 50.6 ºC SH 10.3 ºC | 4 / 50.6 ºC SH 10.3 ºC | 4 / 50.6 ºC SH 10.4 ºC | 4 / 50.6 ºC SH 10.4 ºC | 4.1 / 50.6 ºC SH 10.4 ºC | 4.1 / 50.6 ºC SH 10.5 ºC | 4.1 / 50.6 ºC SH 10.9 ºC | 1.8 / 51.7 ºC SH 10.3 ºC | 1.7 / 51.6 ºC SH 10.8 ºC | 1.7 / 51.6 ºC SH 10 ºC | 4 / 50.7 ºC SH 10.5 ºC | 4 / 50.6 ºC SH 10.4 ºC | 4 / 50.6 ºC SH 10.4 ºC | 4 / 50.1 ºC SH 11.2 ºC | 4 / 50 ºC SH 11 ºC | 4 / 49.9 ºC SH 10.7 ºC | 1.7 / 51.6 ºC SH 9.4 ºC | 1.7 / 51.7 ºC SH 9.5 ºC | 1.7 / 51.6 ºC SH 9.6 ºC | 5.8 / 42 ºC SH 11.1 ºC | 5.8 / 42 ºC SH 11 ºC | 5.7 / 42.1 ºC SH 11.1 ºC | 5.8 / 42 ºC SH 11.4 ºC | 5.8 / 42 ºC SH 11.5 ºC | 5.8 / 41.9 ºC SH 11.5 ºC | 7.4 / 33.2 ºC SH 10.9 ºC | 7.4 / 33.3 ºC SH 11.3 ºC | 7.4 / 33.3 ºC SH 11.7 ºC | 7.7 / 27.9 ºC SH 10.6 ºC | 7.7 / 28 ºC SH 10.7 ºC | 7.9 / 28.1 ºC SH 10.6 ºC | 7.9 / 28.3 ºC SH 10 ºC | 7.8 / 28 ºC SH 10 ºC | 5.8 / 41.9 ºC SH 9.5 ºC | 5.8 / 41.9 ºC SH 9.3 ºC | 5.8 / 42 ºC SH 8.8 ºC | 7.4 / 33.2 ºC SH 9.6 ºC | 7.4 / 33.2 ºC SH 9.4 ºC | 7.4 / 33.2 ºC SH 9.3 ºC | 7.5 / 33.4 ºC SH 8.9 ºC | 7.4 / 33.3 ºC SH 9.4 ºC | 7.4 / 33.2 ºC SH 9.4 ºC | 7.4 / 33.2 ºC SH 9.5 ºC | 5.8 / 33.2 ºC SH 11 ºC | 5.8 / 33.2 ºC SH 11.1 ºC | 5.9 / 33.2 ºC SH 11 ºC | 7.6 / 28.3 ºC SH 10 ºC | 7.9 / 28.3 ºC SH 10.7 ºC | 7.8 / 28.2 ºC SH 10.8 ºC | 7.8 / 28.1 ºC SH 10.5 ºC | 3.8 / 50.4 ºC SH 9.8 ºC | 3.9 / 50.6 ºC SH 10.1 ºC | 4 / 50.6 ºC SH 10.4 ºC | 3.9 / 50.6 ºC SH 10.5 ºC | 3.9 / 50.6 ºC SH 9.6 ºC | 4.1 / 50.6 ºC SH 10.6 ºC | 4.1 / 50.6 ºC SH 10.9 ºC | 4 / 50 ºC SH 14.9 ºC | 4 / 50.1 ºC SH 15.4 ºC | 4.1 / 50.1 ºC SH 14.8 ºC | 4.1 / 50.6 ºC SH 17.6 ºC | 4.1 / 50.6 ºC SH 17.6 ºC | 4 / 50.5 ºC SH 17.6 ºC | 4 / 50.5 ºC SH 17.6 ºC | 4.1 / 50.2 ºC SH 17.4 ºC | 4.1 / 50.3 ºC SH 17.3 ºC | 4.1 / 50.2 ºC SH 17.4 ºC | 4.1 / 50 ºC SH 17.3 ºC | 1.7 / 51.6 ºC SH 10.4 ºC | 1.8 / 51.6 ºC SH 10.7 ºC | 1.7 / 51.7 ºC SH 10.7 ºC | 4.1 / 50.6 ºC SH 9.6 ºC | 4 / 50.5 ºC SH 9.8 ºC | 4 / 50.5 ºC SH 10.6 ºC | 4 / 50 ºC SH 11.5 ºC | 3.9 / 49.9 ºC SH 11.8 ºC | 4 / 50 ºC SH 12 ºC | 4.1 / 50.7 ºC SH 9.1 ºC | 4 / 50.5 ºC SH 9.9 ºC | 4 / 50.6 ºC SH 9.3 ºC | 7.4 / 33.4 ºC SH 10.2 ºC | 7.5 / 33.4 ºC SH 10 ºC | 7.3 / 33.2 ºC SH 10.3 ºC | 1.7 / 51.7 ºC SH 9.7 ºC | 1.7 / 51.8 ºC SH 9.5 ºC | 1.8 / 51.7 ºC SH 9.3 ºC | 4.1 / 50.1 ºC SH 9.5 ºC | 4 / 50 ºC SH 9.3 ºC | 4 / 50 ºC SH 8.9 ºC | 3.9 / 50.6 ºC SH 10.8 ºC | 4 / 50.6 ºC SH 10.4 ºC | 4 / 50.6 ºC SH 10.5 ºC | 4 / 50.5 ºC SH 9.3 ºC | 4 / 50.5 ºC SH 9.5 ºC | 3.9 / 50.4 ºC SH 9.6 ºC | 7.3 / 33.4 ºC SH 9.4 ºC | 7.4 / 33.5 ºC SH 9.3 ºC | 7.3 / 33.2 ºC SH 9.1 ºC | 7.4 / 33.4 ºC SH 10.9 ºC | 7.4 / 33.3 ºC SH 11.1 ºC | 7.4 / 33.4 ºC SH 11.9 ºC | 7.4 / 33.3 ºC SH 11.7 ºC | 7.4 / 33.1 ºC SH 11.3 ºC | 7.4 / 33.2 ºC SH 10.9 ºC | 7.8 / 28 ºC SH 10.1 ºC | 7.8 / 28 ºC SH 10.2 ºC | 7.9 / 28 ºC SH 10.3 ºC | 7.8 / 28.1 ºC SH 10.3 ºC | 7.8 / 28.1 ºC SH 10 ºC | 7.8 / 28 ºC SH 10 ºC | 5.7 / 42 ºC SH 9.8 ºC | 5.8 / 41.9 ºC SH 9.7 ºC | 5.8 / 41.9 ºC SH 9.7 ºC | 5.8 / 41.9 ºC SH 10.5 ºC | 5.8 / 42 ºC SH 10.3 ºC | 5.8 / 41.9 ºC SH 9.9 ºC | 1.7 / 51.8 ºC SH 10.9 ºC | 1.7 / 51.7 ºC SH 9.8 ºC | 1.6 / 51.8 ºC SH 8.4 ºC | 4 / 50.7 ºC SH 9.2 ºC | 4 / 50.7 ºC SH 9 ºC | 3.9 / 50.6 ºC SH 9.1 ºC | 4 / 50.2 ºC SH 9.2 ºC | 4 / 50 ºC SH 8.9 ºC | 3.9 / 50 ºC SH 9 ºC | 4.1 / 50.8 ºC SH 10.8 ºC | 4 / 50.7 ºC SH 12.1 ºC | 4 / 50.5 ºC SH 11.3 ºC | 7.4 / 33.2 ºC SH 11.4 ºC | 7.4 / 33.4 ºC SH 11.2 ºC | 7.4 / 33.2 ºC SH 11 ºC | 4 / 50.1 ºC SH 11.3 ºC | 4 / 50.1 ºC SH 11.3 ºC | 3.9 / 50.1 ºC SH 11.5 ºC | 4 / 50.7 ºC SH 11.6 ºC | 4 / 50.8 ºC SH 11.5 ºC | 4 / 50.9 ºC SH 10.7 ºC
4 | Test Purpose |  | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD - target duty 524 kW | 310-240FS, 2.6VR MOD - target duty 524 kW | 310-240FS, 2.6VR MOD - target duty 524 kW | 310-240FS, 2.6VR MOD - target duty 524 kW | 310-240FS, 2.6VR MOD - target duty 524 kW | 310-240FS, 2.6VR MOD - target duty 332 kW | 310-240FS, 2.6VR MOD - target duty 332 kW | 310-240FS, 2.6VR MOD - target duty 332 kW | 310-240FS, 2.6VR MOD - target duty 332 kW | 310-240FS, 2.6VR MOD - target duty 148 kW | 310-240FS, 2.6VR MOD - target duty 148 kW | 310-240FS, 2.6VR MOD - target duty 148 kW | 310-240FS, 2.6VR MOD - target duty 148 kW | 310-240FS, 2.6VR MOD - target duty 148 kW | 310-240FS, 2.6VR MOD - target duty 569kW | 310-240FS, 2.6VR MOD - target duty 569kW | 310-240FS, 2.6VR MOD - target duty 569kW | 310-240FS, 2.6VR MOD - target duty 361kW | 310-240FS, 2.6VR MOD - target duty 361kW | 310-240FS, 2.6VR MOD - target duty 361kW | 310-240FS, 2.6VR MOD - target duty 361kW | 310-240FS, 2.6VR MOD - target duty 361kW | 310-240FS, 2.6VR MOD - target duty 361kW | 310-240FS, 2.6VR MOD - target duty 361kW | 310-240FS, 2.6VR MOD - target duty 361kW | 310-240FS, 2.6VR MOD - target duty 361kW | 310-240FS, 2.6VR MOD - target duty 361kW | 310-240FS, 2.6VR MOD - target duty 161kW | 310-240FS, 2.6VR MOD - target duty 161kW | 310-240FS, 2.6VR MOD - target duty 161kW | 310-240FS, 2.6VR MOD - target duty 161kW | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE - Target duty 347.6 | 310240FS - DAE - Target duty 347.6 | 310240FS - DAE - Target duty 347.6 | 310240FS - DAE - Target duty 347.6 | 310240FS - DAE - Target duty 347.6 | 310240FS - DAE - Target duty 347.6 | 310240FS - DAE - Target duty 155.3. | 310240FS - DAE - Target duty 155.3. | 310240FS - DAE - Target duty 155.3. | 310240FS - DAE - Target duty 166.2 | 310240FS - DAE - Target duty 166.2 | 310240FS - DAE - Target duty 166.2 | 310240FS - DAE - Target duty 547.2 | 310240FS - DAE - Target duty 547.2 | 310240FS - DAE - Target duty 547.2 | 310240FS - DAE - Target duty 585.8 | 310240FS - DAE - Target duty 585.8 | 310240FS - DAE - Target duty 585.8 | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE
5 | Econ on/off |  | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | econ (should be non econ) | econ (should be non econ) | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | econ | econ | econ | econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | econ | econ | econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | econ | econ | econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | econ | econ | econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ
6 | LI on/off |  | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI
7 | Compressor ID |  | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL
8 | Compressor Size |  | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL
9 | Notes |  | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR Test @20Hz (higher duty) | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR Test @20Hz (higher duty) | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR Test @20Hz (higher duty) | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR Test @20Hz (higher duty) | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR Test @20Hz (higher duty) | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR ? on suction temp reading - prob not fitted at suction compressor flange correctly. | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR ? on suction temp reading - prob not fitted at suction compressor flange correctly. | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR ? on suction temp reading - prob not fitted at suction compressor flange correctly. | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR ? on suction temp reading - prob not fitted at suction compressor flange correctly. | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR ? on suction temp reading - prob not fitted at suction compressor flange correctly. | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR ? on suction temp reading - prob not fitted at suction compressor flange correctly. | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR ? on suction temp reading - prob not fitted at suction compressor flange correctly. | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR ? on suction temp reading - prob not fitted at suction compressor flange correctly. | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer Withour econ plug OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer Withour econ plug OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer Withour econ plug OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer Withour econ plug OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer Withour econ plug OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer Withour econ plug OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer Withour econ plug OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer Withour econ plug OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer Withour econ plug OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer Withour econ plug OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer Withour econ plug OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer Withour econ plug OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer Withour econ plug OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer Withour econ plug OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer Withour econ plug OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice + plug Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice + plug Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice + plug Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice + plug Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice + plug Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice + plug Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice + plug Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice + plug Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice + plug Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice + plug Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice + plug Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice + plug Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice + plug Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice + plug Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice + plug Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Center Bearing orifice 3rd Bearing oil feed orifice Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Center Bearing orifice 3rd Bearing oil feed orifice Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Center Bearing orifice 3rd Bearing oil feed orifice Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Center Bearing orifice 3rd Bearing oil feed orifice Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Center Bearing orifice 3rd Bearing oil feed orifice Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Center Bearing orifice 3rd Bearing oil feed orifice Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR
10 | Refrigerant |  | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a | r134a
11 | Comp PR |  | 2.8081 | 2.8106 | 2.8112 | 3.3098 | 3.3137 | 3.3128 | 3.9518 | 3.9209 | 3.917 | 4.7022 | 4.701 | 4.7066 | 5.6403 | 5.6405 | 5.6414 | 1.887 | 1.8886 | 1.8916 | 1.892 | 1.8862 | 1.8807 | 1.8927 | 1.8919 | 1.8882 | 1.8944 | 1.8858 | 1.8847 | 2.2202 | 2.2222 | 2.2204 | 2.2193 | 2.2193 | 2.2234 | 2.2303 | 2.2324 | 2.2256 | 2.2209 | 2.2245 | 2.2247 | 2.2178 | 2.2346 | 2.2274 | 2.9857 | 2.9747 | 2.9875 | 2.972 | 2.9958 | 2.9831 | 2.9757 | 3.9545 | 3.9622 | 3.9589 | 4.4347 | 4.4193 | 4.4176 | 3.9523 | 3.9584 | 3.9527 | 3.9112 | 3.8988 | 3.912 | 2.9858 | 2.9869 | 2.9931 | 2.9706 | 2.9823 | 2.9793 | 2.2333 | 2.2343 | 2.2308 | 2.2263 | 2.2241 | 2.2252 | 2.2244 | 2.228 | 2.2215 | 1.8915 | 1.8932 | 1.8885 | 1.8847 | 1.8889 | 1.8859 | 2.224 | 2.2252 | 2.2227 | 2.2258 | 2.2238 | 2.2207 | 2.2233 | 2.2259 | 2.2235 | 2.9857 | 2.9888 | 2.989 | 2.9849 | 2.9852 | 2.987 | 2.9829 | 3.9614 | 3.9594 | 3.9661 | 3.9616 | 3.9581 | 3.9564 | 3.9502 | 3.9476 | 4.4051 | 4.4063 | 4.4123 | 3.9712 | 3.9563 | 3.9564 | 3.9107 | 3.9006 | 3.8899 | 4.405 | 4.4122 | 4.4076 | 2.98 | 2.9836 | 2.9955 | 2.9796 | 2.9802 | 2.9803 | 2.2179 | 2.2231 | 2.2217 | 1.8894 | 1.8914 | 1.8906 | 1.8977 | 1.8902 | 2.981 | 2.9781 | 2.979 | 2.2224 | 2.2207 | 2.2233 | 2.2247 | 2.2248 | 2.2204 | 2.2201 | 2.3405 | 2.3463 | 2.3404 | 1.9151 | 1.9033 | 1.8978 | 1.8924 | 3.9666 | 3.9728 | 3.9688 | 3.9737 | 3.9768 | 3.9547 | 3.9441 | 3.9104 | 3.9119 | 3.8939 | 3.9491 | 3.9471 | 3.9514 | 3.9526 | 3.9088 | 3.9152 | 3.9136 | 3.8873 | 4.4074 | 4.4003 | 4.414 | 3.958 | 3.9523 | 3.9526 | 3.9083 | 3.9026 | 3.9017 | 3.9667 | 3.9576 | 3.9603 | 2.2319 | 2.2315 | 2.2254 | 4.4201 | 4.4196 | 4.4103 | 3.9051 | 3.9061 | 3.9083 | 3.9655 | 3.9565 | 3.9543 | 3.9546 | 3.9532 | 3.9548 | 2.2367 | 2.2346 | 2.226 | 2.2327 | 2.2237 | 2.2329 | 2.2206 | 2.2171 | 2.2216 | 1.8879 | 1.8879 | 1.8799 | 1.8948 | 1.8924 | 1.8911 | 2.9917 | 2.9738 | 2.976 | 2.9733 | 2.9767 | 2.9685 | 4.4226 | 4.4207 | 4.4346 | 3.9684 | 3.9736 | 3.9716 | 3.9187 | 3.901 | 3.9152 | 3.9701 | 3.9665 | 3.9521 | 2.2232 | 2.2377 | 2.2212 | 3.9104 | 3.9173 | 3.9207 | 3.9731 | 3.9791 | 3.9886
12 | Comp PD |  | 8.8429 | 8.8538 | 8.827 | 9.585 | 9.6012 | 9.5922 | 10.2824 | 10.2292 | 10.2054 | 10.8304 | 10.8369 | 10.8415 | 11.3042 | 11.2873 | 11.2757 | 3.417 | 3.4204 | 3.428 | 3.4381 | 3.4197 | 3.3944 | 3.4294 | 3.4275 | 3.4217 | 3.4416 | 3.4126 | 3.4069 | 4.6295 | 4.6355 | 4.6363 | 4.6424 | 4.6419 | 4.6541 | 4.6583 | 4.6814 | 4.6584 | 4.6315 | 4.6555 | 4.6584 | 4.6378 | 4.685 | 4.6696 | 7.1438 | 7.1043 | 7.1376 | 7.0978 | 7.1753 | 7.1517 | 7.117 | 9.9777 | 9.9877 | 10.0045 | 10.6761 | 10.6309 | 10.6337 | 9.9811 | 9.9884 | 9.974 | 9.8048 | 9.7764 | 9.8339 | 7.1426 | 7.1277 | 7.1521 | 7.0976 | 7.1247 | 7.1038 | 4.6729 | 4.6898 | 4.6696 | 4.643 | 4.6604 | 4.6644 | 4.6663 | 4.6658 | 4.6401 | 3.4389 | 3.4429 | 3.413 | 3.4068 | 3.4282 | 3.4101 | 4.65 | 4.6654 | 4.6499 | 4.6454 | 4.64 | 4.6399 | 4.6482 | 4.6539 | 4.6569 | 7.1518 | 7.1469 | 7.1342 | 7.1252 | 7.1355 | 7.1274 | 7.1266 | 10.0062 | 10.0071 | 10.0166 | 10.0075 | 10.0038 | 10.0029 | 9.9916 | 9.9888 | 10.6247 | 10.6061 | 10.6064 | 10.039 | 9.9977 | 9.991 | 9.8381 | 9.7982 | 9.7707 | 10.6043 | 10.6306 | 10.6071 | 7.1227 | 7.1257 | 7.1604 | 7.1212 | 7.1159 | 7.1106 | 4.6314 | 4.6529 | 4.6467 | 3.4158 | 3.4246 | 3.4357 | 3.4663 | 3.4242 | 7.1153 | 7.1052 | 7.1191 | 4.6406 | 4.6401 | 4.6475 | 4.6635 | 4.6534 | 4.641 | 4.6386 | 4.826 | 4.8345 | 4.8304 | 3.5019 | 3.4841 | 3.4602 | 3.4404 | 9.9597 | 10.0097 | 10.0188 | 10.0064 | 10.0234 | 9.9958 | 9.9765 | 9.8174 | 9.8236 | 9.8151 | 9.9817 | 9.9969 | 9.9719 | 9.9742 | 9.8485 | 9.882 | 9.8562 | 9.7799 | 10.6135 | 10.6049 | 10.6251 | 10.0097 | 9.9586 | 9.9743 | 9.8113 | 9.7791 | 9.7913 | 10.0376 | 9.9698 | 9.9987 | 4.6848 | 4.685 | 4.6419 | 10.6526 | 10.6554 | 10.6371 | 9.8395 | 9.8161 | 9.8103 | 9.9936 | 9.9923 | 9.993 | 9.9799 | 9.961 | 9.9549 | 4.6872 | 4.6934 | 4.646 | 4.6861 | 4.6506 | 4.6807 | 4.6435 | 4.6232 | 4.6393 | 3.4204 | 3.4206 | 3.402 | 3.4432 | 3.4334 | 3.4253 | 7.1431 | 7.0936 | 7.0933 | 7.1046 | 7.1146 | 7.0838 | 10.6654 | 10.6339 | 10.6672 | 10.0387 | 10.0435 | 10.0101 | 9.855 | 9.7899 | 9.8247 | 10.0653 | 10.0199 | 9.981 | 4.6385 | 4.6942 | 4.6399 | 9.8312 | 9.84 | 9.835 | 10.031 | 10.0718 | 10.0894
13 | LVDT |  | -37.4322 | -37.4332 | -37.4324 | -37.4323 | -37.434 | -37.4331 | -37.433 | -37.4325 | -37.4334 | -37.4329 | -37.4335 | -37.4329 | -37.4328 | -37.4335 | -37.4329 | -37.4342 | -37.4333 | -37.4335 | -37.4337 | -37.4321 | -37.4325 | -37.4323 | -37.4339 | -37.4329 | -37.4327 | -37.4335 | -37.4328 | -37.4338 | -37.4332 | -37.4338 | -37.4335 | -37.4323 | -37.4332 | -37.4334 | -37.4324 | -37.4324 | -37.4328 | -37.4321 | -37.4331 | -37.4338 | -37.433 | -37.4329 | -37.433 | -37.434 | -37.4331 | -37.4316 | -37.4313 | -37.4331 | -37.4333 | -37.4328 | -37.4325 | -37.4335 | -37.4327 | -37.4324 | -37.4326 | -37.4322 | -37.4332 | -37.4317 | -37.4329 | -37.4323 | -37.4321 | -37.4319 | -37.4329 | -37.4326 | -37.432 | -37.4327 | -37.4326 | -37.4326 | -37.4331 | -37.4344 | -37.4323 | -37.4321 | -37.4333 | -37.4331 | -37.4328 | -37.4329 | -37.4325 | -37.4323 | -37.4326 | -37.4335 | -37.4338 | -37.4323 | -37.4334 | -37.4323 | -37.4335 | -37.4319 | -37.4339 | -37.4335 | -37.4317 | -37.4326 | -37.434 | -37.4321 | -37.4342 | -37.4334 | -37.4328 | -37.4333 | -37.4332 | -37.4332 | -37.4327 | -37.4334 | -37.4327 | -37.432 | -37.4335 | -37.4337 | -37.4326 | -37.4337 | -37.4323 | -37.432 | -37.4329 | -37.4331 | -37.4327 | -37.4326 | -37.4329 | -37.4324 | -37.4323 | -37.4335 | -37.433 | -37.4332 | -37.4326 | -37.4329 | -37.4327 | -37.4329 | -37.4324 | -37.4329 | -37.4328 | -37.4327 | -37.4319 | -37.4333 | -37.4329 | -37.4322 | -37.4319 | -37.4326 | -37.4328 | -37.433 | -37.4329 | -37.4324 | -37.4338 | -37.4325 | -37.4332 | -37.4326 | -37.4327 | -37.4328 | -37.4335 | -37.4328 | -37.4336 | -37.433 | -37.4331 | -37.4342 | -37.4333 | -37.4336 | -37.433 | -37.4328 | -37.4331 | -37.4325 | -37.4327 | -37.4323 | -37.4323 | -37.4329 | -37.4329 | -37.4324 | -37.4327 | -37.4318 | -37.4322 | -37.4332 | -37.4334 | -37.4334 | -37.4329 | -37.4326 | -37.4325 | -37.4321 | -37.4328 | -37.4331 | -37.4325 | -37.4327 | -37.4328 | -37.4323 | -37.4333 | -37.433 | -37.4327 | -37.433 | -37.4326 | -37.4323 | -37.4328 | -37.4328 | -37.4326 | -37.4324 | -37.4329 | -37.4321 | -37.4327 | -37.4334 | -37.4337 | -37.4329 | -37.4319 | -37.4328 | -37.4328 | -37.4324 | -37.4315 | -37.4328 | -37.4324 | -37.4327 | -37.4333 | -37.4332 | -37.4328 | -37.4329 | -37.4333 | -37.4338 | -37.433 | -37.4331 | -37.4328 | -37.4332 | -37.4321 | -37.4327 | -37.432 | -37.4325 | -37.4328 | -37.4323 | -37.4329 | -37.4326 | -37.4333 | -37.4323 | -37.4325 | -37.4332 | -37.4334 | -37.4327 | -37.433 | -37.4314 | -37.4332 | -37.434 | -37.4328 | -37.4335 | -37.4327 | -37.4323 | -37.4331 | -37.4333 | -37.4325 | -37.4323
14 | Comp Running |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
15 | Comp data
16 | Tester |  | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | AS | AS | MJ | AS | AS | AS | AS | AS | AS | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | AS | AS | AS | AS | AS | AS | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | AS | AS | AS | AS | AS | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | AS + MJ | AS + MJ | AS + MJ | AS | AS | AS | AS | AS + MJ | AS + MJ | AS + MJ | AS + MJ | AS + MJ | AS + MJ | AS | AS | AS | AS | AS | AS | AS | AS | AS | AS | AS | AS | AS | AS | AS | AS | AS | AS | AS | AS | AS | AS | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ
17 | Comp match?
18 | Motor Size |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | VR |  | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 1.6 | 1.6 | 1.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 2.6 | 2.6 | 2.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 1 2 2.6 | 1 2 2.6 | 1 2 2.6 | 1 2 2.6 | 1 2 2.6 | 1 2 2.6 | 1 2 2.6 | 1 2 2.6 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 1.6 | 1.6 | 1.6 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 1.6 | 1.6 | 1.6 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8
20 | Motor ID |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | Comp Type |  | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL
22 | Comp swept vol | m3/hr | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82 | 546.82
23 | Corrected comp swept vol for Hz | m3/hr | 1312.4774 | 1312.368 | 1312.5867 | 1312.4774 | 1312.368 | 1312.4774 | 1312.368 | 1312.368 | 1312.368 | 1312.2586 | 1312.368 | 1312.4774 | 1312.368 | 1312.8055 | 1312.368 | 207.8572 | 207.7807 | 207.8463 | 218.7717 | 218.7171 | 218.8374 | 207.8025 | 207.7479 | 207.8244 | 218.7827 | 218.7389 | 218.728 | 437.4232 | 437.4779 | 437.4997 | 437.5435 | 437.4669 | 437.4997 | 470.3199 | 470.3418 | 470.2761 | 470.2761 | 470.2761 | 470.2871 | 492.1161 | 492.1599 | 492.138 | 754.5132 | 754.721 | 754.6335 | 765.5152 | 820.2081 | 820.2519 | 820.3066 | 1203.004 | 1203.004 | 1202.8946 | 1312.2586 | 1312.4774 | 1312.2586 | 1312.368 | 1312.368 | 1312.368 | 1312.368 | 1312.2586 | 1312.368 | 765.4714 | 765.4824 | 765.6027 | 820.1972 | 820.1863 | 820.2737 | 492.1708 | 492.1927 | 492.0833 | 437.5216 | 437.4232 | 437.4779 | 437.4669 | 437.5216 | 437.4451 | 207.7588 | 207.7588 | 207.8463 | 218.6405 | 218.6514 | 218.8264 | 437.4997 | 437.4341 | 437.4451 | 470.1886 | 470.298 | 470.3089 | 470.3418 | 470.2324 | 470.2433 | 776.4625 | 776.4078 | 776.4625 | 820.2191 | 820.2191 | 820.2081 | 809.2936 | 1203.004 | 1203.004 | 1203.004 | 1203.004 | 1202.8946 | 1203.004 | 1203.004 | 1203.1134 | 1312.368 | 1312.368 | 1312.4774 | 1312.4774 | 1312.368 | 1312.5867 | 1312.368 | 1312.368 | 1312.2586 | 1312.4774 | 1312.368 | 1312.368 | 754.6335 | 754.4366 | 754.5132 | 765.5371 | 765.4277 | 765.548 | 437.4997 | 437.4779 | 437.4669 | 207.7588 | 207.7916 | 207.7369 | 218.8374 | 218.728 | 820.23 | 820.2519 | 820.1206 | 470.3089 | 470.2761 | 470.298 | 470.1777 | 492.1599 | 492.1271 | 492.1927 | 492.138 | 492.0286 | 492.0833 | 218.8155 | 218.7936 | 218.6952 | 218.6843 | 1203.004 | 1203.004 | 1203.2227 | 1203.2227 | 1312.368 | 1312.368 | 1312.368 | 1312.2586 | 1312.368 | 1312.368 | 1312.2586 | 1312.4774 | 1312.1493 | 1312.2586 | 1312.2586 | 1312.368 | 1312.368 | 1312.368 | 1312.368 | 1312.2586 | 1312.4774 | 1312.4774 | 1312.368 | 1312.368 | 1312.4774 | 1312.2586 | 1312.2586 | 1202.7853 | 1203.004 | 1203.004 | 492.1927 | 492.1489 | 492.0724 | 1312.2586 | 1312.4774 | 1312.4774 | 1312.4774 | 1312.368 | 1312.368 | 1312.368 | 1312.368 | 1312.368 | 1203.1134 | 1203.004 | 1203.004 | 492.1161 | 492.2036 | 492.1599 | 470.2761 | 470.2652 | 470.2761 | 437.456 | 437.4888 | 437.3794 | 207.7479 | 207.7807 | 207.8353 | 218.6843 | 218.7061 | 218.8374 | 776.4844 | 776.4735 | 776.4844 | 831.243 | 831.1227 | 831.2101 | 1312.2586 | 1312.4774 | 1312.368 | 1312.4774 | 1312.368 | 1312.4774 | 1312.368 | 1312.368 | 1312.2586 | 1203.1134 | 1203.1134 | 1203.004 | 492.1271 | 492.1599 | 492.1161 | 1312.2586 | 1312.368 | 1312.1493 | 1312.2586 | 1312.368 | 1312.2586
24
25
26 | Atmopsheric Pressure (manual input) | bar | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135 | 1.0135
27 | Suction Temp | ºC | 25.0492 | 24.9605 | 24.7684 | 21.3108 | 20.8375 | 19.4422 | 16.3206 | 15.6208 | 15.0402 | 10.098 | 10.5134 | 9.7332 | 7.3524 | 7.2084 | 7.0618 | 18.4808 | 18.5859 | 18.8415 | 18.684 | 18.6889 | 18.6476 | 18.323 | 18.6046 | 18.8127 | 18.7143 | 18.7131 | 18.7292 | 16.6336 | 16.8627 | 16.9105 | 16.7911 | 16.6719 | 16.4341 | 17.5757 | 17.3977 | 17.2151 | 15.7404 | 15.4801 | 15.5112 | 15.6782 | 15.91 | 16.4212 | 15.0114 | 15.0351 | 14.7431 | 14.5322 | 14.934 | 14.876 | 14.748 | 13.313 | 13.2327 | 12.9854 | 11.7386 | 10.9293 | 12.2237 | 13.463 | 13.4539 | 13.5436 | 13.5748 | 14.9419 | 15.7748 | 15.2453 | 15.4783 | 15.4345 | 17.5607 | 17.521 | 17.4276 | 20.2842 | 20.2017 | 20.063 | 19.0741 | 18.9792 | 18.8013 | 18.5706 | 18.4883 | 18.493 | 17.1189 | 17.0125 | 16.7228 | 18.9759 | 18.5056 | 18.4042 | 17.3922 | 16.9391 | 16.7895 | 16.1943 | 16.1802 | 16.1937 | 16.3087 | 16.2008 | 16.1704 | 17.1666 | 17.0217 | 16.8172 | 16.5701 | 16.3831 | 16.1233 | 16.9093 | 14.3163 | 14.3056 | 14.2855 | 14.3732 | 14.3977 | 14.4554 | 14.6297 | 14.9905 | 12.1148 | 12.491 | 11.6225 | 14.4707 | 14.4767 | 14.447 | 15.2061 | 14.9845 | 14.7759 | 11.0711 | 11.1825 | 11.2949 | 16.9689 | 16.7949 | 16.82 | 17.2337 | 17.2418 | 17.2429 | 18.3113 | 18.719 | 19.14 | 18.3754 | 18.4238 | 18.4575 | 17.928 | 17.8053 | 15.2657 | 15.1213 | 14.6392 | 16.9474 | 16.8708 | 16.7454 | 16.3672 | 16.8494 | 16.8831 | 16.9756 | 16.818 | 16.8359 | 16.894 | 17.6224 | 18.5485 | 18.5994 | 18.336 | 13.6671 | 14.0142 | 14.3711 | 14.4289 | 13.5508 | 14.6941 | 15.0175 | 18.91 | 19.3815 | 18.9184 | 21.6936 | 21.6804 | 21.6293 | 21.5924 | 21.5042 | 21.445 | 21.4117 | 21.3538 | 12.1552 | 12.4514 | 12.4251 | 13.616 | 13.7924 | 14.5835 | 15.4833 | 15.6995 | 15.957 | 13.1966 | 13.8774 | 13.2902 | 17.6319 | 17.477 | 17.6169 | 11.4366 | 11.2606 | 11.0319 | 13.6057 | 13.3032 | 12.8859 | 14.7596 | 14.4407 | 14.5919 | 13.3308 | 13.5145 | 13.5078 | 16.7238 | 16.7508 | 16.4436 | 18.3129 | 18.5421 | 19.3375 | 19.1512 | 18.6899 | 18.3133 | 17.8738 | 18.0498 | 18.1805 | 18.1335 | 17.8199 | 17.7217 | 15.4962 | 15.4738 | 15.4137 | 16.3355 | 16.1358 | 15.6846 | 12.61 | 11.434 | 10.0759 | 13.2532 | 13.0466 | 13.0493 | 13.1758 | 12.8939 | 12.9535 | 14.8885 | 16.1038 | 15.307 | 18.7739 | 18.5876 | 18.4132 | 15.277 | 15.2205 | 15.4129 | 15.5764 | 15.5655 | 14.7076
28 | Suction Pressure | BarA | 4.8908 | 4.8901 | 4.8736 | 4.1496 | 4.1497 | 4.1475 | 3.4835 | 3.5021 | 3.4986 | 2.9254 | 2.9281 | 2.9249 | 2.4361 | 2.4323 | 2.4294 | 3.8522 | 3.849 | 3.8449 | 3.8544 | 3.8588 | 3.8543 | 3.8415 | 3.8428 | 3.8523 | 3.8478 | 3.8524 | 3.8511 | 3.794 | 3.7928 | 3.7991 | 3.8074 | 3.807 | 3.8043 | 3.7863 | 3.7985 | 3.8009 | 3.7934 | 3.802 | 3.8037 | 3.8084 | 3.7946 | 3.8045 | 3.5977 | 3.5977 | 3.5913 | 3.5993 | 3.5952 | 3.6062 | 3.6023 | 3.3771 | 3.3717 | 3.3812 | 3.1083 | 3.1091 | 3.1114 | 3.3808 | 3.3763 | 3.378 | 3.3679 | 3.3725 | 3.377 | 3.5968 | 3.5873 | 3.5884 | 3.6017 | 3.5943 | 3.5891 | 3.7889 | 3.7995 | 3.794 | 3.7862 | 3.8072 | 3.807 | 3.811 | 3.7996 | 3.7987 | 3.8575 | 3.8547 | 3.8411 | 3.8506 | 3.8567 | 3.8494 | 3.799 | 3.8079 | 3.8029 | 3.7896 | 3.7916 | 3.8008 | 3.7998 | 3.7963 | 3.8064 | 3.6017 | 3.5936 | 3.5869 | 3.5897 | 3.5944 | 3.587 | 3.594 | 3.3789 | 3.3815 | 3.3771 | 3.3791 | 3.3818 | 3.3835 | 3.3868 | 3.3888 | 3.1203 | 3.1137 | 3.1083 | 3.3788 | 3.3818 | 3.3794 | 3.38 | 3.378 | 3.3809 | 3.1144 | 3.1155 | 3.1128 | 3.5974 | 3.5923 | 3.5883 | 3.5973 | 3.5935 | 3.5906 | 3.8027 | 3.8042 | 3.8035 | 3.8404 | 3.8418 | 3.8577 | 3.8611 | 3.8468 | 3.5918 | 3.5918 | 3.5974 | 3.7965 | 3.8012 | 3.7992 | 3.8079 | 3.7993 | 3.8028 | 3.8017 | 3.6002 | 3.591 | 3.6037 | 3.8266 | 3.857 | 3.8543 | 3.8554 | 3.3572 | 3.3671 | 3.3747 | 3.365 | 3.3672 | 3.383 | 3.3887 | 3.3732 | 3.3736 | 3.3916 | 3.3847 | 3.3921 | 3.3787 | 3.3781 | 3.3858 | 3.3898 | 3.3829 | 3.3872 | 3.1149 | 3.1188 | 3.1122 | 3.384 | 3.3732 | 3.3782 | 3.3736 | 3.369 | 3.3743 | 3.3834 | 3.3709 | 3.3776 | 3.803 | 3.8043 | 3.788 | 3.1147 | 3.116 | 3.1191 | 3.3869 | 3.3778 | 3.3733 | 3.37 | 3.3797 | 3.3825 | 3.3777 | 3.373 | 3.3691 | 3.79 | 3.8016 | 3.7897 | 3.8016 | 3.8004 | 3.7965 | 3.8041 | 3.7984 | 3.7979 | 3.852 | 3.8523 | 3.8661 | 3.8482 | 3.8472 | 3.844 | 3.5865 | 3.5939 | 3.5897 | 3.6003 | 3.5993 | 3.5985 | 3.1162 | 3.1087 | 3.1058 | 3.3819 | 3.3775 | 3.3687 | 3.3765 | 3.3746 | 3.3702 | 3.3889 | 3.3777 | 3.381 | 3.792 | 3.7928 | 3.7994 | 3.378 | 3.3731 | 3.3674 | 3.374 | 3.3809 | 3.3759
29 | Suction SH | ºC | 10.0042 | 9.9201 | 9.8332 | 11.2851 | 10.8111 | 9.432 | 11.4288 | 10.5758 | 10.0236 | 10.1228 | 10.5129 | 9.7624 | 12.3236 | 12.2201 | 12.1061 | 10.6629 | 10.7922 | 11.0799 | 10.8494 | 10.8205 | 10.8135 | 10.5871 | 10.859 | 10.9945 | 10.9299 | 10.8939 | 10.9201 | 9.2627 | 9.5011 | 9.5001 | 9.3169 | 9.201 | 8.9837 | 10.265 | 9.9926 | 9.7912 | 8.3744 | 8.048 | 8.0656 | 8.1963 | 8.5344 | 8.9697 | 9.1889 | 9.2126 | 8.9719 | 8.6967 | 9.1314 | 8.9846 | 8.8883 | 9.3092 | 9.2742 | 8.9467 | 10.0784 | 9.2618 | 10.5352 | 9.4275 | 9.4569 | 9.5321 | 9.6483 | 10.9766 | 11.7718 | 9.4295 | 9.7396 | 9.6865 | 11.7056 | 11.726 | 11.674 | 12.9533 | 12.7888 | 12.6923 | 11.7635 | 11.5063 | 11.3301 | 11.0687 | 11.0747 | 11.0859 | 9.2609 | 9.1758 | 8.9897 | 11.1705 | 10.6531 | 10.6074 | 9.9831 | 9.4613 | 9.3503 | 8.8574 | 8.8284 | 8.7703 | 8.893 | 8.8127 | 8.7044 | 11.3115 | 11.2317 | 11.0813 | 10.8116 | 10.5869 | 10.387 | 11.1162 | 10.2972 | 10.2646 | 10.2818 | 10.352 | 10.3537 | 10.3973 | 10.5441 | 10.8877 | 10.3469 | 10.7823 | 9.9621 | 10.4527 | 10.4328 | 10.4233 | 11.178 | 10.9729 | 10.7394 | 9.3561 | 9.4578 | 9.5938 | 11.149 | 11.0158 | 11.073 | 11.4144 | 11.4532 | 11.477 | 10.8738 | 11.2698 | 11.6959 | 10.6476 | 10.6856 | 10.5975 | 10.0422 | 10.029 | 9.4905 | 9.3458 | 8.8189 | 9.5578 | 9.4444 | 9.3344 | 8.8894 | 9.4378 | 9.4443 | 9.5455 | 10.9755 | 11.067 | 11.0231 | 10.001 | 10.694 | 10.7658 | 10.494 | 9.8315 | 10.0948 | 10.3873 | 10.5276 | 9.6302 | 10.6404 | 10.9159 | 14.939 | 15.4072 | 14.7917 | 17.6256 | 17.5501 | 17.6117 | 17.58 | 17.4269 | 17.3341 | 17.3591 | 17.2641 | 10.4357 | 10.6962 | 10.7296 | 9.5537 | 9.8212 | 10.5705 | 11.509 | 11.7638 | 11.9763 | 9.1395 | 9.9261 | 9.2822 | 10.1917 | 10.0266 | 10.2927 | 9.7184 | 9.5313 | 9.2746 | 9.5186 | 9.2937 | 8.9144 | 10.8157 | 10.4146 | 10.5421 | 9.3214 | 9.5454 | 9.5714 | 9.3838 | 9.3217 | 9.1065 | 10.8836 | 11.1218 | 11.9472 | 11.7024 | 11.2851 | 10.9128 | 10.0575 | 10.2315 | 10.2563 | 10.3459 | 10.0403 | 9.9667 | 9.7641 | 9.6814 | 9.6553 | 10.4915 | 10.3002 | 9.8552 | 10.8786 | 9.7704 | 8.4378 | 9.2086 | 9.0391 | 9.1167 | 9.1771 | 8.9107 | 9.0079 | 10.7852 | 12.0946 | 11.2698 | 11.4184 | 11.2262 | 11.0012 | 11.2656 | 11.2507 | 11.491 | 11.5988 | 11.5299 | 10.7134
30 | Suction Gauge | ºC | 15.045 | 15.0404 | 14.9352 | 10.0257 | 10.0264 | 10.0102 | 4.8919 | 5.045 | 5.0166 | -0.024873 | 0.0005201 | -0.029269 | -4.9711 | -5.0117 | -5.0443 | 7.8179 | 7.7937 | 7.7616 | 7.8346 | 7.8684 | 7.8341 | 7.7359 | 7.7456 | 7.8182 | 7.7844 | 7.8192 | 7.8091 | 7.3709 | 7.3616 | 7.4104 | 7.4741 | 7.471 | 7.4504 | 7.3107 | 7.4051 | 7.424 | 7.366 | 7.4322 | 7.4456 | 7.4819 | 7.3756 | 7.4516 | 5.8226 | 5.8226 | 5.7712 | 5.8355 | 5.8026 | 5.8914 | 5.8597 | 4.0038 | 3.9585 | 4.0387 | 1.6602 | 1.6676 | 1.6885 | 4.0355 | 3.9971 | 4.0115 | 3.9265 | 3.9654 | 4.003 | 5.8159 | 5.7387 | 5.7481 | 5.855 | 5.795 | 5.7536 | 7.3309 | 7.4129 | 7.3707 | 7.3106 | 7.4729 | 7.4713 | 7.5019 | 7.4136 | 7.4071 | 7.8581 | 7.8367 | 7.733 | 7.8054 | 7.8525 | 7.7967 | 7.4091 | 7.4779 | 7.4393 | 7.337 | 7.3518 | 7.4234 | 7.4157 | 7.3881 | 7.4661 | 5.8551 | 5.79 | 5.7359 | 5.7585 | 5.7962 | 5.7363 | 5.7931 | 4.0191 | 4.041 | 4.0037 | 4.0212 | 4.044 | 4.0581 | 4.0857 | 4.1028 | 1.7679 | 1.7087 | 1.6604 | 4.018 | 4.0439 | 4.0237 | 4.0281 | 4.0116 | 4.0364 | 1.7149 | 1.7248 | 1.7011 | 5.8199 | 5.7791 | 5.747 | 5.8193 | 5.7885 | 5.7659 | 7.4376 | 7.4492 | 7.4441 | 7.7278 | 7.7381 | 7.86 | 7.8858 | 7.7763 | 5.7751 | 5.7756 | 5.8203 | 7.3896 | 7.4265 | 7.411 | 7.4778 | 7.4116 | 7.4388 | 7.4301 | 5.8425 | 5.7689 | 5.8709 | 7.6214 | 7.8545 | 7.8336 | 7.8419 | 3.8356 | 3.9195 | 3.9838 | 3.9014 | 3.9206 | 4.0538 | 4.1016 | 3.971 | 3.9743 | 4.1267 | 4.068 | 4.1303 | 4.0176 | 4.0123 | 4.0773 | 4.1109 | 4.0527 | 4.0896 | 1.7195 | 1.7552 | 1.6955 | 4.0623 | 3.9712 | 4.013 | 3.9743 | 3.9357 | 3.9807 | 4.0571 | 3.9514 | 4.0081 | 7.4402 | 7.4504 | 7.3242 | 1.7182 | 1.7293 | 1.7573 | 4.0871 | 4.0095 | 3.9715 | 3.9439 | 4.0261 | 4.0498 | 4.0094 | 3.9691 | 3.9364 | 7.34 | 7.4291 | 7.3371 | 7.4293 | 7.4202 | 7.3903 | 7.4488 | 7.4048 | 7.4005 | 7.8163 | 7.8183 | 7.9242 | 7.7876 | 7.7795 | 7.755 | 5.7321 | 5.7925 | 5.7584 | 5.844 | 5.8357 | 5.8295 | 1.7314 | 1.6637 | 1.6382 | 4.0446 | 4.0075 | 3.9326 | 3.9987 | 3.9832 | 3.9456 | 4.1033 | 4.0092 | 4.0372 | 7.3554 | 7.3613 | 7.412 | 4.0114 | 3.9698 | 3.9219 | 3.9776 | 4.0357 | 3.9942
31 | Discharge Temp | ºC | 76.6687 | 76.5849 | 76.4228 | 78.8962 | 78.4349 | 77.2688 | 80.8742 | 80.232 | 79.7171 | 83.792 | 83.7771 | 83.3901 | 90.8678 | 90.7344 | 90.6054 | 47.9543 | 47.9974 | 48.0748 | 47.4335 | 47.1388 | 47.0256 | 47.2552 | 47.3039 | 46.71 | 47.0215 | 46.9679 | 46.7681 | 52.8733 | 53.0544 | 53.2342 | 53.9749 | 53.9215 | 53.8645 | 54.6573 | 54.2959 | 54.3258 | 51.741 | 51.8007 | 51.8306 | 52.1554 | 52.5743 | 52.653 | 63.6603 | 63.581 | 63.4182 | 63.2056 | 64.0455 | 63.8848 | 63.6064 | 77.5141 | 77.4408 | 77.2263 | 82.4291 | 81.9144 | 82.8346 | 78.711 | 78.7044 | 78.7812 | 78.5828 | 79.6879 | 79.9545 | 64.9206 | 65.4558 | 65.7251 | 67.6261 | 67.6046 | 67.6164 | 56.3924 | 56.3225 | 56.2193 | 56.017 | 55.9235 | 55.7537 | 55.4961 | 55.3446 | 55.1113 | 45.7004 | 45.4766 | 45.3926 | 46.4671 | 46.0189 | 45.609 | 53.5322 | 53.2481 | 53.3954 | 52.6919 | 52.6848 | 52.5961 | 53.6881 | 53.541 | 53.3669 | 66.9299 | 66.7963 | 66.7029 | 66.5891 | 66.413 | 66.1839 | 67.2566 | 79.4 | 79.3899 | 79.3811 | 79.4592 | 79.4766 | 79.5019 | 79.6386 | 79.8189 | 83.6596 | 83.69 | 83.1033 | 80.6129 | 80.5601 | 80.7132 | 80.4026 | 80.0417 | 79.8318 | 82.6253 | 82.7389 | 82.8015 | 66.8161 | 66.7456 | 66.7452 | 67.1784 | 67.198 | 67.1985 | 55.9889 | 56.3751 | 56.574 | 46.7646 | 46.6674 | 46.5323 | 45.7305 | 45.2656 | 65.4899 | 65.4777 | 65.9108 | 53.5212 | 53.4746 | 53.3858 | 53.0156 | 53.6689 | 53.7036 | 53.7298 | 56.208 | 56.2506 | 56.3103 | 47.6678 | 48.0269 | 47.9808 | 47.9414 | 79.0585 | 79.3621 | 79.6115 | 79.6811 | 80.2055 | 80.973 | 81.2442 | 84.6134 | 84.8795 | 84.1783 | 81.3351 | 81.2728 | 80.9674 | 80.7776 | 80.4931 | 80.4914 | 80.2766 | 79.5949 | 81.6492 | 81.8133 | 81.7659 | 78.36 | 78.5664 | 79.1082 | 79.3911 | 79.5723 | 79.7772 | 77.2175 | 77.1545 | 76.8154 | 54.0542 | 53.963 | 53.9896 | 81.1123 | 80.8792 | 80.8373 | 77.4235 | 77.1664 | 76.8264 | 79.0837 | 78.7779 | 79.2053 | 76.5866 | 76.7418 | 76.5902 | 52.7574 | 52.5277 | 52.4436 | 54.6356 | 55.0605 | 55.1597 | 54.7452 | 54.0465 | 53.7595 | 46.5342 | 46.5135 | 46.384 | 46.505 | 45.5963 | 45.1859 | 64.4279 | 64.2532 | 64.3681 | 65.2223 | 64.9016 | 64.4856 | 82.3417 | 81.291 | 80.4547 | 78.0616 | 77.9128 | 77.841 | 77.0956 | 77.092 | 77.3296 | 78.4717 | 79.1191 | 78.5143 | 54.4239 | 54.1733 | 53.8665 | 79.6024 | 79.6789 | 79.8482 | 80.4132 | 80.318 | 79.6525
32 | Discharge Pressure | BarA | 13.7337 | 13.7439 | 13.7006 | 13.7346 | 13.7509 | 13.7397 | 13.7659 | 13.7313 | 13.704 | 13.7558 | 13.765 | 13.7664 | 13.7403 | 13.7196 | 13.7051 | 7.2692 | 7.2694 | 7.2729 | 7.2925 | 7.2785 | 7.2488 | 7.2709 | 7.2702 | 7.274 | 7.2894 | 7.265 | 7.258 | 8.4236 | 8.4283 | 8.4355 | 8.4498 | 8.4489 | 8.4585 | 8.4445 | 8.4798 | 8.4593 | 8.4249 | 8.4574 | 8.4622 | 8.4462 | 8.4796 | 8.4741 | 10.7415 | 10.702 | 10.7289 | 10.6971 | 10.7705 | 10.7579 | 10.7193 | 13.3548 | 13.3595 | 13.3857 | 13.7844 | 13.74 | 13.7451 | 13.362 | 13.3646 | 13.352 | 13.1727 | 13.1489 | 13.2108 | 10.7394 | 10.715 | 10.7405 | 10.6993 | 10.719 | 10.6929 | 8.4618 | 8.4893 | 8.4636 | 8.4292 | 8.4677 | 8.4714 | 8.4773 | 8.4653 | 8.4388 | 7.2964 | 7.2976 | 7.2541 | 7.2574 | 7.285 | 7.2595 | 8.4489 | 8.4733 | 8.4528 | 8.435 | 8.4315 | 8.4407 | 8.4481 | 8.4501 | 8.4633 | 10.7535 | 10.7405 | 10.7212 | 10.7149 | 10.7299 | 10.7144 | 10.7206 | 13.3851 | 13.3886 | 13.3936 | 13.3867 | 13.3856 | 13.3864 | 13.3784 | 13.3776 | 13.745 | 13.7197 | 13.7147 | 13.4178 | 13.3795 | 13.3704 | 13.2181 | 13.1762 | 13.1516 | 13.7187 | 13.746 | 13.7199 | 10.7201 | 10.7179 | 10.7487 | 10.7184 | 10.7094 | 10.7013 | 8.4341 | 8.457 | 8.4502 | 7.2563 | 7.2664 | 7.2934 | 7.3274 | 7.271 | 10.7071 | 10.697 | 10.7165 | 8.4371 | 8.4414 | 8.4467 | 8.4713 | 8.4527 | 8.4438 | 8.4403 | 8.4262 | 8.4255 | 8.434 | 7.3284 | 7.3412 | 7.3145 | 7.2958 | 13.3169 | 13.3768 | 13.3935 | 13.3714 | 13.3907 | 13.3788 | 13.3652 | 13.1906 | 13.1972 | 13.2068 | 13.3664 | 13.389 | 13.3506 | 13.3523 | 13.2343 | 13.2717 | 13.2391 | 13.1672 | 13.7284 | 13.7237 | 13.7373 | 13.3937 | 13.3318 | 13.3524 | 13.1849 | 13.1481 | 13.1656 | 13.421 | 13.3407 | 13.3763 | 8.4878 | 8.4893 | 8.4299 | 13.7673 | 13.7713 | 13.7562 | 13.2264 | 13.1938 | 13.1836 | 13.3636 | 13.372 | 13.3756 | 13.3576 | 13.334 | 13.3241 | 8.4772 | 8.4949 | 8.4357 | 8.4877 | 8.451 | 8.4772 | 8.4476 | 8.4216 | 8.4372 | 7.2724 | 7.2728 | 7.2681 | 7.2915 | 7.2806 | 7.2693 | 10.7296 | 10.6876 | 10.683 | 10.7049 | 10.7139 | 10.6824 | 13.7816 | 13.7425 | 13.773 | 13.4206 | 13.421 | 13.3788 | 13.2315 | 13.1645 | 13.1949 | 13.4541 | 13.3976 | 13.362 | 8.4305 | 8.487 | 8.4393 | 13.2092 | 13.2131 | 13.2024 | 13.405 | 13.4526 | 13.4653
33 | Discharge SH | ºC | 25.0201 | 24.9067 | 24.8711 | 27.245 | 26.7359 | 25.6027 | 29.1315 | 28.5905 | 28.1555 | 32.0789 | 32.037 | 31.6458 | 39.2 | 39.127 | 39.0407 | 19.9525 | 19.9945 | 20.0556 | 19.3217 | 19.093 | 19.1202 | 19.2454 | 19.2973 | 18.6858 | 18.9244 | 18.986 | 18.8193 | 19.7219 | 19.8828 | 20.0324 | 20.7128 | 20.663 | 20.5659 | 21.4174 | 20.9074 | 21.0236 | 18.584 | 18.5064 | 18.5164 | 18.9084 | 19.1865 | 19.2887 | 21.5928 | 21.6524 | 21.395 | 21.2945 | 21.8759 | 21.7593 | 21.6169 | 26.9862 | 26.899 | 26.6061 | 30.6324 | 30.2473 | 31.1527 | 28.1617 | 28.1471 | 28.2616 | 28.6018 | 29.779 | 29.8586 | 22.8601 | 23.4816 | 23.6609 | 25.7072 | 25.6162 | 25.72 | 23.0797 | 22.8942 | 22.8991 | 22.8417 | 22.5862 | 22.4006 | 22.1182 | 22.0169 | 21.8955 | 17.5703 | 17.3411 | 17.4621 | 18.5212 | 17.9426 | 17.6529 | 20.2737 | 19.887 | 20.1205 | 19.492 | 19.4996 | 19.3723 | 20.4333 | 20.2775 | 20.0479 | 24.8198 | 24.7321 | 24.7068 | 24.6152 | 24.3861 | 24.2117 | 25.2625 | 28.7816 | 28.7612 | 28.7373 | 28.836 | 28.8567 | 28.8797 | 29.0404 | 29.2228 | 31.978 | 32.0823 | 31.5104 | 29.897 | 29.9585 | 30.1387 | 30.2849 | 30.0503 | 29.9147 | 31.0208 | 31.0542 | 31.1932 | 24.8238 | 24.761 | 24.6522 | 25.192 | 25.2434 | 25.2726 | 22.7931 | 23.0824 | 23.31 | 18.8238 | 18.6786 | 18.4163 | 17.455 | 17.2553 | 23.5433 | 23.5668 | 23.9311 | 20.3127 | 20.2481 | 20.1366 | 19.6627 | 20.3947 | 20.4667 | 20.5079 | 23.0456 | 23.0911 | 23.1146 | 19.3874 | 19.6867 | 19.7657 | 19.8144 | 28.644 | 28.7683 | 28.9679 | 29.1037 | 29.5704 | 30.3734 | 30.6853 | 34.5785 | 34.8248 | 34.0946 | 30.7725 | 30.6428 | 30.4519 | 30.2572 | 30.3266 | 30.2124 | 30.0958 | 29.6308 | 30.0162 | 30.194 | 30.1069 | 27.7159 | 28.1072 | 28.5874 | 29.3735 | 29.6658 | 29.8178 | 26.4922 | 26.6689 | 26.2233 | 20.6321 | 20.5345 | 20.8115 | 29.3654 | 29.1206 | 29.123 | 27.2808 | 27.1218 | 26.8128 | 28.5295 | 28.1986 | 28.6154 | 26.0503 | 26.2762 | 26.1543 | 19.3798 | 19.0757 | 19.2409 | 21.2141 | 21.7933 | 21.7821 | 21.4923 | 20.9033 | 20.5507 | 18.5174 | 18.4945 | 18.3873 | 18.398 | 17.5406 | 17.1837 | 22.4022 | 22.3757 | 22.5068 | 23.2834 | 22.931 | 22.6264 | 30.553 | 29.6166 | 28.6912 | 27.3374 | 27.1873 | 27.2415 | 26.9376 | 27.136 | 27.282 | 27.6477 | 28.4635 | 27.9648 | 21.2429 | 20.7547 | 20.6487 | 29.5114 | 29.5762 | 29.7777 | 29.7355 | 29.4985 | 28.7954
34 | Discharge Gauge | ºC | 51.6485 | 51.6783 | 51.5516 | 51.6512 | 51.699 | 51.6661 | 51.7427 | 51.6415 | 51.5616 | 51.7131 | 51.7401 | 51.7443 | 51.6678 | 51.6074 | 51.5647 | 28.0018 | 28.0029 | 28.0193 | 28.1119 | 28.0458 | 27.9054 | 28.0098 | 28.0066 | 28.0243 | 28.0972 | 27.9819 | 27.9488 | 33.1514 | 33.1716 | 33.2018 | 33.2621 | 33.2585 | 33.2986 | 33.2398 | 33.3885 | 33.3022 | 33.157 | 33.2943 | 33.3142 | 33.247 | 33.3877 | 33.3644 | 42.0675 | 41.9286 | 42.0232 | 41.9111 | 42.1696 | 42.1255 | 41.9895 | 50.5279 | 50.5418 | 50.6202 | 51.7967 | 51.6671 | 51.6819 | 50.5493 | 50.5573 | 50.5196 | 49.9809 | 49.9089 | 50.0958 | 42.0605 | 41.9742 | 42.0643 | 41.9189 | 41.9884 | 41.8964 | 33.3127 | 33.4284 | 33.3203 | 33.1753 | 33.3374 | 33.3531 | 33.3778 | 33.3276 | 33.2157 | 28.1301 | 28.1355 | 27.9304 | 27.9459 | 28.0763 | 27.9561 | 33.2585 | 33.3611 | 33.2748 | 33.1999 | 33.1852 | 33.2237 | 33.2548 | 33.2635 | 33.3189 | 42.11 | 42.0642 | 41.9961 | 41.9739 | 42.0269 | 41.9722 | 41.9941 | 50.6184 | 50.6287 | 50.6438 | 50.6231 | 50.6199 | 50.6222 | 50.5983 | 50.596 | 51.6816 | 51.6077 | 51.5929 | 50.7159 | 50.6016 | 50.5745 | 50.1176 | 49.9914 | 49.9171 | 51.6045 | 51.6847 | 51.6083 | 41.9923 | 41.9847 | 42.093 | 41.9864 | 41.9546 | 41.9259 | 33.1958 | 33.2926 | 33.264 | 27.9408 | 27.9887 | 28.116 | 28.2755 | 28.0103 | 41.9466 | 41.9109 | 41.9798 | 33.2086 | 33.2265 | 33.2491 | 33.3529 | 33.2742 | 33.2369 | 33.2219 | 33.1624 | 33.1595 | 33.1957 | 28.2804 | 28.3402 | 28.2151 | 28.127 | 50.4144 | 50.5938 | 50.6435 | 50.5774 | 50.635 | 50.5996 | 50.5589 | 50.0349 | 50.0548 | 50.0837 | 50.5626 | 50.6299 | 50.5155 | 50.5203 | 50.1665 | 50.279 | 50.1808 | 49.9641 | 51.633 | 51.6193 | 51.659 | 50.6441 | 50.4592 | 50.5208 | 50.0177 | 49.9065 | 49.9594 | 50.7253 | 50.4856 | 50.5921 | 33.4221 | 33.4285 | 33.1781 | 51.7468 | 51.7586 | 51.7144 | 50.1428 | 50.0446 | 50.0136 | 50.5542 | 50.5793 | 50.5899 | 50.5363 | 50.4656 | 50.4359 | 33.3776 | 33.4519 | 33.2027 | 33.4215 | 33.2672 | 33.3777 | 33.253 | 33.1432 | 33.2089 | 28.0168 | 28.019 | 27.9967 | 28.1069 | 28.0557 | 28.0022 | 42.0257 | 41.8775 | 41.8613 | 41.9388 | 41.9706 | 41.8592 | 51.7887 | 51.6744 | 51.7636 | 50.7242 | 50.7255 | 50.5996 | 50.158 | 49.956 | 50.0477 | 50.824 | 50.6556 | 50.5495 | 33.1809 | 33.4186 | 33.2179 | 50.091 | 50.1027 | 50.0705 | 50.6778 | 50.8195 | 50.8571
35
36 | All data
37
38 | Condenser outlet Temp | ºC | 62.9296 | 62.6659 | 62.5821 | 48.8505 | 58.461 | 63.2277 | 62.7848 | 61.703 | 61.6422 | 57.0884 | 62.7943 | 64.121 | 63.9272 | 63.4644 | 63.1777 | 19.9312 | 19.8616 | 19.815 | 19.3698 | 19.2681 | 19.1512 | 19.9629 | 19.8612 | 19.7566 | 19.5568 | 19.441 | 19.2885 | 27.0076 | 27.0194 | 27.0685 | 27.0808 | 27.1023 | 27.0191 | 27.1188 | 27.1549 | 27.0483 | 28.5324 | 28.7134 | 28.6271 | 28.5391 | 28.7299 | 28.5924 | 38.6037 | 38.5102 | 43.8063 | 44.3766 | 44.8269 | 44.8698 | 44.1927 | 58.3007 | 56.3818 | 60.5385 | 61.1673 | 64.9049 | 63.0149 | 48.0944 | 47.9626 | 47.7645 | 47.8734 | 46.5247 | 46.4833 | 37.2105 | 37.3423 | 37.2127 | 36.9054 | 36.8049 | 36.7335 | 24.0654 | 24.1051 | 24.0312 | 24.2811 | 24.4752 | 24.4257 | 24.376 | 24.2513 | 24.0958 | 21.9118 | 22.0541 | 22.3482 | 19.0591 | 18.4114 | 18.1483 | 27.4108 | 27.3923 | 27.2633 | 26.5907 | 26.6012 | 26.5479 | 26.7285 | 26.9909 | 27.5861 | 37.9778 | 37.8682 | 37.8861 | 37.8739 | 37.927 | 37.8274 | 38.0712 | 47.042 | 47.0223 | 47.0176 | 47.0333 | 47.0596 | 46.996 | 46.9506 | 46.9263 | 48.2574 | 48.2035 | 48.141 | 47.19 | 47.0855 | 47.0239 | 46.3966 | 46.255 | 46.1172 | 47.9247 | 47.9743 | 47.9002 | 37.6329 | 37.8385 | 37.8883 | 37.7473 | 37.7458 | 37.6416 | 24.1266 | 24.0718 | 24.0483 | 19.5164 | 19.3356 | 19.1964 | 18.6829 | 18.4405 | 36.5646 | 36.4489 | 36.7001 | 24.0822 | 24.0712 | 24.0346 | 24.2881 | 24.0144 | 23.9092 | 23.8813 | 23.7302 | 23.7073 | 23.6865 | 18.6384 | 18.5637 | 18.592 | 18.5524 | 47.0129 | 47.3693 | 47.1603 | 47.3929 | 46.9336 | 46.8659 | 47.1338 | 46.1954 | 46.3654 | 46.3368 | 66.6618 | 66.7422 | 66.7591 | 67.0782 | 66.1608 | 65.3907 | 65.4746 | 65.2492 | 62.4113 | 60.9815 | 57.1621 | 48.6308 | 48.5012 | 48.1724 | 46.2014 | 46.1408 | 46.2205 | 50.8492 | 54.2135 | 57.7275 | 28.564 | 28.5002 | 28.3152 | 59.874 | 60.8127 | 60.2066 | 58.2772 | 57.745 | 57.3838 | 48.0522 | 57.8868 | 57.3028 | 55.1901 | 55.1102 | 55.8277 | 28.7745 | 28.7561 | 28.5535 | 23.5561 | 23.3952 | 23.6325 | 23.9307 | 23.7626 | 23.2708 | 19.7988 | 19.7113 | 19.6105 | 19.4813 | 19.0958 | 18.9903 | 37.2631 | 37.0439 | 37.0999 | 37.1578 | 37.0797 | 36.9324 | 48.2986 | 48.117 | 48.1633 | 46.9718 | 46.9266 | 46.8632 | 46.1423 | 46.2223 | 46.2472 | 46.7232 | 46.5312 | 46.4658 | 23.7818 | 24.0447 | 23.7941 | 46.0836 | 46.1058 | 46.1002 | 46.693 | 46.9333 | 46.8215
39 | Condenser outlet Pressure | BarA | 13.0064 | 13.0048 | 12.9621 | 13.1964 | 13.2032 | 13.1893 | 13.3369 | 13.3121 | 13.2605 | 13.393 | 13.3898 | 13.4079 | 13.4456 | 13.4332 | 13.4318 | 7.1527 | 7.1526 | 7.1577 | 7.1717 | 7.156 | 7.1253 | 7.1584 | 7.1579 | 7.1666 | 7.1788 | 7.1419 | 7.1413 | 8.2804 | 8.2729 | 8.2877 | 8.2924 | 8.2956 | 8.2914 | 8.2767 | 8.3066 | 8.2786 | 8.2712 | 8.2959 | 8.2968 | 8.2708 | 8.3234 | 8.3047 | 10.4825 | 10.4493 | 10.4656 | 10.4408 | 10.4939 | 10.4833 | 10.4409 | 12.9817 | 12.9788 | 13.0142 | 13.4212 | 13.3754 | 13.3778 | 12.9394 | 12.9323 | 12.9176 | 12.7493 | 12.7385 | 12.7821 | 10.471 | 10.4609 | 10.4743 | 10.4232 | 10.4393 | 10.4292 | 8.2944 | 8.3183 | 8.2991 | 8.2647 | 8.3095 | 8.3117 | 8.3052 | 8.3037 | 8.2809 | 7.1817 | 7.1755 | 7.1434 | 7.1381 | 7.163 | 7.1439 | 8.2899 | 8.3264 | 8.2914 | 8.2593 | 8.2456 | 8.2656 | 8.2774 | 8.2816 | 8.2883 | 10.4781 | 10.4703 | 10.4593 | 10.4346 | 10.4557 | 10.4419 | 10.4605 | 12.9986 | 12.9892 | 13.0031 | 12.9944 | 12.9954 | 12.9767 | 12.9869 | 12.9922 | 13.3806 | 13.363 | 13.3493 | 13.0068 | 12.971 | 12.9539 | 12.8081 | 12.7534 | 12.7318 | 13.3953 | 13.4149 | 13.4024 | 10.49 | 10.4827 | 10.5129 | 10.472 | 10.4938 | 10.4711 | 8.2971 | 8.327 | 8.3119 | 7.16 | 7.1854 | 7.2051 | 7.228 | 7.1724 | 10.4688 | 10.4474 | 10.473 | 8.297 | 8.3109 | 8.3029 | 8.3288 | 8.3157 | 8.3046 | 8.3095 | 8.2741 | 8.2838 | 8.2881 | 7.2382 | 7.2551 | 7.2254 | 7.211 | 12.9908 | 13.0426 | 13.0557 | 13.0323 | 13.0132 | 12.9853 | 12.9845 | 12.8171 | 12.8274 | 12.8091 | 12.957 | 12.9697 | 12.932 | 12.9599 | 12.827 | 12.8467 | 12.817 | 12.7393 | 13.2783 | 13.3158 | 13.3138 | 12.9429 | 12.8841 | 12.9105 | 12.7096 | 12.6638 | 12.6777 | 13.0073 | 12.938 | 12.9628 | 8.3136 | 8.32 | 8.2621 | 13.3887 | 13.3833 | 13.3579 | 12.7786 | 12.7391 | 12.733 | 12.9149 | 12.9196 | 12.9148 | 12.9539 | 12.9369 | 12.923 | 8.3149 | 8.3156 | 8.272 | 8.3288 | 8.2851 | 8.3095 | 8.293 | 8.2718 | 8.2751 | 7.1686 | 7.1471 | 7.1572 | 7.1894 | 7.1705 | 7.1536 | 10.4836 | 10.4276 | 10.4293 | 10.4381 | 10.4373 | 10.4068 | 13.4028 | 13.3585 | 13.3826 | 12.9728 | 12.9793 | 12.9281 | 12.7836 | 12.723 | 12.7363 | 13.0521 | 12.9917 | 12.9708 | 8.2546 | 8.3155 | 8.2593 | 12.7556 | 12.7604 | 12.7499 | 12.9534 | 13.0018 | 13.014
40 | Condenser outlet gauge | ºC | 49.4763 | 49.4714 | 49.3411 | 50.0524 | 50.0727 | 50.031 | 50.4744 | 50.4002 | 50.2454 | 50.642 | 50.6324 | 50.6864 | 50.7987 | 50.7617 | 50.7575 | 27.4485 | 27.448 | 27.4727 | 27.5394 | 27.4643 | 27.3174 | 27.476 | 27.4734 | 27.515 | 27.5734 | 27.397 | 27.394 | 32.5427 | 32.5109 | 32.574 | 32.594 | 32.6076 | 32.5899 | 32.5268 | 32.6549 | 32.535 | 32.5035 | 32.6093 | 32.6128 | 32.5016 | 32.7266 | 32.6467 | 41.1478 | 41.0288 | 41.0872 | 40.998 | 41.1888 | 41.1505 | 40.9986 | 49.4009 | 49.3921 | 49.5 | 50.7261 | 50.5895 | 50.5966 | 49.2715 | 49.2499 | 49.2046 | 48.6865 | 48.6531 | 48.788 | 41.1067 | 41.0703 | 41.1183 | 40.9349 | 40.9926 | 40.9563 | 32.6028 | 32.7046 | 32.6226 | 32.4757 | 32.6671 | 32.6766 | 32.6489 | 32.6425 | 32.5448 | 27.5871 | 27.5575 | 27.4041 | 27.3791 | 27.4976 | 27.4068 | 32.5833 | 32.7392 | 32.5899 | 32.4523 | 32.3937 | 32.4793 | 32.5301 | 32.5478 | 32.5768 | 41.1321 | 41.1042 | 41.0644 | 40.9759 | 41.0518 | 41.0019 | 41.0689 | 49.4525 | 49.4236 | 49.4662 | 49.4395 | 49.4426 | 49.3855 | 49.4166 | 49.4328 | 50.605 | 50.5524 | 50.5116 | 49.4775 | 49.3681 | 49.3158 | 48.8681 | 48.6991 | 48.6323 | 50.6487 | 50.7072 | 50.67 | 41.1746 | 41.1486 | 41.2568 | 41.1101 | 41.1884 | 41.1068 | 32.614 | 32.7417 | 32.6776 | 27.4837 | 27.6047 | 27.6983 | 27.8071 | 27.5428 | 41.0988 | 41.0219 | 41.1136 | 32.6136 | 32.673 | 32.6391 | 32.7494 | 32.6935 | 32.6463 | 32.6672 | 32.5159 | 32.5574 | 32.5758 | 27.8551 | 27.9351 | 27.7946 | 27.7264 | 49.4285 | 49.5865 | 49.6264 | 49.5552 | 49.4969 | 49.4118 | 49.4093 | 48.8959 | 48.9276 | 48.8712 | 49.3253 | 49.3643 | 49.2487 | 49.3342 | 48.9264 | 48.9871 | 48.8955 | 48.6555 | 50.2988 | 50.4112 | 50.4052 | 49.2823 | 49.1022 | 49.183 | 48.5634 | 48.4213 | 48.4645 | 49.4789 | 49.2672 | 49.3431 | 32.6848 | 32.712 | 32.4643 | 50.6291 | 50.6129 | 50.5372 | 48.777 | 48.655 | 48.636 | 49.1964 | 49.211 | 49.1962 | 49.3158 | 49.2639 | 49.2214 | 32.6902 | 32.6931 | 32.5071 | 32.7496 | 32.5629 | 32.6673 | 32.5967 | 32.5059 | 32.52 | 27.5244 | 27.422 | 27.4701 | 27.6236 | 27.5339 | 27.4531 | 41.1516 | 40.9505 | 40.9567 | 40.9883 | 40.9856 | 40.8757 | 50.6712 | 50.5389 | 50.6109 | 49.3737 | 49.3934 | 49.237 | 48.7924 | 48.6051 | 48.6461 | 49.6154 | 49.4314 | 49.3675 | 32.4323 | 32.6926 | 32.4524 | 48.706 | 48.7207 | 48.6883 | 49.3144 | 49.4623 | 49.4993
41 | Condenser outlet enthalpy | KJ/kg | 439.0992 | 438.8027 | 438.792 | 269.828 | 433.5514 | 439.077 | 438.2757 | 437.0815 | 437.1173 | 431.5148 | 438.1801 | 439.6657 | 439.3692 | 438.8628 | 438.5364 | 227.3831 | 227.2854 | 227.2201 | 226.5962 | 226.4536 | 226.2896 | 227.4276 | 227.285 | 227.1383 | 226.8582 | 226.6956 | 226.482 | 237.416 | 237.4328 | 237.5032 | 237.5208 | 237.5516 | 237.4325 | 237.5752 | 237.6269 | 237.4742 | 239.6042 | 239.8646 | 239.7403 | 239.6138 | 239.8883 | 239.6905 | 254.318 | 254.1794 | 423.0037 | 423.708 | 424.0875 | 424.1614 | 423.5003 | 433.8437 | 431.6147 | 436.355 | 436.2366 | 440.6241 | 438.4578 | 268.6634 | 268.4594 | 268.1531 | 268.3279 | 266.2462 | 266.181 | 252.2495 | 252.4449 | 252.2528 | 251.7986 | 251.6499 | 251.5445 | 233.2231 | 233.2796 | 233.1747 | 233.5292 | 233.805 | 233.7347 | 233.6641 | 233.487 | 233.2662 | 230.1701 | 230.3709 | 230.786 | 226.1608 | 225.2551 | 224.8874 | 237.9936 | 237.967 | 237.7822 | 236.8195 | 236.8345 | 236.7583 | 237.0165 | 237.392 | 238.2449 | 253.3872 | 253.2247 | 253.2514 | 253.2337 | 253.3122 | 253.1646 | 253.5263 | 267.0342 | 267.0041 | 266.9964 | 267.0209 | 267.0615 | 266.9641 | 266.8937 | 266.8561 | 268.8998 | 268.8168 | 268.7205 | 267.2622 | 267.1022 | 267.0078 | 266.047 | 265.8311 | 265.6201 | 268.3838 | 268.4599 | 268.3455 | 252.8752 | 253.1804 | 253.2538 | 253.0453 | 253.0427 | 252.8884 | 233.31 | 233.2324 | 233.1989 | 226.8014 | 226.5484 | 226.3535 | 225.6353 | 225.2958 | 251.2944 | 251.1238 | 251.4945 | 233.2471 | 233.2314 | 233.1795 | 233.5394 | 233.151 | 233.0016 | 232.9621 | 232.7478 | 232.7154 | 232.6859 | 225.5731 | 225.4689 | 225.5081 | 225.4527 | 266.9896 | 267.5376 | 267.2147 | 267.5745 | 266.8665 | 266.7632 | 267.1763 | 265.7374 | 265.9983 | 265.9549 | 443.399 | 443.4655 | 443.5539 | 443.8593 | 443.0788 | 442.1807 | 442.3303 | 442.2234 | 437.965 | 436.2408 | 431.781 | 269.4961 | 269.2969 | 268.7855 | 265.7501 | 265.6585 | 265.7805 | 424.9335 | 429.1528 | 433.2195 | 239.6496 | 239.5577 | 239.2919 | 434.8007 | 435.9044 | 435.2536 | 434.2505 | 433.7222 | 433.319 | 268.599 | 433.4979 | 432.8308 | 430.2709 | 430.2156 | 431.0907 | 239.9526 | 239.926 | 239.6345 | 232.5013 | 232.2733 | 232.6095 | 233.0321 | 232.7936 | 232.0971 | 227.1975 | 227.0746 | 226.9334 | 226.7525 | 226.2124 | 226.0646 | 252.3272 | 252.0035 | 252.0863 | 252.1719 | 252.0564 | 251.8388 | 268.9627 | 268.683 | 268.7537 | 266.9268 | 266.8569 | 266.761 | 265.657 | 265.7819 | 265.8196 | 266.5412 | 266.2479 | 266.148 | 232.8208 | 233.1939 | 232.8383 | 265.5678 | 265.6018 | 265.5934 | 266.4981 | 266.8665 | 266.6939
42 | Condenser outlet specific volume | m3/kg | 0.016898 | 0.016872 | 0.016935 | 0.00090248 | 0.016072 | 0.016624 | 0.016335 | 0.016257 | 0.016335 | 0.015607 | 0.016251 | 0.016365 | 0.016284 | 0.016254 | 0.016226 | 0.00081541 | 0.00081523 | 0.00081511 | 0.00081401 | 0.00081376 | 0.00081348 | 0.00081548 | 0.00081523 | 0.00081497 | 0.00081447 | 0.00081419 | 0.00081382 | 0.00083345 | 0.00083349 | 0.00083361 | 0.00083365 | 0.0008337 | 0.00083348 | 0.00083376 | 0.00083384 | 0.00083356 | 0.00083769 | 0.00083819 | 0.00083794 | 0.00083771 | 0.00083822 | 0.00083784 | 0.00086716 | 0.00086687 | 0.019747 | 0.019888 | 0.019818 | 0.01985 | 0.019862 | 0.016423 | 0.016206 | 0.016621 | 0.016023 | 0.016501 | 0.016295 | 0.00089968 | 0.00089917 | 0.0008984 | 0.00089897 | 0.00089373 | 0.00089354 | 0.00086263 | 0.00086306 | 0.00086263 | 0.00086167 | 0.00086134 | 0.00086112 | 0.00082554 | 0.00082564 | 0.00082545 | 0.00082612 | 0.00082662 | 0.00082649 | 0.00082636 | 0.00082603 | 0.00082563 | 0.0008204 | 0.00082076 | 0.00082153 | 0.00081325 | 0.00081165 | 0.00081102 | 0.00083456 | 0.00083449 | 0.00083415 | 0.00083232 | 0.00083235 | 0.0008322 | 0.00083269 | 0.0008334 | 0.00083504 | 0.00086511 | 0.00086476 | 0.00086482 | 0.0008648 | 0.00086496 | 0.00086464 | 0.00086542 | 0.00089552 | 0.00089545 | 0.00089542 | 0.00089549 | 0.00089559 | 0.00089536 | 0.00089517 | 0.00089507 | 0.00089996 | 0.00089976 | 0.00089952 | 0.00089608 | 0.00089571 | 0.00089548 | 0.00089319 | 0.00089269 | 0.00089218 | 0.00089863 | 0.00089881 | 0.00089853 | 0.00086398 | 0.00086465 | 0.0008648 | 0.00086436 | 0.00086434 | 0.00086402 | 0.0008257 | 0.00082555 | 0.00082549 | 0.00081437 | 0.00081392 | 0.00081357 | 0.0008123 | 0.00081172 | 0.00086056 | 0.00086021 | 0.00086099 | 0.00082559 | 0.00082555 | 0.00082546 | 0.00082612 | 0.0008254 | 0.00082513 | 0.00082505 | 0.00082467 | 0.00082461 | 0.00082455 | 0.00081218 | 0.00081199 | 0.00081207 | 0.00081198 | 0.00089541 | 0.00089675 | 0.00089593 | 0.00089685 | 0.00089509 | 0.00089485 | 0.00089588 | 0.00089241 | 0.00089305 | 0.00089296 | 0.017382 | 0.017368 | 0.017435 | 0.01742 | 0.017553 | 0.017437 | 0.017498 | 0.01761 | 0.01639 | 0.016172 | 0.015743 | 0.00090182 | 0.00090135 | 0.00090002 | 0.00089252 | 0.00089233 | 0.00089262 | 0.015485 | 0.016018 | 0.016389 | 0.00083776 | 0.00083758 | 0.00083708 | 0.015931 | 0.016045 | 0.016018 | 0.016769 | 0.016777 | 0.016746 | 0.00089954 | 0.016481 | 0.016422 | 0.016108 | 0.016127 | 0.016236 | 0.00083835 | 0.0008383 | 0.00083775 | 0.0008242 | 0.00082379 | 0.0008244 | 0.00082519 | 0.00082476 | 0.00082347 | 0.00081507 | 0.00081486 | 0.00081461 | 0.00081428 | 0.00081333 | 0.00081308 | 0.00086279 | 0.00086212 | 0.00086229 | 0.00086248 | 0.00086223 | 0.00086177 | 0.0009001 | 0.00089942 | 0.00089958 | 0.00089526 | 0.00089509 | 0.00089488 | 0.00089224 | 0.00089259 | 0.00089267 | 0.00089425 | 0.00089356 | 0.00089332 | 0.00082482 | 0.00082548 | 0.00082485 | 0.00089204 | 0.00089212 | 0.00089211 | 0.00089421 | 0.00089509 | 0.00089465
43 | Oil flow(from Coriolis meter) | m3/hr | 0.8232 | 1.2957 | 0.58466 | 2.5652 | 2.2198 | 3.585 | 3.2995 | 3.4562 | 3.4459 | 3.0125 | 3.3249 | 3.3453 | 2.6173 | 2.5554 | 2.548 | 1.7097 | 1.548 | 2.0649 | 2.4146 | 1.9063 | 2.8224 | 1.0809 | 3.3334 | 1.7294 | 2.1767 | 2.3383 | 2.6578 | 1.6925 | 1.7112 | 1.5511 | 1.7967 | 1.7283 | 1.7522 | 1.727 | 1.7675 | 1.7125 | 1.7026 | 1.7455 | 1.7419 | 1.6737 | 1.5884 | 1.6711 | 2.7545 | 2.391 | 2.5158 | 2.7106 | 2.8878 | 2.6815 | 3.077 | 3.449 | 3.4526 | 3.5135 | 3.3598 | 3.3923 | 3.2014 | 3.4012 | 3.2829 | 3.4435 | 3.1465 | 3.3399 | 3.4754 | 3.3203 | 3.1158 | 2.9665 | 3.3055 | 3.3343 | 3.4 | 1.2898 | -0.087323 | -0.087149 | -0.08721 | -0.087407 | -0.087445 | -0.087371 | -0.087287 | -0.087356 | -0.087435 | -0.08743 | -0.087407 | 1.1153 | 1.3586 | 0.95133 | 1.7877 | 1.7826 | 1.7745 | 1.8736 | 1.8327 | 1.798 | 1.7297 | 1.7758 | 1.8303 | 3.2635 | 2.9657 | 2.9667 | 3.4473 | 3.4487 | 3.4911 | 3.1709 | 3.5254 | 3.4988 | 3.4647 | 3.4244 | 3.5817 | 3.4874 | 3.396 | 3.5166 | 3.3631 | 3.4401 | 3.409 | 3.3709 | 3.4555 | 3.4289 | 3.3061 | 3.3695 | 3.2814 | 3.1415 | 3.227 | 3.4368 | 2.4513 | 2.8303 | 2.3925 | 2.7399 | 2.8007 | 2.6863 | 1.7121 | 1.6289 | 1.7105 | 0.95405 | 0.96186 | 0.9611 | 0.95635 | 0.94654 | 3.3347 | 3.225 | 2.9106 | 1.7246 | 1.6962 | 1.815 | 1.7036 | 1.7167 | 1.6121 | 1.6906 | 1.0886 | 0.97593 | 0.76148 | -0.087224 | 1.2108 | 1.632 | 1.2297 | 3.438 | 3.3868 | 3.4775 | 3.4096 | 3.4376 | 3.3661 | 3.1758 | 3.3718 | 3.434 | 3.3974 | 3.0165 | 3.2518 | 3.4668 | 3.1946 | 3.0268 | 3.0704 | 3.4377 | 2.8544 | 2.4486 | 2.4486 | 2.4395 | 2.2385 | 2.3954 | 2.4339 | 2.3551 | 2.33 | 2.3509 | 2.3829 | 2.6506 | 2.1368 | 1.0563 | 1.0465 | 1.0489 | 2.4192 | 2.4118 | 2.4414 | 2.8753 | 3.1463 | 2.9777 | 2.8234 | 2.9772 | 2.7899 | 2.4674 | 2.4217 | 2.4947 | 1.6339 | 1.7331 | 1.6461 | 1.087 | 1.0489 | 1.0594 | 1.0384 | 1.1851 | 0.99594 | -0.087317 | 0.63614 | -0.087444 | 0.64103 | -0.087417 | 1.1103 | 2.1786 | 2.1492 | 1.986 | 2.4165 | 2.3444 | 2.5862 | 2.5215 | 2.5056 | 2.6371 | 2.8738 | 3.0474 | 3.0115 | 2.8429 | 3.0321 | 3.1359 | 2.8283 | 3.2098 | 2.9735 | 1.668 | 1.7092 | 1.7219 | 3.1612 | 3.2919 | 3.3233 | 3.0149 | 3.2999 | 3.008
44 | Liquid subcoooling | ºC | no subcooling | no subcooling | no subcooling | 1.2019 | no subcooling | no subcooling | no subcooling | no subcooling | no subcooling | no subcooling | no subcooling | no subcooling | no subcooling | no subcooling | no subcooling | 7.5173 | 7.5864 | 7.6576 | 8.1696 | 8.1962 | 8.1662 | 7.5132 | 7.6121 | 7.7584 | 8.0166 | 7.956 | 8.1055 | 5.535 | 5.4916 | 5.5055 | 5.5131 | 5.5053 | 5.5708 | 5.408 | 5.5 | 5.4867 | 3.971 | 3.8959 | 3.9858 | 3.9625 | 3.9967 | 4.0543 | 2.5441 | 2.5186 | no subcooling | no subcooling | no subcooling | no subcooling | no subcooling | no subcooling | no subcooling | no subcooling | no subcooling | no subcooling | no subcooling | 1.1771 | 1.2873 | 1.4401 | 0.81315 | 2.1284 | 2.3047 | 3.8962 | 3.728 | 3.9056 | 4.0295 | 4.1878 | 4.2228 | 8.5374 | 8.5995 | 8.5914 | 8.1946 | 8.1919 | 8.2509 | 8.2729 | 8.3912 | 8.4491 | 5.6753 | 5.5034 | 5.0559 | 8.32 | 9.0863 | 9.2585 | 5.1725 | 5.3469 | 5.3265 | 5.8616 | 5.7925 | 5.9313 | 5.8017 | 5.5569 | 4.9907 | 3.1543 | 3.236 | 3.1783 | 3.1019 | 3.1248 | 3.1745 | 2.9977 | 2.4105 | 2.4014 | 2.4486 | 2.4062 | 2.3829 | 2.3895 | 2.4659 | 2.5065 | 2.3475 | 2.3489 | 2.3706 | 2.2875 | 2.2825 | 2.2919 | 2.4714 | 2.444 | 2.5151 | 2.724 | 2.7329 | 2.7698 | 3.5417 | 3.3101 | 3.3685 | 3.3628 | 3.4426 | 3.4652 | 8.4875 | 8.6699 | 8.6293 | 7.9673 | 8.2691 | 8.5019 | 9.1242 | 9.1024 | 4.5341 | 4.5731 | 4.4135 | 8.5314 | 8.6018 | 8.6046 | 8.4613 | 8.6791 | 8.7371 | 8.786 | 8.7857 | 8.8501 | 8.8893 | 9.2167 | 9.3713 | 9.2026 | 9.174 | 2.4156 | 2.2173 | 2.4661 | 2.1623 | 2.5633 | 2.5459 | 2.2755 | 2.7005 | 2.5622 | 2.5344 | no subcooling | no subcooling | no subcooling | no subcooling | no subcooling | no subcooling | no subcooling | no subcooling | no subcooling | no subcooling | no subcooling | 0.65151 | 0.601 | 1.0105 | 2.362 | 2.2805 | 2.244 | no subcooling | no subcooling | no subcooling | 4.1208 | 4.2119 | 4.1491 | no subcooling | no subcooling | no subcooling | no subcooling | no subcooling | no subcooling | 1.1442 | no subcooling | no subcooling | no subcooling | no subcooling | no subcooling | 3.9157 | 3.937 | 3.9536 | 9.1935 | 9.1677 | 9.0348 | 8.666 | 8.7433 | 9.2492 | 7.7255 | 7.7107 | 7.8595 | 8.1424 | 8.4381 | 8.4628 | 3.8886 | 3.9066 | 3.8568 | 3.8305 | 3.9059 | 3.9433 | 2.3726 | 2.4219 | 2.4476 | 2.4019 | 2.4668 | 2.3738 | 2.6501 | 2.3827 | 2.399 | 2.8922 | 2.9002 | 2.9017 | 8.6505 | 8.6479 | 8.6583 | 2.6224 | 2.6149 | 2.5881 | 2.6214 | 2.529 | 2.6778
45 | Condenser Duty (refrigerant side) | kw | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
46 | Water inlet Temp | ºC | 27.6021 | 27.1138 | 26.5739 | 20.0131 | 25.4186 | 44.8106 | 44.0981 | 44.3989 | 47.9532 | 20.627 | 24.847 | 28.8585 | 26.0266 | 25.979 | 25.8482 | 12.4576 | 12.4522 | 12.3534 | 11.7712 | 11.6617 | 11.542 | 13.0214 | 12.9077 | 12.7539 | 12.5297 | 12.4147 | 12.2925 | 11.6868 | 11.7121 | 11.6945 | 11.6133 | 11.5991 | 11.6294 | 11.621 | 11.7003 | 11.7871 | 12.0094 | 12.1021 | 12.2977 | 12.1133 | 12.2552 | 12.3396 | 17.8031 | 18.2117 | 20.2815 | 22.2195 | 20.2343 | 19.4981 | 18.7659 | 37.5454 | 35.5569 | 38.5649 | 28.5304 | 39.9277 | 44.2978 | 26.9598 | 30.973 | 28.1868 | 22.7969 | 18.2961 | 17.5048 | 19.1706 | 19.2579 | 19.2399 | 19.3284 | 19.195 | 19.2122 | 16.3518 | 16.3348 | 16.1146 | 15.946 | 15.8575 | 15.7966 | 15.5707 | 15.5261 | 15.421 | 15.5106 | 15.2922 | 14.4391 | 13.8599 | 16.2164 | 17.8913 | 13.3663 | 13.2669 | 13.1478 | 13.2412 | 13.371 | 13.4436 | 13.6418 | 13.7093 | 13.853 | 16.1733 | 16.0673 | 16.0418 | 16.064 | 16.1212 | 16.0748 | 17.7088 | 19.5885 | 19.5834 | 19.5744 | 19.5845 | 19.599 | 19.6388 | 19.6134 | 19.3662 | 19.8731 | 19.9867 | 20.0976 | 19.5893 | 19.5332 | 19.5603 | 19.4082 | 19.2273 | 19.0251 | 20.7719 | 20.7342 | 20.8174 | 15.4273 | 15.3216 | 15.2496 | 15.2471 | 15.1754 | 15.1093 | 13.9511 | 13.8172 | 13.6947 | 12.6948 | 13.0823 | 13.7749 | 18.1605 | 18.0699 | 17.7684 | 17.9092 | 17.8826 | 13.815 | 13.8442 | 13.8815 | 13.8543 | 13.8974 | 13.8801 | 13.8312 | 13.4268 | 13.3494 | 13.3756 | 15.9948 | 15.8921 | 15.852 | 15.8267 | 20.1856 | 20.0852 | 20.1214 | 20.136 | 20.5078 | 20.4149 | 20.3691 | 20.1037 | 19.9334 | 19.4516 | 28.874 | 28.8325 | 28.7274 | 28.699 | 28.4905 | 28.3242 | 28.2643 | 28.1149 | 21.4464 | 21.4876 | 21.5159 | 21.2924 | 21.2721 | 21.2758 | 21.2081 | 21.0269 | 20.8481 | 20.2567 | 19.6765 | 20.0889 | 13.6438 | 13.6113 | 13.5818 | 33.3389 | 36.6842 | 37.3747 | 37.4102 | 36.2679 | 35.6916 | 22.9187 | 37.6857 | 40.7735 | 40.0671 | 40.3214 | 40.6087 | 12.7142 | 12.6812 | 12.6039 | 13.639 | 13.5863 | 13.5706 | 12.6107 | 12.4486 | 12.2551 | 13.9622 | 13.9383 | 13.8689 | 13.8046 | 13.6867 | 13.6523 | 17.3045 | 17.5048 | 17.534 | 17.8022 | 17.7281 | 17.6796 | 19.6289 | 19.5284 | 19.3725 | 19.1337 | 19.015 | 18.9288 | 18.9337 | 18.8658 | 18.7066 | 18.1262 | 18.0776 | 18.0933 | 12.1947 | 11.0955 | 11.0197 | 22.8478 | 22.8397 | 22.8634 | 22.4285 | 22.2296 | 22.1522
47 | Water outlet temp | ºC | 31.5564 | 30.0601 | 31.6703 | 39.6957 | 44.0714 | 30.3964 | 30.2094 | 29.9294 | 30.9877 | 32.1909 | 43.6189 | 33.9653 | 37.619 | 36.9253 | 33.4177 | 16.3561 | 16.3462 | 19.3143 | 18.3466 | 17.5733 | 15.8671 | 16.1684 | 16.8745 | 15.2569 | 16.5049 | 15.7798 | 16.5462 | 24.5081 | 26.209 | 24.9913 | 25.2999 | 25.2507 | 24.5418 | 24.6348 | 24.8275 | 27.3191 | 24.9972 | 26.8587 | 25.2799 | 27.744 | 28.1517 | 26.7868 | 33.9203 | 25.0308 | 38.5371 | 24.8292 | 22.9492 | 25.4844 | 21.6727 | 31.7105 | 31.934 | 40.3174 | 49.6287 | 36.9957 | 37.9361 | 39.2377 | 39.4004 | 41.8507 | 46.9558 | 33.0344 | 42.8495 | 44.9395 | 47.2846 | 45.8457 | 50.1188 | 47.1407 | 48.3521 | 36.4704 | 35.9823 | 36.2697 | 32.8356 | 34.3842 | 32.7164 | 31.7966 | 32.1115 | 32.9647 | 20.0584 | 15.5873 | 15.4895 | 16.5552 | 19.5249 | 15.1391 | 21.4277 | 19.7597 | 20.6889 | 24.9823 | 24.8287 | 29.4682 | 27.2473 | 25.5081 | 27.071 | 36.5213 | 42.202 | 37.9827 | 38.8177 | 36.3446 | 35.3697 | 37.5654 | 47.5238 | 45.5295 | 48.5766 | 50.1006 | 46.1432 | 46.632 | 49.6106 | 46.0687 | 53.156 | 53.7208 | 49.2415 | 52.4622 | 49.8108 | 48.4789 | 52.862 | 54.0405 | 50.7946 | 57.664 | 61.944 | 61.3853 | 38.7612 | 39.793 | 36.3515 | 40.8879 | 35.7884 | 37.9032 | 29.6009 | 30.4048 | 29.329 | 18.7343 | 18.253 | 19.3824 | 14.3899 | 15.2207 | 47.0884 | 47.5911 | 46.9919 | 30.6469 | 29.6385 | 29.7104 | 27.5687 | 28.6781 | 28.6398 | 29.7591 | 29.9805 | 30.0481 | 30.5321 | 12.702 | 13.6852 | 14.3204 | 13.0383 | 47.837 | 48.3072 | 34.9512 | 50.805 | 48.2934 | 49.9925 | 55.7676 | 59.7699 | 58.827 | 54.7037 | 34.7344 | 34.3884 | 34.4314 | 31.0737 | 38.1057 | 35.0242 | 33.4602 | 36.5148 | 39.1721 | 42.9336 | 39.0972 | 47.2853 | 42.5878 | 46.753 | 44.869 | 50.6929 | 51.1671 | 36.9144 | 48.3349 | 39.7977 | 25.8963 | 23.517 | 25.3456 | 49.6756 | 37.7648 | 40.5525 | 35.2966 | 37.0462 | 35.5421 | 42.004 | 47.9044 | 38.4117 | 40.1793 | 36.5618 | 39.2312 | 22.381 | 22.1141 | 22.1801 | 34.9776 | 35.7639 | 33.8167 | 33.5131 | 32.4609 | 33.0911 | 21.8727 | 21.3105 | 19.6911 | 20.9913 | 21.1958 | 20.5297 | 44.9197 | 47.9299 | 47.2804 | 48.4287 | 46.177 | 49.6908 | 53.6828 | 54.1247 | 53.4829 | 51.7569 | 51.2061 | 57.7445 | 56.3868 | 51.9502 | 54.8903 | 61.2735 | 56.6091 | 58.1285 | 33.711 | 33.8634 | 33.4014 | 61.5977 | 62.4826 | 61.2339 | 63.0719 | 63.2921 | 64.1162
48 | Water Flow rate (calculated) | m3/hr | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
49
50 | Liquid line strainers temp | ºC | 35.77 | 35.7491 | 35.387 | 36.7821 | 36.7457 | 35.8513 | 36.1013 | 36.1943 | 36.1801 | 35.9573 | 36.2061 | 36.3279 | 35.845 | 35.9299 | 35.9001 | 17.8168 | 17.8047 | 17.7367 | 17.8598 | 17.7771 | 17.6045 | 17.8895 | 17.8429 | 17.8426 | 17.8509 | 17.787 | 17.6719 | 20.9027 | 20.875 | 20.9086 | 20.9696 | 20.9914 | 21.049 | 20.583 | 20.6927 | 20.833 | 20.4365 | 20.6213 | 20.4039 | 20.3054 | 20.3683 | 20.3179 | 28.9708 | 28.7566 | 28.819 | 28.4852 | 28.3413 | 28.3495 | 28.1883 | 35.6903 | 35.5584 | 35.8228 | 36.6247 | 35.4899 | 35.9645 | 34.7294 | 34.68 | 34.6276 | 34.2346 | 34.1851 | 34.6106 | 29.7919 | 29.6403 | 29.7927 | 29.731 | 29.5642 | 29.455 | 21.8173 | 21.8672 | 21.609 | 21.6596 | 21.7639 | 21.7194 | 21.698 | 21.508 | 21.4127 | 17.2275 | 17.1544 | 17.0246 | 17.2791 | 17.2687 | 17.1197 | 19.3802 | 19.5041 | 19.4294 | 19.8333 | 19.9069 | 19.9265 | 19.9314 | 19.9789 | 19.9628 | 28.2511 | 28.1549 | 28.1877 | 27.7717 | 27.9333 | 27.8063 | 27.5638 | 35.1703 | 35.1374 | 35.1211 | 35.1275 | 35.1411 | 34.968 | 35.0275 | 35.0547 | 35.5169 | 35.4045 | 35.5792 | 34.0782 | 33.9412 | 33.8676 | 33.6533 | 33.4583 | 33.1871 | 35.291 | 35.3984 | 35.336 | 26.7387 | 27.0113 | 26.8133 | 26.5493 | 26.5671 | 26.4097 | 19.5811 | 19.5401 | 19.3927 | 16.1917 | 16.2726 | 16.384 | 16.6414 | 16.3755 | 27.8706 | 27.5711 | 27.7412 | 19.1731 | 19.1998 | 19.1668 | 19.0656 | 18.9145 | 18.8172 | 18.7174 | 18.1569 | 18.1129 | 18.0443 | 14.4297 | 14.4271 | 14.4092 | 14.451 | 33.076 | 33.2669 | 33.0264 | 33.2927 | 32.2822 | 32.212 | 32.5648 | 31.3818 | 32.2057 | 31.5219 | 35.9596 | 36.12 | 35.8515 | 35.8122 | 35.3043 | 35.5121 | 35.4678 | 35.1191 | 36.357 | 36.6341 | 36.6941 | 35.5966 | 35.2948 | 35.3649 | 34.878 | 34.9249 | 35.1476 | 36.6823 | 36.6097 | 36.3613 | 20.2797 | 20.2475 | 20.0054 | 37.6986 | 37.483 | 37.5144 | 35.1415 | 35.0416 | 35.0195 | 35.8057 | 35.6554 | 35.5957 | 36.7519 | 36.5958 | 36.5478 | 20.3036 | 20.4673 | 20.3016 | 22.6112 | 22.4146 | 22.4245 | 22.4484 | 22.279 | 22.4022 | 19.0951 | 19.0934 | 19.0829 | 19.1539 | 19.2934 | 19.1855 | 30.9115 | 30.6281 | 30.6611 | 30.2285 | 30.1831 | 30.0949 | 38.4898 | 38.181 | 38.1918 | 36.7929 | 36.7892 | 36.5988 | 35.9225 | 35.7306 | 35.7006 | 38.4095 | 38.1857 | 38.3361 | 21.6485 | 21.7534 | 21.5388 | 37.0339 | 36.9675 | 36.9494 | 37.5945 | 38.0217 | 38.2088
51 | Liquid line strainers pressure | BarA | 12.8496 | 12.834 | 12.7952 | 13.0417 | 13.0542 | 13.0414 | 13.191 | 13.1698 | 13.1282 | 13.2526 | 13.2613 | 13.2872 | 13.3197 | 13.3152 | 13.3075 | 7.1448 | 7.1469 | 7.1353 | 7.1626 | 7.1552 | 7.1061 | 7.1471 | 7.1405 | 7.1501 | 7.1623 | 7.1463 | 7.1463 | 8.2294 | 8.2328 | 8.2374 | 8.2465 | 8.2482 | 8.261 | 8.236 | 8.2804 | 8.2519 | 8.2387 | 8.2638 | 8.2638 | 8.2422 | 8.2865 | 8.2763 | 10.3785 | 10.3501 | 10.3732 | 10.3461 | 10.4026 | 10.3845 | 10.3413 | 12.8588 | 12.8404 | 12.8787 | 13.2851 | 13.2294 | 13.2454 | 12.7994 | 12.7936 | 12.7912 | 12.6222 | 12.5948 | 12.6509 | 10.3828 | 10.3634 | 10.3768 | 10.3394 | 10.3383 | 10.3277 | 8.2585 | 8.303 | 8.2708 | 8.2441 | 8.2933 | 8.301 | 8.2912 | 8.2769 | 8.27 | 7.1722 | 7.1567 | 7.1381 | 7.134 | 7.1345 | 7.1247 | 8.2672 | 8.2911 | 8.2498 | 8.2157 | 8.2031 | 8.2106 | 8.2368 | 8.2198 | 8.2558 | 10.3897 | 10.3653 | 10.3477 | 10.3453 | 10.3319 | 10.3332 | 10.3597 | 12.8745 | 12.8619 | 12.8733 | 12.8773 | 12.8779 | 12.8588 | 12.8556 | 12.8539 | 13.2649 | 13.2267 | 13.2111 | 12.8946 | 12.8459 | 12.8259 | 12.6775 | 12.6341 | 12.5907 | 13.2516 | 13.281 | 13.2825 | 10.3842 | 10.4104 | 10.4288 | 10.4015 | 10.3998 | 10.3931 | 8.2688 | 8.2896 | 8.2865 | 7.1585 | 7.168 | 7.191 | 7.2348 | 7.1713 | 10.3564 | 10.36 | 10.3599 | 8.2802 | 8.2849 | 8.28 | 8.3125 | 8.2815 | 8.2834 | 8.2725 | 8.2486 | 8.2517 | 8.2699 | 7.2271 | 7.2361 | 7.2182 | 7.1957 | 12.854 | 12.9301 | 12.946 | 12.9293 | 12.8835 | 12.8626 | 12.8586 | 12.6828 | 12.6903 | 12.6839 | 12.7984 | 12.823 | 12.7871 | 12.7981 | 12.6595 | 12.6962 | 12.6586 | 12.591 | 13.1417 | 13.1712 | 13.1865 | 12.7768 | 12.7235 | 12.7404 | 12.5484 | 12.5193 | 12.5504 | 12.8694 | 12.8014 | 12.8415 | 8.3089 | 8.3144 | 8.2466 | 13.2443 | 13.2325 | 13.2168 | 12.6372 | 12.589 | 12.5783 | 12.763 | 12.7622 | 12.7777 | 12.815 | 12.8048 | 12.797 | 8.2864 | 8.3042 | 8.2654 | 8.2954 | 8.2568 | 8.2908 | 8.2713 | 8.2379 | 8.2517 | 7.1445 | 7.1607 | 7.1396 | 7.1718 | 7.1576 | 7.1414 | 10.3696 | 10.3265 | 10.3218 | 10.3236 | 10.3393 | 10.2928 | 13.2456 | 13.2288 | 13.229 | 12.8331 | 12.8263 | 12.7862 | 12.6396 | 12.5837 | 12.5961 | 12.9097 | 12.8599 | 12.8321 | 8.2176 | 8.2781 | 8.2282 | 12.6131 | 12.6181 | 12.61 | 12.794 | 12.8459 | 12.8796
52 | Liquid line strainers gauge | ºC | 48.996 | 48.9479 | 48.8283 | 49.5837 | 49.6216 | 49.5827 | 50.0361 | 49.9719 | 49.8463 | 50.2215 | 50.2477 | 50.3254 | 50.4228 | 50.4094 | 50.3864 | 27.4111 | 27.4212 | 27.3653 | 27.496 | 27.4604 | 27.2255 | 27.4217 | 27.3903 | 27.4362 | 27.4944 | 27.4183 | 27.418 | 32.3242 | 32.3386 | 32.3583 | 32.3974 | 32.4048 | 32.4598 | 32.3526 | 32.5429 | 32.4209 | 32.3642 | 32.4716 | 32.4718 | 32.3793 | 32.5689 | 32.5254 | 40.7736 | 40.6708 | 40.7545 | 40.6563 | 40.8605 | 40.7954 | 40.6392 | 49.0244 | 48.9677 | 49.0853 | 50.3193 | 50.1518 | 50.2 | 48.8413 | 48.8235 | 48.8159 | 48.2917 | 48.2063 | 48.3809 | 40.789 | 40.719 | 40.7676 | 40.6321 | 40.6283 | 40.5897 | 32.4491 | 32.6395 | 32.5018 | 32.3872 | 32.5982 | 32.631 | 32.5891 | 32.5277 | 32.4984 | 27.5418 | 27.4677 | 27.3787 | 27.3592 | 27.3614 | 27.3145 | 32.4863 | 32.5887 | 32.4118 | 32.2653 | 32.2109 | 32.2433 | 32.3558 | 32.2826 | 32.4373 | 40.8141 | 40.726 | 40.6623 | 40.6535 | 40.6049 | 40.6099 | 40.7058 | 49.0726 | 49.0339 | 49.0689 | 49.0811 | 49.0828 | 49.0244 | 49.0143 | 49.0093 | 50.2585 | 50.1437 | 50.0967 | 49.1341 | 48.9847 | 48.9231 | 48.4637 | 48.3287 | 48.1933 | 50.2185 | 50.3067 | 50.3112 | 40.7942 | 40.8889 | 40.9548 | 40.8564 | 40.8505 | 40.8263 | 32.4932 | 32.5822 | 32.5691 | 27.4762 | 27.5218 | 27.6313 | 27.8394 | 27.5372 | 40.6936 | 40.7067 | 40.7064 | 32.5419 | 32.5619 | 32.5409 | 32.6798 | 32.5477 | 32.5555 | 32.5089 | 32.4065 | 32.4197 | 32.4977 | 27.8029 | 27.8451 | 27.7607 | 27.6536 | 49.0094 | 49.2431 | 49.2917 | 49.2405 | 49.1001 | 49.0359 | 49.0237 | 48.4801 | 48.5034 | 48.4836 | 48.8381 | 48.9139 | 48.8034 | 48.8371 | 48.4079 | 48.5218 | 48.405 | 48.1943 | 49.8871 | 49.9764 | 50.0223 | 48.7716 | 48.6066 | 48.6588 | 48.0609 | 47.9696 | 48.0673 | 49.0568 | 48.8476 | 48.9712 | 32.6647 | 32.6881 | 32.3979 | 50.1966 | 50.1611 | 50.1138 | 48.3383 | 48.1879 | 48.1546 | 48.7288 | 48.7262 | 48.7742 | 48.8896 | 48.858 | 48.8338 | 32.5685 | 32.6447 | 32.4788 | 32.6069 | 32.4419 | 32.5873 | 32.5039 | 32.3607 | 32.4201 | 27.4095 | 27.4869 | 27.386 | 27.5396 | 27.4719 | 27.3948 | 40.7415 | 40.5855 | 40.5685 | 40.5752 | 40.6319 | 40.4631 | 50.2006 | 50.1499 | 50.1504 | 48.9451 | 48.9243 | 48.8004 | 48.3458 | 48.1715 | 48.2102 | 49.1807 | 49.0275 | 48.9421 | 32.2732 | 32.533 | 32.3188 | 48.2633 | 48.2788 | 48.2535 | 48.8246 | 48.9845 | 49.0883
53 | Liquid line strainers enthalpy | KJ/kg | 250.0976 | 250.067 | 249.5361 | 251.5844 | 251.5306 | 250.215 | 250.5809 | 250.7178 | 250.6973 | 250.3687 | 250.7341 | 250.913 | 250.203 | 250.3278 | 250.2841 | 224.4247 | 224.4078 | 224.3129 | 224.4849 | 224.3694 | 224.1282 | 224.5261 | 224.4611 | 224.4608 | 224.4725 | 224.3833 | 224.2227 | 228.7564 | 228.7174 | 228.7647 | 228.8505 | 228.8812 | 228.9624 | 228.3072 | 228.4617 | 228.6586 | 228.1015 | 228.3612 | 228.0559 | 227.9175 | 228.0062 | 227.9352 | 240.2327 | 239.9248 | 240.0145 | 239.5351 | 239.3285 | 239.3402 | 239.109 | 249.9804 | 249.7871 | 250.1749 | 251.3498 | 249.683 | 250.3793 | 248.5729 | 248.5007 | 248.424 | 247.851 | 247.779 | 248.4003 | 241.4149 | 241.1965 | 241.4161 | 241.3272 | 241.0869 | 240.9296 | 230.0441 | 230.1147 | 229.7506 | 229.8217 | 229.969 | 229.9065 | 229.8762 | 229.6085 | 229.4742 | 223.6035 | 223.5015 | 223.3206 | 223.6749 | 223.6605 | 223.4529 | 226.6209 | 226.7945 | 226.6895 | 227.2551 | 227.3581 | 227.3857 | 227.3927 | 227.4592 | 227.4369 | 239.1991 | 239.0611 | 239.1081 | 238.5118 | 238.7433 | 238.5615 | 238.2141 | 249.2177 | 249.1697 | 249.1457 | 249.155 | 249.1749 | 248.9216 | 249.0088 | 249.0486 | 249.7222 | 249.5578 | 249.814 | 247.6206 | 247.4211 | 247.314 | 247.0025 | 246.7186 | 246.324 | 249.3913 | 249.5483 | 249.4568 | 237.0345 | 237.4241 | 237.1411 | 236.7643 | 236.7897 | 236.5651 | 226.9022 | 226.8449 | 226.6385 | 222.1625 | 222.2751 | 222.4301 | 222.7885 | 222.4181 | 238.6535 | 238.2246 | 238.4682 | 226.331 | 226.3684 | 226.3223 | 226.1809 | 225.9693 | 225.8333 | 225.6938 | 224.9109 | 224.8495 | 224.754 | 219.7213 | 219.7178 | 219.6928 | 219.7503 | 246.1609 | 246.4382 | 246.0882 | 246.4757 | 245.008 | 244.9062 | 245.4181 | 243.7046 | 244.8978 | 243.9074 | 250.3767 | 250.6121 | 250.218 | 250.1601 | 249.4161 | 249.7206 | 249.6559 | 249.1453 | 250.9573 | 251.3648 | 251.4531 | 249.8437 | 249.4015 | 249.5042 | 248.7926 | 248.8615 | 249.1874 | 251.4393 | 251.3331 | 250.9669 | 227.882 | 227.8368 | 227.4966 | 252.9348 | 252.6162 | 252.6628 | 249.1777 | 249.0317 | 248.9994 | 250.1508 | 249.9302 | 249.8425 | 251.5425 | 251.3126 | 251.242 | 227.9153 | 228.1453 | 227.9123 | 231.1645 | 230.8867 | 230.9008 | 230.9345 | 230.6951 | 230.8691 | 226.2112 | 226.209 | 226.1941 | 226.2937 | 226.4891 | 226.3378 | 243.0323 | 242.6224 | 242.6701 | 242.045 | 241.9795 | 241.8522 | 254.1063 | 253.6488 | 253.6649 | 251.6027 | 251.5973 | 251.3173 | 250.3237 | 250.0424 | 249.9983 | 253.992 | 253.6609 | 253.8844 | 229.806 | 229.9541 | 229.6515 | 251.9609 | 251.8628 | 251.8362 | 252.7867 | 253.4182 | 253.6949
54 | Liquid line strainers specific volume | m3/kg | 0.00085674 | 0.00085668 | 0.00085559 | 0.00085979 | 0.00085967 | 0.00085689 | 0.00085758 | 0.00085788 | 0.00085786 | 0.0008571 | 0.00085787 | 0.00085823 | 0.00085671 | 0.00085698 | 0.00085689 | 0.00081021 | 0.00081018 | 0.00081002 | 0.00081031 | 0.00081012 | 0.00080971 | 0.00081039 | 0.00081028 | 0.00081028 | 0.00081029 | 0.00081014 | 0.00080986 | 0.00081744 | 0.00081737 | 0.00081745 | 0.0008176 | 0.00081766 | 0.0008178 | 0.00081664 | 0.00081689 | 0.00081726 | 0.00081627 | 0.00081672 | 0.00081618 | 0.00081594 | 0.00081608 | 0.00081596 | 0.00083796 | 0.00083737 | 0.00083754 | 0.00083662 | 0.00083619 | 0.00083622 | 0.00083579 | 0.00085649 | 0.00085609 | 0.00085689 | 0.00085916 | 0.00085567 | 0.00085712 | 0.00085357 | 0.00085343 | 0.00085327 | 0.00085217 | 0.00085203 | 0.00085329 | 0.00084027 | 0.00083985 | 0.00084028 | 0.00084012 | 0.00083965 | 0.00083934 | 0.00081974 | 0.00081985 | 0.00081921 | 0.00081935 | 0.00081959 | 0.00081948 | 0.00081943 | 0.00081895 | 0.00081871 | 0.00080878 | 0.00080861 | 0.00080831 | 0.00080892 | 0.0008089 | 0.00080854 | 0.00081364 | 0.00081394 | 0.00081377 | 0.00081478 | 0.00081496 | 0.00081501 | 0.00081501 | 0.00081514 | 0.00081508 | 0.00083595 | 0.00083569 | 0.00083579 | 0.00083464 | 0.00083509 | 0.00083474 | 0.00083407 | 0.00085488 | 0.00085478 | 0.00085473 | 0.00085475 | 0.00085479 | 0.00085427 | 0.00085445 | 0.00085454 | 0.00085573 | 0.00085541 | 0.00085595 | 0.00085155 | 0.00085117 | 0.00085096 | 0.00085039 | 0.00084983 | 0.00084905 | 0.00085505 | 0.00085536 | 0.00085517 | 0.00083181 | 0.00083253 | 0.00083199 | 0.00083129 | 0.00083134 | 0.00083091 | 0.00081413 | 0.00081402 | 0.00081366 | 0.00080632 | 0.0008065 | 0.00080676 | 0.00080736 | 0.00080675 | 0.00083491 | 0.00083409 | 0.00083455 | 0.00081312 | 0.00081319 | 0.00081311 | 0.00081285 | 0.00081249 | 0.00081225 | 0.00081201 | 0.00081066 | 0.00081055 | 0.00081038 | 0.00080216 | 0.00080215 | 0.00080212 | 0.00080222 | 0.00084859 | 0.00084911 | 0.00084839 | 0.00084919 | 0.00084624 | 0.00084605 | 0.00084708 | 0.00084373 | 0.00084611 | 0.00084413 | 0.00085735 | 0.00085784 | 0.00085703 | 0.0008569 | 0.00085541 | 0.00085603 | 0.00085591 | 0.00085487 | 0.0008584 | 0.00085925 | 0.00085943 | 0.00085624 | 0.00085534 | 0.00085555 | 0.00085416 | 0.00085432 | 0.00085498 | 0.00085957 | 0.00085938 | 0.00085858 | 0.00081585 | 0.00081577 | 0.00081519 | 0.00086258 | 0.0008619 | 0.00086201 | 0.00085492 | 0.00085464 | 0.00085458 | 0.0008569 | 0.00085643 | 0.00085624 | 0.00085982 | 0.00085934 | 0.00085919 | 0.00081592 | 0.00081632 | 0.00081592 | 0.00082176 | 0.00082127 | 0.00082128 | 0.00082135 | 0.00082093 | 0.00082124 | 0.00081334 | 0.00081333 | 0.00081331 | 0.00081347 | 0.00081382 | 0.00081356 | 0.00084348 | 0.00084269 | 0.00084278 | 0.00084154 | 0.00084141 | 0.00084118 | 0.00086513 | 0.00086414 | 0.00086417 | 0.00085994 | 0.00085993 | 0.00085936 | 0.00085733 | 0.00085676 | 0.00085666 | 0.00086507 | 0.00086437 | 0.00086487 | 0.00081933 | 0.00081957 | 0.00081905 | 0.00086083 | 0.00086062 | 0.00086056 | 0.00086251 | 0.00086385 | 0.00086443
55 | Liquid line strainers sub cooling | ºC | 13.226 | 13.1988 | 13.4414 | 12.8016 | 12.8759 | 13.7315 | 13.9347 | 13.7776 | 13.6662 | 14.2642 | 14.0416 | 13.9975 | 14.5779 | 14.4795 | 14.4863 | 9.5943 | 9.6165 | 9.6286 | 9.6362 | 9.6833 | 9.621 | 9.5323 | 9.5474 | 9.5936 | 9.6435 | 9.6312 | 9.7461 | 11.4215 | 11.4636 | 11.4497 | 11.4278 | 11.4135 | 11.4108 | 11.7696 | 11.8502 | 11.5879 | 11.9277 | 11.8503 | 12.0678 | 12.0739 | 12.2006 | 12.2075 | 11.8028 | 11.9143 | 11.9355 | 12.1711 | 12.5192 | 12.4459 | 12.4509 | 13.3341 | 13.4093 | 13.2625 | 13.6946 | 14.6618 | 14.2355 | 14.1119 | 14.1434 | 14.1883 | 14.0571 | 14.0211 | 13.7703 | 10.9972 | 11.0787 | 10.9748 | 10.9012 | 11.064 | 11.1347 | 10.6318 | 10.7723 | 10.8929 | 10.7276 | 10.8343 | 10.9116 | 10.891 | 11.0197 | 11.0857 | 10.3143 | 10.3133 | 10.3541 | 10.0801 | 10.0927 | 10.1948 | 13.106 | 13.0846 | 12.9825 | 12.432 | 12.304 | 12.3168 | 12.4245 | 12.3037 | 12.4745 | 12.5629 | 12.5711 | 12.4746 | 12.8818 | 12.6716 | 12.8035 | 13.142 | 13.9023 | 13.8964 | 13.9478 | 13.9537 | 13.9418 | 14.0564 | 13.9867 | 13.9546 | 14.7416 | 14.7392 | 14.5175 | 15.0559 | 15.0435 | 15.0555 | 14.8104 | 14.8704 | 15.0062 | 14.9275 | 14.9084 | 14.9753 | 14.0556 | 13.8775 | 14.1415 | 14.3071 | 14.2834 | 14.4166 | 12.912 | 13.0421 | 13.1763 | 11.2845 | 11.2491 | 11.2473 | 11.198 | 11.1618 | 12.823 | 13.1355 | 12.9651 | 13.3688 | 13.3621 | 13.3741 | 13.6143 | 13.6333 | 13.7384 | 13.7915 | 14.2495 | 14.3068 | 14.4534 | 13.3732 | 13.4181 | 13.3515 | 13.2027 | 15.9334 | 15.9762 | 16.2653 | 15.9478 | 16.8179 | 16.8239 | 16.4589 | 17.0984 | 16.2978 | 16.9616 | 12.8785 | 12.7939 | 12.9518 | 13.0249 | 13.1036 | 13.0097 | 12.9372 | 13.0752 | 13.5301 | 13.3424 | 13.3283 | 13.175 | 13.3118 | 13.2939 | 13.1828 | 13.0447 | 12.9197 | 12.3745 | 12.2379 | 12.6099 | 12.385 | 12.4406 | 12.3925 | 12.498 | 12.6781 | 12.5995 | 13.1968 | 13.1464 | 13.1351 | 12.9231 | 13.0708 | 13.1785 | 12.1376 | 12.2622 | 12.286 | 12.265 | 12.1774 | 12.1772 | 9.9957 | 10.0273 | 10.1628 | 10.0555 | 10.0818 | 10.0179 | 8.3144 | 8.3935 | 8.3031 | 8.3857 | 8.1784 | 8.2092 | 9.83 | 9.9574 | 9.9074 | 10.3467 | 10.4487 | 10.3682 | 11.7108 | 11.9689 | 11.9586 | 12.1522 | 12.1351 | 12.2016 | 12.4234 | 12.4409 | 12.5095 | 10.7712 | 10.8418 | 10.606 | 10.6247 | 10.7796 | 10.7799 | 11.2294 | 11.3113 | 11.3041 | 11.2301 | 10.9628 | 10.8795
56 | Sub cooling loss cond - strainers | ºC
57 | Liquid line loss PD | BarA | 0.15681 | 0.17085 | 0.16693 | 0.15472 | 0.149 | 0.14796 | 0.1459 | 0.14239 | 0.13233 | 0.14043 | 0.12849 | 0.12071 | 0.12594 | 0.118 | 0.12426 | 0.007817 | 0.005605 | 0.022468 | 0.009098 | 0.000811 | 0.019161 | 0.011367 | 0.017386 | 0.016495 | 0.016563 | -0.004446 | -0.005032 | 0.050927 | 0.040173 | 0.050323 | 0.045893 | 0.047362 | 0.030396 | 0.040619 | 0.026214 | 0.026625 | 0.032469 | 0.032177 | 0.032973 | 0.028515 | 0.036933 | 0.028391 | 0.10401 | 0.099276 | 0.09239 | 0.094711 | 0.09135 | 0.098737 | 0.099602 | 0.12288 | 0.13843 | 0.13556 | 0.13608 | 0.14603 | 0.13236 | 0.13998 | 0.13871 | 0.12638 | 0.12709 | 0.14367 | 0.13129 | 0.088283 | 0.097509 | 0.097454 | 0.083853 | 0.10097 | 0.10152 | 0.035904 | 0.015258 | 0.028243 | 0.020639 | 0.016135 | 0.01067 | 0.014 | 0.026853 | 0.010852 | 0.00951 | 0.018822 | 0.005326 | 0.004168 | 0.028504 | 0.019279 | 0.022679 | 0.035257 | 0.041571 | 0.043523 | 0.042508 | 0.054926 | 0.040647 | 0.061808 | 0.032564 | 0.088407 | 0.10502 | 0.11156 | 0.089335 | 0.12389 | 0.10864 | 0.10077 | 0.1241 | 0.12725 | 0.12979 | 0.11707 | 0.11752 | 0.11784 | 0.1313 | 0.13823 | 0.1157 | 0.13627 | 0.13824 | 0.11226 | 0.12502 | 0.12793 | 0.13061 | 0.11928 | 0.14111 | 0.14367 | 0.13394 | 0.11993 | 0.10575 | 0.072277 | 0.084188 | 0.070531 | 0.094002 | 0.077969 | 0.028252 | 0.037386 | 0.025403 | 0.00156 | 0.017408 | 0.014081 | -0.006809 | 0.001169 | 0.11247 | 0.08746 | 0.11308 | 0.016776 | 0.026005 | 0.022977 | 0.01632 | 0.034122 | 0.02124 | 0.037033 | 0.02552 | 0.032156 | 0.018244 | 0.01102 | 0.019007 | 0.007138 | 0.015319 | 0.13679 | 0.11251 | 0.10975 | 0.10307 | 0.12968 | 0.12271 | 0.12586 | 0.13434 | 0.13712 | 0.12523 | 0.15861 | 0.14679 | 0.14484 | 0.16185 | 0.16747 | 0.15054 | 0.15839 | 0.14829 | 0.13663 | 0.14457 | 0.12734 | 0.1661 | 0.16065 | 0.17013 | 0.16121 | 0.14459 | 0.12731 | 0.1379 | 0.13655 | 0.12126 | 0.004718 | 0.005609 | 0.015493 | 0.14437 | 0.15078 | 0.1411 | 0.1414 | 0.15017 | 0.15471 | 0.1519 | 0.15746 | 0.13713 | 0.13882 | 0.13206 | 0.12606 | 0.02848 | 0.011346 | 0.006601 | 0.033436 | 0.028258 | 0.018741 | 0.02168 | 0.033835 | 0.023329 | 0.024049 | -0.013576 | 0.017576 | 0.017645 | 0.01299 | 0.012205 | 0.11396 | 0.10106 | 0.10747 | 0.11442 | 0.098026 | 0.11402 | 0.15719 | 0.1297 | 0.15364 | 0.13975 | 0.15295 | 0.14197 | 0.14397 | 0.13931 | 0.14017 | 0.14238 | 0.13186 | 0.13866 | 0.037021 | 0.037358 | 0.031128 | 0.14249 | 0.14229 | 0.1399 | 0.15943 | 0.15596 | 0.13434
58 | Liquid line solenoid valve open (circuit 1)
59 | Liquid line solenoid valve open (circuit 2)
60
61 | Note for temp / pressure between exp and flowmeter refer to ICAD / EKC
62
63 | Suction flow meter (High) Temp | ºC | 25.9109 | 25.8124 | 25.5781 | 22.197 | 21.9077 | 20.0413 | 17.0498 | 16.3563 | 15.7449 | 10.1125 | 10.8025 | 10.6209 | 7.7482 | 7.5782 | 7.4421 | 18.2387 | 18.3291 | 18.7295 | 18.6987 | 18.7376 | 18.7217 | 17.8876 | 18.2877 | 18.8424 | 18.653 | 18.6247 | 18.6285 | 16.3609 | 16.6406 | 16.8161 | 16.7337 | 16.6356 | 16.3679 | 17.5771 | 17.4449 | 17.233 | 15.6855 | 15.3842 | 15.039 | 15.4347 | 15.3707 | 16.0669 | 15.0017 | 15.0318 | 14.6919 | 14.6098 | 15.0736 | 14.9495 | 14.9655 | 13.6921 | 13.5696 | 13.4204 | 12.5787 | 11.3295 | 13.3369 | 14.0076 | 13.8764 | 13.8043 | 14.0072 | 15.156 | 16.3903 | 15.2297 | 15.3698 | 15.5567 | 17.6118 | 17.6091 | 17.5038 | 20.4014 | 20.3128 | 20.1394 | 19.1442 | 19.0634 | 18.8666 | 18.6152 | 18.4872 | 18.5596 | 17.037 | 16.9921 | 16.7394 | 19.1675 | 18.549 | 18.3818 | 17.5931 | 16.9054 | 16.7132 | 16.0549 | 16.0284 | 16.0511 | 16.2887 | 16.1463 | 16.0964 | 17.3012 | 17.1679 | 17.0034 | 16.7474 | 16.5928 | 16.3034 | 16.988 | 14.6452 | 14.6343 | 14.6348 | 14.6544 | 14.7171 | 14.7525 | 14.8143 | 15.3291 | 12.3966 | 12.7973 | 12.2684 | 14.9808 | 14.9493 | 14.7773 | 15.7954 | 15.5731 | 15.2555 | 11.3692 | 11.4864 | 11.5449 | 17.1477 | 16.8812 | 16.8236 | 17.2557 | 17.2695 | 17.263 | 17.9453 | 18.2663 | 18.7981 | 18.3316 | 18.467 | 18.6333 | 18.0898 | 17.93 | 15.3888 | 15.2316 | 14.376 | 16.9786 | 16.8976 | 16.7832 | 16.4797 | 16.7158 | 16.7295 | 16.7941 | 16.6939 | 16.6729 | 16.7389 | 17.1019 | 18.4491 | 18.8525 | 18.7704 | 13.8548 | 14.3446 | 14.6265 | 14.9816 | 13.5804 | 14.8653 | 15.1748 | 19.2237 | 20.0499 | 19.3508 | 15.5393 | 15.5293 | 15.1965 | 14.9407 | 15.1549 | 15.2405 | 15.1364 | 14.6628 | 12.468 | 12.9078 | 13.2549 | 14.0641 | 14.1239 | 14.8673 | 16.0009 | 16.1561 | 16.361 | 13.0496 | 14.5876 | 13.6658 | 17.8229 | 17.3381 | 17.6227 | 12.0038 | 11.7832 | 11.4284 | 14.2679 | 13.9934 | 13.5985 | 15.6402 | 14.9683 | 15.186 | 13.7282 | 13.9645 | 14.0237 | 16.7333 | 16.8359 | 16.6708 | 18.177 | 18.2612 | 19.2329 | 19.4394 | 19.0394 | 18.4852 | 17.5775 | 17.7874 | 18.1119 | 18.222 | 17.8873 | 17.7857 | 15.5527 | 15.514 | 15.4571 | 16.5659 | 16.4167 | 16.2779 | 13.2602 | 12.073 | 10.0483 | 13.7469 | 13.6043 | 13.481 | 13.5088 | 13.6009 | 13.1505 | 14.7542 | 16.5898 | 15.9957 | 18.983 | 18.7162 | 18.4693 | 15.8354 | 15.7533 | 15.8323 | 16.0615 | 16.3192 | 15.4266
64 | Suction flow meter (High) Pressure | BarA | 5.3465 | 5.3435 | 5.3306 | 4.5366 | 4.5336 | 4.5386 | 3.8009 | 3.8276 | 3.8271 | 3.1977 | 3.1955 | 3.1905 | 2.6482 | 2.6454 | 2.6426 | 3.8526 | 3.8548 | 3.8485 | 3.8596 | 3.8628 | 3.8606 | 3.8483 | 3.8481 | 3.8569 | 3.8537 | 3.858 | 3.8589 | 3.8278 | 3.8266 | 3.8305 | 3.841 | 3.8421 | 3.8385 | 3.8251 | 3.8366 | 3.8408 | 3.8319 | 3.8415 | 3.841 | 3.8509 | 3.838 | 3.8494 | 3.6973 | 3.6963 | 3.6891 | 3.701 | 3.7151 | 3.7253 | 3.7211 | 3.6289 | 3.6234 | 3.6389 | 3.3801 | 3.3824 | 3.3861 | 3.6875 | 3.6855 | 3.6878 | 3.6741 | 3.6806 | 3.6871 | 3.7034 | 3.6923 | 3.6945 | 3.7203 | 3.714 | 3.7085 | 3.838 | 3.8489 | 3.8445 | 3.8266 | 3.8474 | 3.8475 | 3.8504 | 3.8402 | 3.8378 | 3.8766 | 3.8707 | 3.8579 | 3.8729 | 3.8773 | 3.8707 | 3.8401 | 3.8472 | 3.8453 | 3.8317 | 3.8354 | 3.8423 | 3.8442 | 3.84 | 3.8494 | 3.7088 | 3.6999 | 3.6933 | 3.7075 | 3.7073 | 3.705 | 3.7095 | 3.6166 | 3.6173 | 3.6182 | 3.6183 | 3.6219 | 3.6229 | 3.6276 | 3.626 | 3.3766 | 3.3696 | 3.3647 | 3.6655 | 3.6717 | 3.6681 | 3.6711 | 3.6699 | 3.6726 | 3.3914 | 3.3951 | 3.3922 | 3.7038 | 3.7028 | 3.6968 | 3.706 | 3.7068 | 3.7008 | 3.8443 | 3.8449 | 3.846 | 3.8561 | 3.8584 | 3.8732 | 3.8782 | 3.8653 | 3.7247 | 3.7226 | 3.7296 | 3.8468 | 3.8505 | 3.847 | 3.8552 | 3.8521 | 3.8563 | 3.8524 | 3.6494 | 3.6417 | 3.6543 | 3.8501 | 3.8812 | 3.8781 | 3.8795 | 3.6076 | 3.6189 | 3.6282 | 3.6153 | 3.6727 | 3.6845 | 3.6905 | 3.6679 | 3.6665 | 3.6912 | 3.6817 | 3.6906 | 3.6771 | 3.6759 | 3.6839 | 3.6895 | 3.6808 | 3.686 | 3.4138 | 3.416 | 3.4132 | 3.7119 | 3.6981 | 3.705 | 3.7002 | 3.6967 | 3.6994 | 3.6569 | 3.6451 | 3.6564 | 3.8468 | 3.8471 | 3.833 | 3.4136 | 3.4147 | 3.4154 | 3.7124 | 3.7009 | 3.6995 | 3.6977 | 3.7083 | 3.7157 | 3.6591 | 3.6511 | 3.6491 | 3.8374 | 3.8464 | 3.8401 | 3.8424 | 3.8403 | 3.8358 | 3.8416 | 3.8331 | 3.8347 | 3.8566 | 3.8593 | 3.8737 | 3.8539 | 3.8544 | 3.8526 | 3.6984 | 3.7057 | 3.704 | 3.7281 | 3.7293 | 3.728 | 3.3997 | 3.3977 | 3.395 | 3.6944 | 3.6901 | 3.6801 | 3.6926 | 3.6883 | 3.6831 | 3.6604 | 3.6516 | 3.6532 | 3.8359 | 3.8301 | 3.8405 | 3.6934 | 3.6947 | 3.687 | 3.693 | 3.7021 | 3.6962
65 | Suction flow meter (High) gauge | ºC | 17.8502 | 17.8318 | 17.7553 | 12.7243 | 12.7043 | 12.7381 | 7.4239 | 7.6291 | 7.6256 | 2.4565 | 2.4371 | 2.3928 | -2.7411 | -2.7691 | -2.798 | 7.8209 | 7.8376 | 7.7898 | 7.8742 | 7.8985 | 7.8822 | 7.7882 | 7.7868 | 7.8538 | 7.8291 | 7.8618 | 7.8691 | 7.6312 | 7.6221 | 7.6517 | 7.7321 | 7.7408 | 7.7127 | 7.6103 | 7.6982 | 7.7304 | 7.6626 | 7.7359 | 7.7322 | 7.8077 | 7.7089 | 7.7967 | 6.6161 | 6.6082 | 6.5513 | 6.6451 | 6.7564 | 6.8359 | 6.8032 | 6.0731 | 6.0289 | 6.1525 | 4.029 | 4.049 | 4.0796 | 6.5385 | 6.5226 | 6.5407 | 6.4328 | 6.4843 | 6.5354 | 6.6636 | 6.5762 | 6.5942 | 6.7968 | 6.7472 | 6.704 | 7.7088 | 7.7926 | 7.7593 | 7.6219 | 7.7814 | 7.7816 | 7.8039 | 7.7263 | 7.7079 | 8.0041 | 7.9587 | 7.8612 | 7.9759 | 8.0093 | 7.9587 | 7.7253 | 7.7793 | 7.7649 | 7.6607 | 7.6889 | 7.7421 | 7.7566 | 7.7242 | 7.7963 | 6.7069 | 6.6365 | 6.5843 | 6.6961 | 6.695 | 6.6765 | 6.7118 | 5.9749 | 5.9801 | 5.9872 | 5.9885 | 6.0172 | 6.0248 | 6.0628 | 6.0495 | 3.9998 | 3.9406 | 3.8991 | 6.3647 | 6.4135 | 6.3853 | 6.4089 | 6.3994 | 6.4211 | 4.1247 | 4.1555 | 4.1317 | 6.667 | 6.659 | 6.6121 | 6.6848 | 6.6907 | 6.6434 | 7.7574 | 7.7621 | 7.7702 | 7.8475 | 7.8654 | 7.9779 | 8.016 | 7.9178 | 6.8313 | 6.8149 | 6.8697 | 7.7766 | 7.8049 | 7.7779 | 7.841 | 7.8167 | 7.8494 | 7.8194 | 6.2362 | 6.1754 | 6.2753 | 7.8018 | 8.0389 | 8.0153 | 8.0256 | 5.9023 | 5.9932 | 6.0674 | 5.9644 | 6.4217 | 6.5147 | 6.5627 | 6.3833 | 6.3724 | 6.5675 | 6.4931 | 6.5634 | 6.4562 | 6.4467 | 6.5106 | 6.5547 | 6.4858 | 6.5269 | 4.3131 | 4.3313 | 4.3074 | 6.7307 | 6.6221 | 6.6766 | 6.6388 | 6.6114 | 6.6326 | 6.2966 | 6.2021 | 6.2919 | 7.7766 | 7.7789 | 7.6709 | 4.3114 | 4.3199 | 4.3263 | 6.7351 | 6.6444 | 6.6333 | 6.6192 | 6.7026 | 6.7604 | 6.3137 | 6.2503 | 6.2342 | 7.7049 | 7.7738 | 7.7254 | 7.7431 | 7.7265 | 7.6923 | 7.7364 | 7.6713 | 7.6836 | 7.8512 | 7.8719 | 7.9818 | 7.8309 | 7.835 | 7.821 | 6.6249 | 6.6822 | 6.6689 | 6.8582 | 6.8673 | 6.8572 | 4.1944 | 4.178 | 4.1547 | 6.5929 | 6.5595 | 6.48 | 6.5789 | 6.5447 | 6.5038 | 6.3239 | 6.254 | 6.2665 | 7.6932 | 7.649 | 7.7286 | 6.5856 | 6.5953 | 6.5344 | 6.5821 | 6.6538 | 6.6074
66 | Suction flow meter (low) SH | ºC | 8.0607 | 7.9807 | 7.8228 | 9.4727 | 9.2035 | 7.3032 | 9.6259 | 8.7271 | 8.1193 | 7.6559 | 8.3654 | 8.2281 | 10.4893 | 10.3473 | 10.2401 | 10.4178 | 10.4916 | 10.9397 | 10.8245 | 10.8391 | 10.8395 | 10.0994 | 10.5009 | 10.9887 | 10.8239 | 10.7629 | 10.7594 | 8.7297 | 9.0186 | 9.1645 | 9.0016 | 8.8948 | 8.6552 | 9.9667 | 9.7467 | 9.5027 | 8.0229 | 7.6483 | 7.3068 | 7.627 | 7.6618 | 8.2702 | 8.3856 | 8.4236 | 8.1405 | 7.9647 | 8.3172 | 8.1136 | 8.1623 | 7.619 | 7.5407 | 7.2679 | 8.5497 | 7.2805 | 9.2572 | 7.4691 | 7.3538 | 7.2636 | 7.5744 | 8.6717 | 9.8549 | 8.5661 | 8.7936 | 8.9626 | 10.815 | 10.8619 | 10.7999 | 12.6926 | 12.5202 | 12.3801 | 11.5223 | 11.282 | 11.085 | 10.8112 | 10.7609 | 10.8517 | 9.0329 | 9.0334 | 8.8782 | 11.1915 | 10.5397 | 10.4231 | 9.8678 | 9.1261 | 8.9483 | 8.3943 | 8.3396 | 8.309 | 8.5321 | 8.4221 | 8.3002 | 10.5943 | 10.5315 | 10.4191 | 10.0513 | 9.8978 | 9.6269 | 10.2762 | 8.6703 | 8.6542 | 8.6475 | 8.6659 | 8.6999 | 8.7277 | 8.7515 | 9.2796 | 8.3967 | 8.8567 | 8.3693 | 8.6161 | 8.5358 | 8.392 | 9.3865 | 9.1737 | 8.8344 | 7.2446 | 7.3309 | 7.4132 | 10.4807 | 10.2223 | 10.2115 | 10.5709 | 10.5788 | 10.6197 | 10.188 | 10.5042 | 11.028 | 10.4841 | 10.6016 | 10.6553 | 10.0738 | 10.0122 | 8.5575 | 8.4166 | 7.5063 | 9.2021 | 9.0927 | 9.0053 | 8.6387 | 8.8991 | 8.8801 | 8.9747 | 10.4577 | 10.4975 | 10.4636 | 9.3001 | 10.4102 | 10.8372 | 10.7448 | 7.9525 | 8.3514 | 8.5591 | 9.0172 | 7.1587 | 8.3505 | 8.6121 | 12.8404 | 13.6775 | 12.7833 | 9.0462 | 8.9659 | 8.7403 | 8.494 | 8.6443 | 8.6858 | 8.6506 | 8.1359 | 8.1549 | 8.5765 | 8.9475 | 7.3334 | 7.5018 | 8.1907 | 9.3621 | 9.5447 | 9.7284 | 6.753 | 8.3855 | 7.3739 | 10.0463 | 9.5592 | 9.9518 | 7.6925 | 7.4632 | 7.1021 | 7.5329 | 7.349 | 6.9652 | 9.021 | 8.2657 | 8.4255 | 7.4146 | 7.7142 | 7.7896 | 9.0284 | 9.0621 | 8.9454 | 10.4339 | 10.5347 | 11.5406 | 11.703 | 11.3681 | 10.8017 | 9.7264 | 9.9155 | 10.1301 | 10.3911 | 10.0523 | 9.9647 | 8.9278 | 8.8318 | 8.7882 | 9.7077 | 9.5494 | 9.4206 | 9.0658 | 7.895 | 5.8936 | 7.154 | 7.0448 | 7.001 | 6.93 | 7.0563 | 6.6468 | 8.4303 | 10.3358 | 9.7291 | 11.2898 | 11.0672 | 10.7407 | 9.2498 | 9.158 | 9.2979 | 9.4794 | 9.6654 | 8.8192
67 | suction flow meter (high) Low SH warning |  | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok
68 | Suction flow meter (High) enthalpy | KJ/kg | 416.4735 | 416.3856 | 416.189 | 414.8129 | 414.5477 | 412.7776 | 411.7599 | 411.0591 | 410.4982 | 406.9401 | 407.5654 | 407.4149 | 406.2232 | 406.081 | 405.9688 | 412.7293 | 412.8072 | 413.1895 | 413.1355 | 413.1638 | 413.1542 | 412.4167 | 412.7848 | 413.2737 | 413.1073 | 413.0713 | 413.0726 | 411.0627 | 411.3227 | 411.4747 | 411.3738 | 411.2808 | 411.0435 | 412.1864 | 412.0379 | 411.8332 | 410.4318 | 410.1311 | 409.8145 | 410.1546 | 410.1273 | 410.74 | 410.1328 | 410.1628 | 409.8693 | 409.7651 | 410.1551 | 410.0166 | 410.0415 | 409.1036 | 409.0054 | 408.8306 | 408.7073 | 407.5711 | 409.378 | 409.247 | 409.1318 | 409.0601 | 409.2797 | 410.3145 | 411.4271 | 410.3268 | 410.4818 | 410.6473 | 412.4651 | 412.4774 | 412.3941 | 414.7479 | 414.6418 | 414.4926 | 413.6209 | 413.4986 | 413.3179 | 413.0802 | 412.9864 | 413.0584 | 411.5673 | 411.5403 | 411.3384 | 413.5351 | 412.9565 | 412.8184 | 412.1657 | 411.5168 | 411.3446 | 410.7722 | 410.7389 | 410.7428 | 410.9569 | 410.8361 | 410.7674 | 412.208 | 412.1073 | 411.9726 | 411.705 | 411.564 | 411.305 | 411.9202 | 410.0037 | 409.9922 | 409.9905 | 410.008 | 410.0565 | 410.0864 | 410.1313 | 410.6049 | 408.5511 | 408.9306 | 408.4647 | 410.1912 | 410.1474 | 409.9988 | 410.9219 | 410.7217 | 410.4249 | 407.5845 | 407.6813 | 407.7415 | 412.0797 | 411.8385 | 411.8 | 412.173 | 412.1839 | 412.1921 | 412.4793 | 412.7726 | 413.2585 | 412.8064 | 412.9253 | 413.0436 | 412.5322 | 412.4157 | 410.4205 | 410.2816 | 409.4803 | 411.585 | 411.5016 | 411.4049 | 411.1059 | 411.3308 | 411.333 | 411.4019 | 411.7939 | 411.7928 | 411.8234 | 411.6905 | 412.8555 | 413.2337 | 413.155 | 409.3048 | 409.7239 | 409.9585 | 410.3137 | 408.8926 | 410.0393 | 410.3076 | 414.0577 | 414.8139 | 414.1205 | 410.6623 | 410.6317 | 410.3602 | 410.1293 | 410.3055 | 410.3702 | 410.2961 | 409.8503 | 408.5234 | 408.9163 | 409.2376 | 409.2383 | 409.3273 | 409.991 | 411.0398 | 411.1901 | 411.371 | 408.4461 | 409.8818 | 409.0114 | 412.3609 | 411.9147 | 412.2096 | 408.1035 | 407.901 | 407.5775 | 409.4237 | 409.2007 | 408.8423 | 410.7159 | 410.0754 | 410.2567 | 409.0617 | 409.2975 | 409.3567 | 411.3819 | 411.4547 | 411.318 | 412.6964 | 412.7789 | 413.6811 | 413.8572 | 413.5098 | 412.9976 | 412.1123 | 412.2988 | 412.5631 | 412.7108 | 412.402 | 412.313 | 410.6342 | 410.5812 | 410.5332 | 411.4899 | 411.3506 | 411.2265 | 409.2754 | 408.2058 | 406.3782 | 408.9911 | 408.871 | 408.7832 | 408.7774 | 408.8726 | 408.4729 | 409.9965 | 411.6936 | 411.1478 | 413.4515 | 413.22 | 412.9693 | 410.9047 | 410.8267 | 410.9175 | 411.1125 | 411.3263 | 410.5242
69 | Suction flow meter (High) specific Vol | m3/kg | 0.040239 | 0.040245 | 0.040306 | 0.0476 | 0.047566 | 0.047056 | 0.056559 | 0.05593 | 0.055768 | 0.066176 | 0.066449 | 0.066506 | 0.08037 | 0.080396 | 0.080439 | 0.056041 | 0.05603 | 0.05624 | 0.056053 | 0.056013 | 0.056043 | 0.056014 | 0.056126 | 0.056136 | 0.056136 | 0.056059 | 0.056045 | 0.055926 | 0.056023 | 0.056009 | 0.055816 | 0.05577 | 0.055756 | 0.056306 | 0.056083 | 0.055957 | 0.055673 | 0.055435 | 0.055347 | 0.055298 | 0.055488 | 0.055496 | 0.057737 | 0.057763 | 0.057791 | 0.057561 | 0.057449 | 0.05724 | 0.057316 | 0.058566 | 0.058629 | 0.058309 | 0.063009 | 0.062576 | 0.063118 | 0.057623 | 0.05762 | 0.05756 | 0.057856 | 0.058072 | 0.05831 | 0.057697 | 0.057929 | 0.057943 | 0.058077 | 0.058185 | 0.058251 | 0.056867 | 0.056664 | 0.056688 | 0.056711 | 0.056349 | 0.056295 | 0.056179 | 0.056309 | 0.056368 | 0.055328 | 0.05541 | 0.055546 | 0.055966 | 0.055728 | 0.055789 | 0.056066 | 0.055763 | 0.055741 | 0.055779 | 0.055713 | 0.055606 | 0.055641 | 0.055671 | 0.055505 | 0.058188 | 0.058306 | 0.058375 | 0.058056 | 0.058014 | 0.057973 | 0.058089 | 0.059063 | 0.059048 | 0.059032 | 0.059035 | 0.058989 | 0.058982 | 0.058914 | 0.059092 | 0.063024 | 0.063292 | 0.06323 | 0.058287 | 0.058169 | 0.058182 | 0.058421 | 0.058379 | 0.05824 | 0.062405 | 0.062367 | 0.062442 | 0.058232 | 0.058175 | 0.058262 | 0.058224 | 0.058215 | 0.058317 | 0.056095 | 0.056173 | 0.056301 | 0.05601 | 0.056009 | 0.055817 | 0.055589 | 0.055752 | 0.057375 | 0.057366 | 0.057004 | 0.055789 | 0.055707 | 0.055733 | 0.055517 | 0.055633 | 0.055568 | 0.055648 | 0.059064 | 0.059195 | 0.058989 | 0.05577 | 0.055639 | 0.055798 | 0.055754 | 0.058997 | 0.058935 | 0.058849 | 0.059184 | 0.057758 | 0.057921 | 0.057904 | 0.05945 | 0.059706 | 0.059072 | 0.058161 | 0.058003 | 0.058145 | 0.058093 | 0.058013 | 0.05794 | 0.058063 | 0.057836 | 0.062288 | 0.062378 | 0.062541 | 0.057218 | 0.057473 | 0.057565 | 0.057971 | 0.058075 | 0.058086 | 0.057881 | 0.058536 | 0.05807 | 0.056021 | 0.055883 | 0.05619 | 0.06215 | 0.062062 | 0.061938 | 0.057267 | 0.057386 | 0.057298 | 0.057911 | 0.057537 | 0.057472 | 0.058039 | 0.058249 | 0.058302 | 0.055873 | 0.055756 | 0.055813 | 0.056189 | 0.056247 | 0.056585 | 0.056547 | 0.056577 | 0.056399 | 0.055796 | 0.05581 | 0.055667 | 0.056015 | 0.055915 | 0.055917 | 0.057874 | 0.057737 | 0.05775 | 0.057648 | 0.057586 | 0.057569 | 0.062816 | 0.062493 | 0.061925 | 0.057429 | 0.057461 | 0.0576 | 0.057391 | 0.057493 | 0.057453 | 0.058312 | 0.058994 | 0.058796 | 0.056515 | 0.056536 | 0.056299 | 0.058041 | 0.057996 | 0.058153 | 0.058113 | 0.058028 | 0.057877
70 | Suction flow meter (High) vol Flow | m^3/hr | 1151.4805 | 1152.8279 | 1152.0968 | 1151.4604 | 1154.0277 | 1147.5392 | 1142.2198 | 1144.5347 | 1143.7614 | 1127.7631 | 1131.9011 | 1133.7521 | 1125.7011 | 1125.3593 | 1124.7775 | 170.4691 | 170.7793 | 173.1454 | 185.5478 | 185.3106 | 182.0024 | 173.6105 | 179.6716 | 175.2181 | 186.2916 | 190.8848 | 189.2306 | 405.5737 | 406.1605 | 406.501 | 405.8454 | 405.5364 | 404.5136 | 438.866 | 437.9952 | 440.3912 | 441.9586 | 439.6614 | 437.6309 | 460.2157 | 459.3186 | 458.4065 | 709.7458 | 708.8906 | 708.9545 | 721.6864 | 763.8997 | 761.9131 | 763.2113 | 1069.3069 | 1070.9042 | 1068.5406 | 1140.6536 | 1137.8028 | 1140.7737 | 1141.7769 | 1138.8727 | 1136.4648 | 1139.9488 | 1141.6015 | 1143.08 | 708.5533 | 708.239 | 708.9824 | 753.3499 | 754.6669 | 753.9793 | 459.6092 | 459.1117 | 458.4765 | 402.5823 | 402.5339 | 405.1102 | 404.9291 | 403.8661 | 404.6599 | 179.8175 | 180.006 | 180.6444 | 192.8903 | 193.2239 | 196.0088 | 402.7638 | 402.2725 | 402.9232 | 432.2026 | 432.5648 | 432.9053 | 431.5543 | 433.2524 | 432.0915 | 717.0727 | 716.8703 | 717.2743 | 752.582 | 752.1472 | 750.0536 | 744.4851 | 1058.93 | 1061.3358 | 1060.2397 | 1059.7164 | 1057.6105 | 1057.1208 | 1059.3345 | 1060.6859 | 1120.7046 | 1122.7851 | 1125.4913 | 1126.2432 | 1125.8052 | 1122.9724 | 1128.7409 | 1127.6508 | 1125.5224 | 1094.5429 | 1094.4888 | 1094.2393 | 682.6334 | 679.5682 | 680.3845 | 695.7665 | 697.6081 | 696.4332 | 389.4074 | 389.6914 | 388.8562 | 163.5925 | 166.9995 | 155.5166 | 179.5908 | 180.9583 | 735.1244 | 734.6323 | 734.4339 | 421.724 | 421.0643 | 422.7079 | 422.476 | 444.7665 | 446.4117 | 445.5893 | 444.5517 | 445.6618 | 445.5565 | 175.3381 | 180.2559 | 176.42 | 182.0249 | 1032.9634 | 1033.6461 | 1034.0407 | 1036.3232 | 1100.9827 | 1103.1869 | 1101.1818 | 1107.5314 | 1112.7848 | 1109.5549 | 1106.4373 | 1107.5957 | 1107.953 | 1106.9884 | 1107.5945 | 1107.8572 | 1108.7734 | 1107.5527 | 1138.231 | 1138.4527 | 1142.0461 | 1141.9203 | 1141.2077 | 1141.1278 | 1145.9468 | 1145.4018 | 1146.4713 | 1066.1123 | 1071.2948 | 1069.3823 | 457.3374 | 457.0021 | 458.2307 | 1135.4609 | 1134.0225 | 1134.7348 | 1144.781 | 1140.8975 | 1140.9929 | 1147.2442 | 1141.9289 | 1147.5331 | 1068.0927 | 1069.1057 | 1069.6966 | 458.1127 | 459.1281 | 460.5906 | 432.0657 | 432.1927 | 432.6537 | 402.8876 | 402.368 | 402.4024 | 165.5452 | 166.7393 | 175.6701 | 189.3809 | 185.1499 | 186.6649 | 721.4893 | 722.4118 | 722.2458 | 763.2945 | 764.0845 | 765.0877 | 1133.5116 | 1132.8965 | 1126.0625 | 1134.0115 | 1136.7857 | 1137.393 | 1134.7679 | 1137.4385 | 1134.6126 | 1063.7015 | 1072.4233 | 1068.1636 | 455.8056 | 454.8754 | 455.8404 | 1141.5298 | 1139.8152 | 1139.1977 | 1141.3384 | 1142.9751 | 1143.4111
71 | Suction flow meter (High) mass Flow | kg/s | 7.9489 | 7.9571 | 7.9399 | 6.7195 | 6.7394 | 6.7741 | 5.6098 | 5.6844 | 5.697 | 4.7338 | 4.7317 | 4.7354 | 3.8907 | 3.8882 | 3.8842 | 0.84497 | 0.84666 | 0.85519 | 0.9195 | 0.91899 | 0.9021 | 0.86095 | 0.88922 | 0.86704 | 0.92182 | 0.94585 | 0.93789 | 2.0144 | 2.0139 | 2.0161 | 2.0198 | 2.0199 | 2.0153 | 2.1651 | 2.1694 | 2.1862 | 2.2051 | 2.2031 | 2.1964 | 2.3118 | 2.2994 | 2.2945 | 3.4147 | 3.409 | 3.4077 | 3.4827 | 3.6936 | 3.6974 | 3.6988 | 5.0717 | 5.0738 | 5.0904 | 5.0286 | 5.0508 | 5.0205 | 5.5041 | 5.4903 | 5.4845 | 5.4731 | 5.4607 | 5.4454 | 3.4113 | 3.3961 | 3.3989 | 3.6032 | 3.6028 | 3.5954 | 2.245 | 2.2506 | 2.2466 | 1.9719 | 1.9843 | 1.9989 | 2.0022 | 1.9923 | 1.9941 | 0.90279 | 0.90239 | 0.90339 | 0.95738 | 0.96313 | 0.97594 | 1.9955 | 2.0039 | 2.0079 | 2.1523 | 2.1567 | 2.1625 | 2.1544 | 2.1618 | 2.1624 | 3.4232 | 3.4153 | 3.4132 | 3.6009 | 3.6014 | 3.5939 | 3.5601 | 4.9802 | 4.9928 | 4.989 | 4.9863 | 4.9803 | 4.9786 | 4.9947 | 4.986 | 4.9395 | 4.9277 | 4.9444 | 5.3674 | 5.3761 | 5.3614 | 5.3669 | 5.3656 | 5.3682 | 4.872 | 4.8748 | 4.8678 | 3.2563 | 3.2448 | 3.2439 | 3.3194 | 3.3287 | 3.3173 | 1.9283 | 1.927 | 1.9185 | 0.81133 | 0.82824 | 0.77394 | 0.89741 | 0.9016 | 3.5591 | 3.5572 | 3.5789 | 2.0998 | 2.0996 | 2.1068 | 2.1139 | 2.2208 | 2.2316 | 2.2242 | 2.0907 | 2.0913 | 2.0981 | 0.87332 | 0.89993 | 0.87827 | 0.90689 | 4.8635 | 4.8719 | 4.8808 | 4.8639 | 5.295 | 5.2907 | 5.2826 | 5.1749 | 5.1771 | 5.2175 | 5.2843 | 5.3043 | 5.293 | 5.2932 | 5.3034 | 5.3113 | 5.3045 | 5.3194 | 5.076 | 5.0697 | 5.0724 | 5.5437 | 5.5157 | 5.5064 | 5.491 | 5.4786 | 5.4826 | 5.1164 | 5.0837 | 5.1154 | 2.2677 | 2.2716 | 2.2653 | 5.0749 | 5.0757 | 5.089 | 5.5529 | 5.5225 | 5.5315 | 5.5029 | 5.513 | 5.5463 | 5.1119 | 5.0984 | 5.0966 | 2.2775 | 2.2874 | 2.2923 | 2.136 | 2.1344 | 2.1239 | 1.9791 | 1.9755 | 1.9819 | 0.82416 | 0.8299 | 0.87659 | 0.93914 | 0.9198 | 0.92729 | 3.4629 | 3.4756 | 3.474 | 3.6779 | 3.6857 | 3.6916 | 5.0125 | 5.0357 | 5.0512 | 5.4851 | 5.4954 | 5.4851 | 5.4924 | 5.4956 | 5.4857 | 5.0671 | 5.0496 | 5.0464 | 2.2403 | 2.2349 | 2.2491 | 5.4632 | 5.4592 | 5.4415 | 5.4556 | 5.4714 | 5.4878
72
73 | Suction flow meter (low) Temp | ºC | 25.0695 | 25.0279 | 24.9531 | 24.3264 | 24.2797 | 24.1316 | 23.5377 | 23.4213 | 23.34 | 22.6807 | 22.5876 | 22.4853 | 21.5998 | 21.5538 | 21.5159 | 18.1515 | 18.121 | 18.0538 | 17.8513 | 17.8207 | 17.7615 | 18.7782 | 18.7339 | 18.6613 | 18.6012 | 18.5539 | 18.513 | 22.4896 | 22.5012 | 22.508 | 22.519 | 22.5241 | 22.5216 | 22.4928 | 22.4989 | 22.4822 | 22.556 | 22.5896 | 22.6653 | 22.7679 | 22.7808 | 22.8072 | 22.9038 | 22.8948 | 22.8896 | 22.9012 | 22.933 | 22.9577 | 22.9945 | 23.3475 | 23.2942 | 23.148 | 22.3854 | 22.2278 | 21.8496 | 21 | 20.8452 | 20.6619 | 20.0258 | 19.6257 | 19.3737 | 23.5147 | 23.4328 | 23.3883 | 22.9184 | 22.8296 | 22.7641 | 21.2502 | 21.2102 | 21.1259 | 20.913 | 20.8716 | 20.7969 | 20.6793 | 20.5983 | 20.5379 | 19.7559 | 19.7553 | 19.741 | 18.9023 | 18.6581 | 18.3921 | 22.3693 | 22.388 | 22.3845 | 22.4817 | 22.5132 | 22.542 | 22.6549 | 22.6767 | 22.7055 | 23.3211 | 23.3074 | 23.2991 | 23.2309 | 23.2364 | 23.2459 | 23.7533 | 23.7272 | 23.714 | 23.6977 | 23.5702 | 23.5569 | 23.5119 | 23.4423 | 23.2982 | 22.3945 | 22.3239 | 22.2083 | 21.0039 | 20.8648 | 20.7187 | 20.3358 | 20.0463 | 19.8197 | 23.4144 | 23.3217 | 23.2528 | 21.6434 | 21.6334 | 21.607 | 21.4336 | 21.4112 | 21.3888 | 20.0598 | 20.0167 | 19.9864 | 17.9231 | 17.8527 | 17.7983 | 17.5471 | 17.4421 | 22.4259 | 22.3736 | 22.3127 | 20.8064 | 20.7962 | 20.7794 | 20.5932 | 20.5328 | 20.5193 | 20.5045 | 19.9872 | 19.9415 | 19.9055 | 18.7521 | 18.6795 | 18.665 | 18.6497 | 26.1837 | 26.1401 | 26.1129 | 26.0928 | 25.9967 | 25.9339 | 25.9055 | 25.1433 | 24.9805 | 24.3988 | 25.1837 | 25.1726 | 25.0833 | 25.0247 | 24.8882 | 24.7915 | 24.7017 | 24.6017 | 23.3242 | 23.2553 | 23.1951 | 22.7517 | 22.6698 | 22.5846 | 22.4558 | 22.354 | 22.258 | 21.7372 | 21.5049 | 21.3427 | 18.9132 | 18.8514 | 18.7742 | 23.0502 | 22.933 | 22.8201 | 22.2498 | 22.1316 | 22.046 | 21.4822 | 21.3977 | 21.3175 | 21.0842 | 20.9579 | 20.8466 | 17.4399 | 17.384 | 17.2631 | 19.094 | 19.0085 | 18.8638 | 17.8161 | 17.6353 | 17.4635 | 19.5179 | 19.4865 | 19.4576 | 19.451 | 19.392 | 19.3776 | 21.1707 | 21.1609 | 21.1385 | 20.7782 | 20.7431 | 20.7168 | 22.9411 | 22.7288 | 22.594 | 22.2581 | 22.1752 | 22.0486 | 21.7812 | 21.6279 | 21.4427 | 22.0095 | 21.928 | 21.811 | 19.1893 | 19.053 | 18.9404 | 23.1801 | 23.0555 | 22.9106 | 22.49 | 22.3149 | 22.1282
74 | Suction flow meter (low) Pressure | BarA | 5.3465 | 5.3435 | 5.3306 | 4.5366 | 4.5336 | 4.5386 | 3.8009 | 3.8276 | 3.8271 | 3.1977 | 3.1955 | 3.1905 | 2.6482 | 2.6454 | 2.6426 | 3.8526 | 3.8548 | 3.8485 | 3.8596 | 3.8628 | 3.8606 | 3.8483 | 3.8481 | 3.8569 | 3.8537 | 3.858 | 3.8589 | 3.8278 | 3.8266 | 3.8305 | 3.841 | 3.8421 | 3.8385 | 3.8251 | 3.8366 | 3.8408 | 3.8319 | 3.8415 | 3.841 | 3.8509 | 3.838 | 3.8494 | 3.6973 | 3.6963 | 3.6891 | 3.701 | 3.7151 | 3.7253 | 3.7211 | 3.6289 | 3.6234 | 3.6389 | 3.3801 | 3.3824 | 3.3861 | 3.6875 | 3.6855 | 3.6878 | 3.6741 | 3.6806 | 3.6871 | 3.7034 | 3.6923 | 3.6945 | 3.7203 | 3.714 | 3.7085 | 3.838 | 3.8489 | 3.8445 | 3.8266 | 3.8474 | 3.8475 | 3.8504 | 3.8402 | 3.8378 | 3.8766 | 3.8707 | 3.8579 | 3.8729 | 3.8773 | 3.8707 | 3.8401 | 3.8472 | 3.8453 | 3.8317 | 3.8354 | 3.8423 | 3.8442 | 3.84 | 3.8494 | 3.7088 | 3.6999 | 3.6933 | 3.7075 | 3.7073 | 3.705 | 3.7095 | 3.6166 | 3.6173 | 3.6182 | 3.6183 | 3.6219 | 3.6229 | 3.6276 | 3.626 | 3.3766 | 3.3696 | 3.3647 | 3.6655 | 3.6717 | 3.6681 | 3.6711 | 3.6699 | 3.6726 | 3.3914 | 3.3951 | 3.3922 | 3.7038 | 3.7028 | 3.6968 | 3.706 | 3.7068 | 3.7008 | 3.8443 | 3.8449 | 3.846 | 3.8561 | 3.8584 | 3.8732 | 3.8782 | 3.8653 | 3.7247 | 3.7226 | 3.7296 | 3.8468 | 3.8505 | 3.847 | 3.8552 | 3.8521 | 3.8563 | 3.8524 | 3.6494 | 3.6417 | 3.6543 | 3.8501 | 3.8812 | 3.8781 | 3.8795 | 3.6076 | 3.6189 | 3.6282 | 3.6153 | 3.6727 | 3.6845 | 3.6905 | 3.6679 | 3.6665 | 3.6912 | 3.6817 | 3.6906 | 3.6771 | 3.6759 | 3.6839 | 3.6895 | 3.6808 | 3.686 | 3.4138 | 3.416 | 3.4132 | 3.7119 | 3.6981 | 3.705 | 3.7002 | 3.6967 | 3.6994 | 3.6569 | 3.6451 | 3.6564 | 3.8468 | 3.8471 | 3.833 | 3.4136 | 3.4147 | 3.4154 | 3.7124 | 3.7009 | 3.6995 | 3.6977 | 3.7083 | 3.7157 | 3.6591 | 3.6511 | 3.6491 | 3.8374 | 3.8464 | 3.8401 | 3.8424 | 3.8403 | 3.8358 | 3.8416 | 3.8331 | 3.8347 | 3.8566 | 3.8593 | 3.8737 | 3.8539 | 3.8544 | 3.8526 | 3.6984 | 3.7057 | 3.704 | 3.7281 | 3.7293 | 3.728 | 3.3997 | 3.3977 | 3.395 | 3.6944 | 3.6901 | 3.6801 | 3.6926 | 3.6883 | 3.6831 | 3.6604 | 3.6516 | 3.6532 | 3.8359 | 3.8301 | 3.8405 | 3.6934 | 3.6947 | 3.687 | 3.693 | 3.7021 | 3.6962
75 | Suction flow meter (low) gauge | ºC | 17.8502 | 17.8318 | 17.7553 | 12.7243 | 12.7043 | 12.7381 | 7.4239 | 7.6291 | 7.6256 | 2.4565 | 2.4371 | 2.3928 | -2.7411 | -2.7691 | -2.798 | 7.8209 | 7.8376 | 7.7898 | 7.8742 | 7.8985 | 7.8822 | 7.7882 | 7.7868 | 7.8538 | 7.8291 | 7.8618 | 7.8691 | 7.6312 | 7.6221 | 7.6517 | 7.7321 | 7.7408 | 7.7127 | 7.6103 | 7.6982 | 7.7304 | 7.6626 | 7.7359 | 7.7322 | 7.8077 | 7.7089 | 7.7967 | 6.6161 | 6.6082 | 6.5513 | 6.6451 | 6.7564 | 6.8359 | 6.8032 | 6.0731 | 6.0289 | 6.1525 | 4.029 | 4.049 | 4.0796 | 6.5385 | 6.5226 | 6.5407 | 6.4328 | 6.4843 | 6.5354 | 6.6636 | 6.5762 | 6.5942 | 6.7968 | 6.7472 | 6.704 | 7.7088 | 7.7926 | 7.7593 | 7.6219 | 7.7814 | 7.7816 | 7.8039 | 7.7263 | 7.7079 | 8.0041 | 7.9587 | 7.8612 | 7.9759 | 8.0093 | 7.9587 | 7.7253 | 7.7793 | 7.7649 | 7.6607 | 7.6889 | 7.7421 | 7.7566 | 7.7242 | 7.7963 | 6.7069 | 6.6365 | 6.5843 | 6.6961 | 6.695 | 6.6765 | 6.7118 | 5.9749 | 5.9801 | 5.9872 | 5.9885 | 6.0172 | 6.0248 | 6.0628 | 6.0495 | 3.9998 | 3.9406 | 3.8991 | 6.3647 | 6.4135 | 6.3853 | 6.4089 | 6.3994 | 6.4211 | 4.1247 | 4.1555 | 4.1317 | 6.667 | 6.659 | 6.6121 | 6.6848 | 6.6907 | 6.6434 | 7.7574 | 7.7621 | 7.7702 | 7.8475 | 7.8654 | 7.9779 | 8.016 | 7.9178 | 6.8313 | 6.8149 | 6.8697 | 7.7766 | 7.8049 | 7.7779 | 7.841 | 7.8167 | 7.8494 | 7.8194 | 6.2362 | 6.1754 | 6.2753 | 7.8018 | 8.0389 | 8.0153 | 8.0256 | 5.9023 | 5.9932 | 6.0674 | 5.9644 | 6.4217 | 6.5147 | 6.5627 | 6.3833 | 6.3724 | 6.5675 | 6.4931 | 6.5634 | 6.4562 | 6.4467 | 6.5106 | 6.5547 | 6.4858 | 6.5269 | 4.3131 | 4.3313 | 4.3074 | 6.7307 | 6.6221 | 6.6766 | 6.6388 | 6.6114 | 6.6326 | 6.2966 | 6.2021 | 6.2919 | 7.7766 | 7.7789 | 7.6709 | 4.3114 | 4.3199 | 4.3263 | 6.7351 | 6.6444 | 6.6333 | 6.6192 | 6.7026 | 6.7604 | 6.3137 | 6.2503 | 6.2342 | 7.7049 | 7.7738 | 7.7254 | 7.7431 | 7.7265 | 7.6923 | 7.7364 | 7.6713 | 7.6836 | 7.8512 | 7.8719 | 7.9818 | 7.8309 | 7.835 | 7.821 | 6.6249 | 6.6822 | 6.6689 | 6.8582 | 6.8673 | 6.8572 | 4.1944 | 4.178 | 4.1547 | 6.5929 | 6.5595 | 6.48 | 6.5789 | 6.5447 | 6.5038 | 6.3239 | 6.254 | 6.2665 | 7.6932 | 7.649 | 7.7286 | 6.5856 | 6.5953 | 6.5344 | 6.5821 | 6.6538 | 6.6074
76 | Suction flow meter (low) SH | ºC | 7.2193 | 7.1961 | 7.1978 | 11.6021 | 11.5755 | 11.3936 | 16.1138 | 15.7921 | 15.7144 | 20.2241 | 20.1505 | 20.0925 | 24.3409 | 24.3229 | 24.3139 | 10.3306 | 10.2835 | 10.2639 | 9.9771 | 9.9221 | 9.8794 | 10.99 | 10.9471 | 10.8075 | 10.7721 | 10.6921 | 10.6439 | 14.8584 | 14.8791 | 14.8563 | 14.7869 | 14.7832 | 14.809 | 14.8825 | 14.8007 | 14.7518 | 14.8934 | 14.8537 | 14.9332 | 14.9602 | 15.0719 | 15.0105 | 16.2878 | 16.2866 | 16.3382 | 16.2561 | 16.1766 | 16.1218 | 16.1913 | 17.2743 | 17.2653 | 16.9956 | 18.3564 | 18.1788 | 17.77 | 14.4615 | 14.3226 | 14.1211 | 13.593 | 13.1414 | 12.8384 | 16.8511 | 16.8565 | 16.7941 | 16.1216 | 16.0824 | 16.0601 | 13.5414 | 13.4176 | 13.3666 | 13.2911 | 13.0901 | 13.0153 | 12.8754 | 12.872 | 12.83 | 11.7518 | 11.7966 | 11.8799 | 10.9264 | 10.6488 | 10.4334 | 14.644 | 14.6087 | 14.6196 | 14.8211 | 14.8243 | 14.7999 | 14.8982 | 14.9525 | 14.9093 | 16.6142 | 16.671 | 16.7148 | 16.5348 | 16.5414 | 16.5694 | 17.0415 | 17.7523 | 17.7339 | 17.7105 | 17.5817 | 17.5397 | 17.4871 | 17.3794 | 17.2487 | 18.3946 | 18.3833 | 18.3092 | 14.6392 | 14.4513 | 14.3334 | 13.9269 | 13.6469 | 13.3986 | 19.2897 | 19.1662 | 19.1211 | 14.9763 | 14.9744 | 14.9949 | 14.7488 | 14.7206 | 14.7455 | 12.3025 | 12.2547 | 12.2162 | 10.0756 | 9.9872 | 9.8204 | 9.5312 | 9.5243 | 15.5946 | 15.5587 | 15.443 | 13.0299 | 12.9912 | 13.0016 | 12.7522 | 12.7161 | 12.6699 | 12.6851 | 13.751 | 13.7661 | 13.6302 | 10.9503 | 10.6406 | 10.6497 | 10.624 | 20.2814 | 20.1469 | 20.0455 | 20.1284 | 19.5749 | 19.4191 | 19.3428 | 18.76 | 18.608 | 17.8313 | 18.6906 | 18.6092 | 18.6271 | 18.578 | 18.3776 | 18.2368 | 18.216 | 18.0748 | 19.011 | 18.924 | 18.8877 | 16.0209 | 16.0476 | 15.9081 | 15.817 | 15.7425 | 15.6253 | 15.4406 | 15.3028 | 15.0508 | 11.1365 | 11.0725 | 11.1033 | 18.7388 | 18.613 | 18.4938 | 15.5148 | 15.4872 | 15.4128 | 14.863 | 14.6952 | 14.5571 | 14.7705 | 14.7076 | 14.6124 | 9.735 | 9.6103 | 9.5377 | 11.3509 | 11.2819 | 11.1715 | 10.0797 | 9.9641 | 9.78 | 11.6668 | 11.6147 | 11.4758 | 11.62 | 11.557 | 11.5566 | 14.5458 | 14.4787 | 14.4696 | 13.9201 | 13.8758 | 13.8595 | 18.7467 | 18.5509 | 18.4393 | 15.6652 | 15.6157 | 15.5686 | 15.2023 | 15.0832 | 14.9389 | 15.6857 | 15.674 | 15.5444 | 11.4961 | 11.4041 | 11.2118 | 16.5945 | 16.4603 | 16.3762 | 15.9079 | 15.6611 | 15.5208
77 | suction flow meter (low) Low SH warning |  | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok | FM SH ok
78 | Suction flow meter (low) enthalpy | KJ/kg | 415.6598 | 415.6269 | 415.5848 | 416.8133 | 416.7762 | 416.6259 | 417.7026 | 417.5383 | 417.4648 | 418.2128 | 418.1339 | 418.0527 | 418.3978 | 418.3629 | 418.3354 | 412.6491 | 412.616 | 412.5689 | 412.3568 | 412.3211 | 412.2719 | 413.2347 | 413.1945 | 413.1074 | 413.0597 | 413.0063 | 412.9665 | 416.6843 | 416.6976 | 416.6953 | 416.6823 | 416.6844 | 416.6903 | 416.6932 | 416.6736 | 416.6491 | 416.7361 | 416.7459 | 416.8164 | 416.8888 | 416.9289 | 416.9279 | 417.3477 | 417.3416 | 417.3524 | 417.3373 | 417.3356 | 417.3362 | 417.3788 | 417.8992 | 417.8626 | 417.6963 | 417.5601 | 417.4127 | 417.0635 | 415.6331 | 415.4964 | 415.3241 | 414.7748 | 414.3952 | 414.1507 | 417.8918 | 417.8409 | 417.7955 | 417.3111 | 417.2438 | 417.196 | 415.5262 | 415.4649 | 415.3974 | 415.2425 | 415.1576 | 415.0891 | 414.9747 | 414.9233 | 414.8733 | 414.0672 | 414.0803 | 414.0966 | 413.2915 | 413.0568 | 412.8279 | 416.5471 | 416.5487 | 416.5496 | 416.6687 | 416.6894 | 416.7005 | 416.7998 | 416.8291 | 416.8348 | 417.7033 | 417.7102 | 417.7169 | 417.624 | 417.6293 | 417.6431 | 418.0963 | 418.2709 | 418.2575 | 418.2408 | 418.1245 | 418.1047 | 418.0618 | 417.9882 | 417.8607 | 417.5756 | 417.5269 | 417.4331 | 415.6854 | 415.545 | 415.4198 | 415.0642 | 414.803 | 414.5902 | 418.465 | 418.3736 | 418.3173 | 416.1838 | 416.177 | 416.166 | 415.9874 | 415.9654 | 415.9583 | 414.4202 | 414.3793 | 414.349 | 412.4311 | 412.3608 | 412.2759 | 412.033 | 411.967 | 416.852 | 416.8088 | 416.738 | 415.0993 | 415.0815 | 415.0742 | 414.8847 | 414.8365 | 414.8144 | 414.8097 | 414.7953 | 414.7709 | 414.7098 | 413.2066 | 413.0674 | 413.0613 | 413.044 | 420.5245 | 420.4615 | 420.4176 | 420.4259 | 420.2196 | 420.1379 | 420.0994 | 419.4519 | 419.3064 | 418.7241 | 419.4596 | 419.4309 | 419.3779 | 419.327 | 419.1856 | 419.0857 | 419.0222 | 418.92 | 418.3361 | 418.2692 | 418.2209 | 417.1773 | 417.1325 | 417.0398 | 416.9328 | 416.8475 | 416.754 | 416.3724 | 416.187 | 416.0144 | 413.3621 | 413.3048 | 413.2666 | 418.0889 | 417.9808 | 417.8772 | 416.7181 | 416.6355 | 416.5606 | 416.0502 | 415.9497 | 415.8602 | 415.7729 | 415.6755 | 415.5786 | 412.0312 | 411.9585 | 411.8624 | 413.5382 | 413.4648 | 413.3424 | 412.367 | 412.2211 | 412.0595 | 413.8948 | 413.8597 | 413.7999 | 413.8394 | 413.784 | 413.775 | 415.7644 | 415.7393 | 415.7227 | 415.3401 | 415.3054 | 415.2842 | 418.02 | 417.8324 | 417.7165 | 416.7652 | 416.6988 | 416.6055 | 416.3342 | 416.2039 | 416.0464 | 416.613 | 416.5579 | 416.4479 | 413.6407 | 413.5291 | 413.4017 | 417.608 | 417.4917 | 417.3762 | 416.9796 | 416.8001 | 416.6427
79 | Suction flow meter (low) specific Vol | m3/kg | 0.04006 | 0.040078 | 0.040173 | 0.048108 | 0.048132 | 0.048037 | 0.05833 | 0.057852 | 0.057838 | 0.070136 | 0.07016 | 0.070247 | 0.085454 | 0.085532 | 0.085616 | 0.056017 | 0.055973 | 0.056056 | 0.055822 | 0.055763 | 0.055781 | 0.056257 | 0.056248 | 0.056086 | 0.056122 | 0.05604 | 0.056014 | 0.057598 | 0.05762 | 0.057558 | 0.057388 | 0.057371 | 0.057431 | 0.057644 | 0.057456 | 0.057382 | 0.057548 | 0.057399 | 0.057427 | 0.057292 | 0.057508 | 0.057327 | 0.05995 | 0.059965 | 0.060092 | 0.059884 | 0.059643 | 0.059472 | 0.059555 | 0.061312 | 0.0614 | 0.061074 | 0.06596 | 0.065863 | 0.065674 | 0.059597 | 0.05959 | 0.059498 | 0.059563 | 0.059336 | 0.059151 | 0.060011 | 0.060186 | 0.060133 | 0.059548 | 0.059635 | 0.059714 | 0.057097 | 0.056906 | 0.056955 | 0.057192 | 0.056839 | 0.056818 | 0.056739 | 0.056883 | 0.056906 | 0.056066 | 0.056161 | 0.056364 | 0.055894 | 0.055758 | 0.055792 | 0.057363 | 0.057252 | 0.057282 | 0.057532 | 0.05748 | 0.057373 | 0.057372 | 0.057447 | 0.0573 | 0.05986 | 0.060015 | 0.060131 | 0.05986 | 0.059864 | 0.059908 | 0.059968 | 0.061646 | 0.06163 | 0.061609 | 0.06157 | 0.0615 | 0.06147 | 0.061362 | 0.061353 | 0.066036 | 0.066164 | 0.066234 | 0.059991 | 0.059842 | 0.059864 | 0.059704 | 0.059644 | 0.059532 | 0.066023 | 0.065918 | 0.065958 | 0.059487 | 0.059503 | 0.059601 | 0.05939 | 0.05937 | 0.05947 | 0.056671 | 0.056649 | 0.056624 | 0.055898 | 0.055841 | 0.05559 | 0.055442 | 0.055619 | 0.059336 | 0.059358 | 0.059219 | 0.056832 | 0.056769 | 0.056822 | 0.056637 | 0.056672 | 0.056599 | 0.056659 | 0.059997 | 0.060122 | 0.059885 | 0.056221 | 0.055701 | 0.055747 | 0.055721 | 0.062499 | 0.062274 | 0.062094 | 0.062329 | 0.061242 | 0.061012 | 0.060895 | 0.061096 | 0.061076 | 0.060471 | 0.060856 | 0.060693 | 0.060913 | 0.060918 | 0.060735 | 0.060608 | 0.06074 | 0.060619 | 0.065525 | 0.06546 | 0.065502 | 0.05965 | 0.059872 | 0.059726 | 0.059775 | 0.059809 | 0.059735 | 0.06035 | 0.060501 | 0.060251 | 0.056318 | 0.056297 | 0.056505 | 0.06545 | 0.065394 | 0.065345 | 0.059502 | 0.059673 | 0.059675 | 0.05955 | 0.05934 | 0.059189 | 0.060129 | 0.060238 | 0.060243 | 0.056068 | 0.055907 | 0.055976 | 0.056439 | 0.056451 | 0.056484 | 0.056104 | 0.056193 | 0.056119 | 0.056325 | 0.056272 | 0.056032 | 0.056349 | 0.056325 | 0.05635 | 0.059451 | 0.05932 | 0.059344 | 0.058822 | 0.058792 | 0.058807 | 0.065709 | 0.065688 | 0.065706 | 0.059824 | 0.059876 | 0.060021 | 0.059724 | 0.059758 | 0.059799 | 0.060364 | 0.060501 | 0.060439 | 0.056571 | 0.056628 | 0.056428 | 0.060095 | 0.060039 | 0.060136 | 0.059912 | 0.059703 | 0.059755
80 | Suction flow meter (low) vol Flow | m^3/hr | 337.5 | 337.5 | 62.8112 | 337.5 | 63.7369 | 337.5 | 62.4118 | 61.5254 | 337.5 | 337.5 | 337.5 | 61.8859 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 61.5412 | 337.5 | 337.5 | 337.5 | 62.2787 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 253.6056 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 62.662 | 61.1592 | 337.5 | 61.3157 | 337.5 | 337.5 | 62.1509 | 337.5 | 62.0331 | 59.8879 | 52.3908 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 284.6359 | 337.5 | 337.5 | 61.4666 | 337.5 | 337.5 | 337.5 | 63.271 | 337.5 | 337.5 | 337.5 | 79.3762 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 62.6372 | 337.5 | 337.5 | 337.5 | 337.5 | 34.8992 | 63.7147 | 337.5 | 337.5 | 337.5 | 283.0505 | 337.5 | 63.5516 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 327.8145 | 61.6379 | 62.2928 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 279.7698 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 61.9268 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 62.8289 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 280.1211 | 337.5 | 53.2033 | 337.5 | 286.7679 | 337.5 | 337.5 | 337.5 | 337.5 | 62.6991 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 61.0153 | 337.5 | 337.5 | 337.5 | 62.0509 | 307.1505 | 337.5 | 337.5 | 62.5315 | 337.5 | 23.8928 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 63.0696 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 311.0876 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 57.5395 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 62.3779 | 62.5444 | 337.5 | 62.3906 | 337.5 | 337.5 | 337.5 | 61.4216 | 337.5 | 337.5 | 337.5 | 337.5 | 69.6895 | 337.5 | 63.3226 | 63.5784 | 337.5 | 337.5 | 337.5
81 | Suction flow meter (low) mass Flow | kg/s | 2.3402 | 2.3392 | 0.43431 | 1.9487 | 0.36784 | 1.9516 | 0.29722 | 0.29541 | 1.6209 | 1.3367 | 1.3362 | 0.24472 | 1.0971 | 1.0961 | 1.095 | 1.6736 | 1.6749 | 0.30496 | 1.6794 | 1.6812 | 1.6807 | 0.30751 | 1.6667 | 1.6715 | 1.6705 | 1.6729 | 1.6737 | 1.2231 | 1.627 | 1.6288 | 1.6336 | 1.6341 | 1.6324 | 1.6264 | 1.6317 | 1.6338 | 1.6291 | 1.6333 | 1.6325 | 0.30381 | 0.29541 | 1.6354 | 0.28411 | 1.5634 | 1.5601 | 0.28829 | 1.5719 | 0.28974 | 0.27933 | 0.23736 | 1.5269 | 1.535 | 1.4213 | 1.4234 | 1.4275 | 1.5731 | 1.5732 | 1.3289 | 1.574 | 1.58 | 0.28865 | 1.5622 | 1.5577 | 1.559 | 0.29514 | 1.5721 | 1.57 | 1.642 | 0.38746 | 1.646 | 1.6392 | 1.6494 | 1.65 | 1.6523 | 1.6481 | 1.6475 | 1.6721 | 1.6693 | 1.6633 | 0.31129 | 1.6814 | 1.6804 | 1.6343 | 1.6375 | 0.16924 | 0.30763 | 1.631 | 1.6341 | 1.6341 | 1.3686 | 1.6361 | 0.29491 | 1.5621 | 1.5591 | 1.5662 | 1.5661 | 1.5649 | 1.5633 | 1.5208 | 1.5212 | 1.5217 | 1.479 | 0.2784 | 0.2815 | 1.5278 | 1.528 | 1.4197 | 1.4169 | 1.4154 | 1.5627 | 1.5666 | 1.2982 | 1.5702 | 1.5718 | 1.5748 | 1.42 | 1.4222 | 1.4214 | 1.576 | 1.5756 | 1.573 | 1.5786 | 0.28974 | 1.5764 | 1.6543 | 1.6549 | 1.6557 | 1.6771 | 1.6789 | 1.6865 | 1.691 | 1.6856 | 1.58 | 1.5794 | 1.5831 | 1.6496 | 1.6514 | 1.6499 | 1.6553 | 1.6542 | 1.6564 | 0.30803 | 1.5626 | 1.5593 | 1.5655 | 1.6675 | 1.6831 | 1.6817 | 1.6825 | 1.5 | 1.2495 | 1.5098 | 0.23711 | 1.5308 | 1.3056 | 1.5395 | 1.5345 | 1.535 | 1.5503 | 0.28619 | 1.5447 | 1.5391 | 1.5389 | 1.5436 | 1.5468 | 1.5435 | 1.5465 | 1.4307 | 1.4322 | 0.25875 | 1.5717 | 1.5658 | 1.5697 | 0.28835 | 1.4265 | 1.5694 | 1.5534 | 0.2871 | 1.556 | 0.11785 | 1.6653 | 1.6591 | 1.4324 | 1.4336 | 1.4347 | 1.5756 | 1.5711 | 0.29358 | 1.5743 | 1.5799 | 1.5839 | 1.5591 | 1.5563 | 1.5562 | 1.6721 | 1.6769 | 1.6748 | 1.6611 | 1.6607 | 1.6598 | 1.671 | 1.6684 | 1.5398 | 1.6645 | 1.666 | 1.6731 | 1.6637 | 1.6645 | 0.28364 | 1.5769 | 1.5804 | 1.5798 | 1.5938 | 1.5946 | 1.5942 | 1.4267 | 1.4272 | 0.26371 | 0.29041 | 1.5657 | 0.28875 | 1.5697 | 1.5688 | 1.5678 | 0.28264 | 1.5496 | 1.5511 | 1.6572 | 1.6555 | 0.34306 | 1.56 | 0.29297 | 0.29368 | 1.5648 | 1.5703 | 1.5689
82
83 | Active flow meter : NA adding apples & oranges! | m^3/hr
84 | Active flow meter | kg/s | 7.9489 | 7.9571 | 7.9399 | 6.7195 | 6.7394 | 6.7741 | 5.6098 | 5.6844 | 5.697 | 4.7338 | 4.7317 | 4.7354 | 3.8907 | 3.8882 | 3.8842 | 0.84497 | 0.84666 | 0.85519 | 0.9195 | 0.91899 | 0.9021 | 0.86095 | 0.88922 | 0.86704 | 0.92182 | 0.94585 | 0.93789 | 2.0144 | 2.0139 | 2.0161 | 2.0198 | 2.0199 | 2.0153 | 2.1651 | 2.1694 | 2.1862 | 2.2051 | 2.2031 | 2.1964 | 2.3118 | 2.2994 | 2.2945 | 3.4147 | 3.409 | 3.4077 | 3.4827 | 3.6936 | 3.6974 | 3.6988 | 5.0717 | 5.0738 | 5.0904 | 5.0286 | 5.0508 | 5.0205 | 5.5041 | 5.4903 | 5.4845 | 5.4731 | 5.4607 | 5.4454 | 3.4113 | 3.3961 | 3.3989 | 3.6032 | 3.6028 | 3.5954 | 2.245 | 2.2506 | 2.2466 | 1.9719 | 1.9843 | 1.9989 | 2.0022 | 1.9923 | 1.9941 | 0.90279 | 0.90239 | 0.90339 | 0.95738 | 0.96313 | 0.97594 | 1.9955 | 2.0039 | 2.0079 | 2.1523 | 2.1567 | 2.1625 | 2.1544 | 2.1618 | 2.1624 | 3.4232 | 3.4153 | 3.4132 | 3.6009 | 3.6014 | 3.5939 | 3.5601 | 4.9802 | 4.9928 | 4.989 | 4.9863 | 4.9803 | 4.9786 | 4.9947 | 4.986 | 4.9395 | 4.9277 | 4.9444 | 5.3674 | 5.3761 | 5.3614 | 5.3669 | 5.3656 | 5.3682 | 4.872 | 4.8748 | 4.8678 | 3.2563 | 3.2448 | 3.2439 | 3.3194 | 3.3287 | 3.3173 | 1.9283 | 1.927 | 1.9185 | 0.81133 | 0.82824 | 0.77394 | 0.89741 | 0.9016 | 3.5591 | 3.5572 | 3.5789 | 2.0998 | 2.0996 | 2.1068 | 2.1139 | 2.2208 | 2.2316 | 2.2242 | 2.0907 | 2.0913 | 2.0981 | 0.87332 | 0.89993 | 0.87827 | 0.90689 | 4.8635 | 4.8719 | 4.8808 | 4.8639 | 5.295 | 5.2907 | 5.2826 | 5.1749 | 5.1771 | 5.2175 | 5.2843 | 5.3043 | 5.293 | 5.2932 | 5.3034 | 5.3113 | 5.3045 | 5.3194 | 5.076 | 5.0697 | 5.0724 | 5.5437 | 5.5157 | 5.5064 | 5.491 | 5.4786 | 5.4826 | 5.1164 | 5.0837 | 5.1154 | 2.2677 | 2.2716 | 2.2653 | 5.0749 | 5.0757 | 5.089 | 5.5529 | 5.5225 | 5.5315 | 5.5029 | 5.513 | 5.5463 | 5.1119 | 5.0984 | 5.0966 | 2.2775 | 2.2874 | 2.2923 | 2.136 | 2.1344 | 2.1239 | 1.9791 | 1.9755 | 1.9819 | 0.82416 | 0.8299 | 0.87659 | 0.93914 | 0.9198 | 0.92729 | 3.4629 | 3.4756 | 3.474 | 3.6779 | 3.6857 | 3.6916 | 5.0125 | 5.0357 | 5.0512 | 5.4851 | 5.4954 | 5.4851 | 5.4924 | 5.4956 | 5.4857 | 5.0671 | 5.0496 | 5.0464 | 2.2403 | 2.2349 | 2.2491 | 5.4632 | 5.4592 | 5.4415 | 5.4556 | 5.4714 | 5.4878
85 | Flow meter used, 1=large, 2=small, 3=both |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
86 | Total suction vol flow, at flow meter | m^3/hr | 1151.4805 | 1152.8279 | 1152.0968 | 1151.4604 | 1154.0277 | 1147.5392 | 1142.2198 | 1144.5347 | 1143.7614 | 1127.7631 | 1131.9011 | 1133.7521 | 1125.7011 | 1125.3593 | 1124.7775 | 170.4691 | 170.7793 | 173.1454 | 185.5478 | 185.3106 | 182.0024 | 173.6105 | 179.6716 | 175.2181 | 186.2916 | 190.8848 | 189.2306 | 405.5737 | 406.1605 | 406.501 | 405.8454 | 405.5364 | 404.5136 | 438.866 | 437.9952 | 440.3912 | 441.9586 | 439.6614 | 437.6309 | 460.2157 | 459.3186 | 458.4065 | 709.7458 | 708.8906 | 708.9545 | 721.6864 | 763.8997 | 761.9131 | 763.2113 | 1069.3069 | 1070.9042 | 1068.5406 | 1140.6536 | 1137.8028 | 1140.7737 | 1141.7769 | 1138.8727 | 1136.4648 | 1139.9488 | 1141.6015 | 1143.08 | 708.5533 | 708.239 | 708.9824 | 753.3499 | 754.6669 | 753.9793 | 459.6092 | 459.1117 | 458.4765 | 402.5823 | 402.5339 | 405.1102 | 404.9291 | 403.8661 | 404.6599 | 179.8175 | 180.006 | 180.6444 | 192.8903 | 193.2239 | 196.0088 | 402.7638 | 402.2725 | 402.9232 | 432.2026 | 432.5648 | 432.9053 | 431.5543 | 433.2524 | 432.0915 | 717.0727 | 716.8703 | 717.2743 | 752.582 | 752.1472 | 750.0536 | 744.4851 | 1058.93 | 1061.3358 | 1060.2397 | 1059.7164 | 1057.6105 | 1057.1208 | 1059.3345 | 1060.6859 | 1120.7046 | 1122.7851 | 1125.4913 | 1126.2432 | 1125.8052 | 1122.9724 | 1128.7409 | 1127.6508 | 1125.5224 | 1094.5429 | 1094.4888 | 1094.2393 | 682.6334 | 679.5682 | 680.3845 | 695.7665 | 697.6081 | 696.4332 | 389.4074 | 389.6914 | 388.8562 | 163.5925 | 166.9995 | 155.5166 | 179.5908 | 180.9583 | 735.1244 | 734.6323 | 734.4339 | 421.724 | 421.0643 | 422.7079 | 422.476 | 444.7665 | 446.4117 | 445.5893 | 444.5517 | 445.6618 | 445.5565 | 175.3381 | 180.2559 | 176.42 | 182.0249 | 1032.9634 | 1033.6461 | 1034.0407 | 1036.3232 | 1100.9827 | 1103.1869 | 1101.1818 | 1107.5314 | 1112.7848 | 1109.5549 | 1106.4373 | 1107.5957 | 1107.953 | 1106.9884 | 1107.5945 | 1107.8572 | 1108.7734 | 1107.5527 | 1138.231 | 1138.4527 | 1142.0461 | 1141.9203 | 1141.2077 | 1141.1278 | 1145.9468 | 1145.4018 | 1146.4713 | 1066.1123 | 1071.2948 | 1069.3823 | 457.3374 | 457.0021 | 458.2307 | 1135.4609 | 1134.0225 | 1134.7348 | 1144.781 | 1140.8975 | 1140.9929 | 1147.2442 | 1141.9289 | 1147.5331 | 1068.0927 | 1069.1057 | 1069.6966 | 458.1127 | 459.1281 | 460.5906 | 432.0657 | 432.1927 | 432.6537 | 402.8876 | 402.368 | 402.4024 | 165.5452 | 166.7393 | 175.6701 | 189.3809 | 185.1499 | 186.6649 | 721.4893 | 722.4118 | 722.2458 | 763.2945 | 764.0845 | 765.0877 | 1133.5116 | 1132.8965 | 1126.0625 | 1134.0115 | 1136.7857 | 1137.393 | 1134.7679 | 1137.4385 | 1134.6126 | 1063.7015 | 1072.4233 | 1068.1636 | 455.8056 | 454.8754 | 455.8404 | 1141.5298 | 1139.8152 | 1139.1977 | 1141.3384 | 1142.9751 | 1143.4111
87 | Total Suction mass Flow | kg/s | 7.9489 | 7.9571 | 7.9399 | 6.7195 | 6.7394 | 6.7741 | 5.6098 | 5.6844 | 5.697 | 4.7338 | 4.7317 | 4.7354 | 3.8907 | 3.8882 | 3.8842 | 0.84497 | 0.84666 | 0.85519 | 0.9195 | 0.91899 | 0.9021 | 0.86095 | 0.88922 | 0.86704 | 0.92182 | 0.94585 | 0.93789 | 2.0144 | 2.0139 | 2.0161 | 2.0198 | 2.0199 | 2.0153 | 2.1651 | 2.1694 | 2.1862 | 2.2051 | 2.2031 | 2.1964 | 2.3118 | 2.2994 | 2.2945 | 3.4147 | 3.409 | 3.4077 | 3.4827 | 3.6936 | 3.6974 | 3.6988 | 5.0717 | 5.0738 | 5.0904 | 5.0286 | 5.0508 | 5.0205 | 5.5041 | 5.4903 | 5.4845 | 5.4731 | 5.4607 | 5.4454 | 3.4113 | 3.3961 | 3.3989 | 3.6032 | 3.6028 | 3.5954 | 2.245 | 2.2506 | 2.2466 | 1.9719 | 1.9843 | 1.9989 | 2.0022 | 1.9923 | 1.9941 | 0.90279 | 0.90239 | 0.90339 | 0.95738 | 0.96313 | 0.97594 | 1.9955 | 2.0039 | 2.0079 | 2.1523 | 2.1567 | 2.1625 | 2.1544 | 2.1618 | 2.1624 | 3.4232 | 3.4153 | 3.4132 | 3.6009 | 3.6014 | 3.5939 | 3.5601 | 4.9802 | 4.9928 | 4.989 | 4.9863 | 4.9803 | 4.9786 | 4.9947 | 4.986 | 4.9395 | 4.9277 | 4.9444 | 5.3674 | 5.3761 | 5.3614 | 5.3669 | 5.3656 | 5.3682 | 4.872 | 4.8748 | 4.8678 | 3.2563 | 3.2448 | 3.2439 | 3.3194 | 3.3287 | 3.3173 | 1.9283 | 1.927 | 1.9185 | 0.81133 | 0.82824 | 0.77394 | 0.89741 | 0.9016 | 3.5591 | 3.5572 | 3.5789 | 2.0998 | 2.0996 | 2.1068 | 2.1139 | 2.2208 | 2.2316 | 2.2242 | 2.0907 | 2.0913 | 2.0981 | 0.87332 | 0.89993 | 0.87827 | 0.90689 | 4.8635 | 4.8719 | 4.8808 | 4.8639 | 5.295 | 5.2907 | 5.2826 | 5.1749 | 5.1771 | 5.2175 | 5.2843 | 5.3043 | 5.293 | 5.2932 | 5.3034 | 5.3113 | 5.3045 | 5.3194 | 5.076 | 5.0697 | 5.0724 | 5.5437 | 5.5157 | 5.5064 | 5.491 | 5.4786 | 5.4826 | 5.1164 | 5.0837 | 5.1154 | 2.2677 | 2.2716 | 2.2653 | 5.0749 | 5.0757 | 5.089 | 5.5529 | 5.5225 | 5.5315 | 5.5029 | 5.513 | 5.5463 | 5.1119 | 5.0984 | 5.0966 | 2.2775 | 2.2874 | 2.2923 | 2.136 | 2.1344 | 2.1239 | 1.9791 | 1.9755 | 1.9819 | 0.82416 | 0.8299 | 0.87659 | 0.93914 | 0.9198 | 0.92729 | 3.4629 | 3.4756 | 3.474 | 3.6779 | 3.6857 | 3.6916 | 5.0125 | 5.0357 | 5.0512 | 5.4851 | 5.4954 | 5.4851 | 5.4924 | 5.4956 | 5.4857 | 5.0671 | 5.0496 | 5.0464 | 2.2403 | 2.2349 | 2.2491 | 5.4632 | 5.4592 | 5.4415 | 5.4556 | 5.4714 | 5.4878
88
89 | Suction orifice Plate Temp | ºC | 25.0492 | 24.9605 | 24.7684 | 21.3108 | 20.8375 | 19.4422 | 16.3206 | 15.6208 | 15.0402 | 10.098 | 10.5134 | 9.7332 | 7.3524 | 7.2084 | 7.0618 | 18.4808 | 18.5859 | 18.8415 | 18.684 | 18.6889 | 18.6476 | 18.323 | 18.6046 | 18.8127 | 18.7143 | 18.7131 | 18.7292 | 16.6336 | 16.8627 | 16.9105 | 16.7911 | 16.6719 | 16.4341 | 17.5757 | 17.3977 | 17.2151 | 15.7404 | 15.4801 | 15.5112 | 15.6782 | 15.91 | 16.4212 | 15.0114 | 15.0351 | 14.7431 | 14.5322 | 14.934 | 14.876 | 14.748 | 13.313 | 13.2327 | 12.9854 | 11.7386 | 10.9293 | 12.2237 | 13.463 | 13.4539 | 13.5436 | 13.5748 | 14.9419 | 15.7748 | 15.2453 | 15.4783 | 15.4345 | 17.5607 | 17.521 | 17.4276 | 20.2842 | 20.2017 | 20.063 | 19.0741 | 18.9792 | 18.8013 | 18.5706 | 18.4883 | 18.493 | 17.1189 | 17.0125 | 16.7228 | 18.9759 | 18.5056 | 18.4042 | 17.3922 | 16.9391 | 16.7895 | 16.1943 | 16.1802 | 16.1937 | 16.3087 | 16.2008 | 16.1704 | 17.1666 | 17.0217 | 16.8172 | 16.5701 | 16.3831 | 16.1233 | 16.9093 | 14.3163 | 14.3056 | 14.2855 | 14.3732 | 14.3977 | 14.4554 | 14.6297 | 14.9905 | 12.1148 | 12.491 | 11.6225 | 14.4707 | 14.4767 | 14.447 | 15.2061 | 14.9845 | 14.7759 | 11.0711 | 11.1825 | 11.2949 | 16.9689 | 16.7949 | 16.82 | 17.2337 | 17.2418 | 17.2429 | 18.3113 | 18.719 | 19.14 | 18.3754 | 18.4238 | 18.4575 | 17.928 | 17.8053 | 15.2657 | 15.1213 | 14.6392 | 16.9474 | 16.8708 | 16.7454 | 16.3672 | 16.8494 | 16.8831 | 16.9756 | 16.818 | 16.8359 | 16.894 | 17.6224 | 18.5485 | 18.5994 | 18.336 | 13.6671 | 14.0142 | 14.3711 | 14.4289 | 13.5508 | 14.6941 | 15.0175 | 18.91 | 19.3815 | 18.9184 | 21.6936 | 21.6804 | 21.6293 | 21.5924 | 21.5042 | 21.445 | 21.4117 | 21.3538 | 12.1552 | 12.4514 | 12.4251 | 13.616 | 13.7924 | 14.5835 | 15.4833 | 15.6995 | 15.957 | 13.1966 | 13.8774 | 13.2902 | 17.6319 | 17.477 | 17.6169 | 11.4366 | 11.2606 | 11.0319 | 13.6057 | 13.3032 | 12.8859 | 14.7596 | 14.4407 | 14.5919 | 13.3308 | 13.5145 | 13.5078 | 16.7238 | 16.7508 | 16.4436 | 18.3129 | 18.5421 | 19.3375 | 19.1512 | 18.6899 | 18.3133 | 17.8738 | 18.0498 | 18.1805 | 18.1335 | 17.8199 | 17.7217 | 15.4962 | 15.4738 | 15.4137 | 16.3355 | 16.1358 | 15.6846 | 12.61 | 11.434 | 10.0759 | 13.2532 | 13.0466 | 13.0493 | 13.1758 | 12.8939 | 12.9535 | 14.8885 | 16.1038 | 15.307 | 18.7739 | 18.5876 | 18.4132 | 15.277 | 15.2205 | 15.4129 | 15.5764 | 15.5655 | 14.7076
90 | Suction orifice plate Pressure | BarA | 5.216 | 5.2182 | 5.1985 | 4.4265 | 4.426 | 4.4279 | 3.7075 | 3.7354 | 3.7322 | 3.1181 | 3.1164 | 3.1118 | 2.5861 | 2.5828 | 2.5799 | 3.8566 | 3.8564 | 3.8503 | 3.8623 | 3.8631 | 3.8596 | 3.8487 | 3.8484 | 3.8559 | 3.8528 | 3.8599 | 3.86 | 3.8239 | 3.8214 | 3.8248 | 3.8339 | 3.8354 | 3.8331 | 3.8163 | 3.8294 | 3.833 | 3.8248 | 3.8342 | 3.8347 | 3.8437 | 3.8285 | 3.8413 | 3.6717 | 3.6699 | 3.6662 | 3.6728 | 3.681 | 3.69 | 3.6895 | 3.5548 | 3.5498 | 3.5606 | 3.301 | 3.3016 | 3.3031 | 3.5973 | 3.5954 | 3.5964 | 3.58 | 3.5867 | 3.5951 | 3.6758 | 3.6644 | 3.6705 | 3.6877 | 3.6863 | 3.6779 | 3.8293 | 3.8382 | 3.8343 | 3.8213 | 3.8409 | 3.8422 | 3.8433 | 3.8336 | 3.8282 | 3.8756 | 3.8735 | 3.856 | 3.8731 | 3.8784 | 3.8715 | 3.8344 | 3.8415 | 3.8397 | 3.8255 | 3.8266 | 3.8332 | 3.8361 | 3.8331 | 3.8404 | 3.6831 | 3.6728 | 3.6675 | 3.6826 | 3.6794 | 3.6735 | 3.6803 | 3.5481 | 3.5496 | 3.5505 | 3.5514 | 3.5526 | 3.5538 | 3.5599 | 3.5616 | 3.3022 | 3.2934 | 3.2919 | 3.5812 | 3.5881 | 3.5827 | 3.5863 | 3.5838 | 3.5866 | 3.3081 | 3.3152 | 3.3094 | 3.6831 | 3.6812 | 3.6711 | 3.6819 | 3.682 | 3.678 | 3.8382 | 3.8405 | 3.8411 | 3.8554 | 3.8625 | 3.8756 | 3.8783 | 3.8683 | 3.6928 | 3.688 | 3.6981 | 3.8405 | 3.8409 | 3.8385 | 3.8478 | 3.8444 | 3.849 | 3.8462 | 3.6404 | 3.6361 | 3.6467 | 3.8491 | 3.8824 | 3.8803 | 3.881 | 3.5336 | 3.5451 | 3.5526 | 3.5419 | 3.5812 | 3.5953 | 3.5991 | 3.5806 | 3.5825 | 3.6027 | 3.5932 | 3.5989 | 3.5887 | 3.5867 | 3.5919 | 3.598 | 3.5949 | 3.5978 | 3.3181 | 3.3226 | 3.3133 | 3.6081 | 3.5952 | 3.6013 | 3.5956 | 3.5958 | 3.599 | 3.5679 | 3.5541 | 3.567 | 3.8387 | 3.8398 | 3.8213 | 3.319 | 3.3222 | 3.3213 | 3.6086 | 3.599 | 3.598 | 3.5944 | 3.6047 | 3.6118 | 3.5723 | 3.5622 | 3.5611 | 3.832 | 3.8366 | 3.8303 | 3.837 | 3.8328 | 3.8283 | 3.8341 | 3.8272 | 3.8319 | 3.859 | 3.8605 | 3.8767 | 3.8528 | 3.8544 | 3.8517 | 3.6691 | 3.6747 | 3.6724 | 3.6921 | 3.6929 | 3.694 | 3.3126 | 3.306 | 3.3061 | 3.5963 | 3.5948 | 3.5821 | 3.5941 | 3.5918 | 3.5857 | 3.576 | 3.5635 | 3.5706 | 3.8283 | 3.8228 | 3.8324 | 3.5924 | 3.5943 | 3.5849 | 3.5937 | 3.6008 | 3.5953
91 | Suction orifice plate DP | mb | 323.2773 | 325.4291 | 322.0993 | 270.6982 | 273.5318 | 273.1486 | 224.3841 | 226.8361 | 229.2083 | 186.1282 | 188.184 | 185.5767 | 151.7925 | 151.7388 | 150.665 | 1.3097 | 1.674 | 1.5389 | 2.2373 | 1.982 | 2.2151 | 1.6721 | 1.5708 | 1.6275 | 2.2243 | 2.2516 | 2.3649 | 23.9647 | 23.8745 | 24.1535 | 23.9946 | 24.2287 | 23.9784 | 28.3516 | 28.7205 | 28.7446 | 28.5867 | 28.8264 | 28.9657 | 32.4752 | 32.4983 | 32.6608 | 80.9685 | 80.4602 | 81.1306 | 82.5922 | 92.7642 | 92.7023 | 92.6066 | 187.6478 | 186.9884 | 187.976 | 199.4122 | 199.897 | 199.1162 | 219.1486 | 220.8378 | 218.5636 | 217.5305 | 217.2101 | 218.5795 | 79.8628 | 79.2624 | 79.6515 | 89.5666 | 89.0704 | 88.9981 | 31.0156 | 30.5822 | 30.9036 | 22.9183 | 22.818 | 23.0146 | 23.1846 | 23.0049 | 22.6776 | 1.6981 | 1.6955 | 1.8036 | 2.7025 | 2.6085 | 2.7387 | 23.3978 | 23.4844 | 23.4356 | 27.7894 | 27.7675 | 28.393 | 28.2084 | 27.9007 | 28.0143 | 81.7623 | 82.0445 | 81.8173 | 91.2603 | 89.7492 | 89.8254 | 86.746 | 179.0383 | 179.583 | 179.664 | 180.9687 | 179.2053 | 179.6663 | 179.2186 | 180.6522 | 191.7625 | 191.5935 | 191.1097 | 209.5718 | 209.675 | 211.0695 | 210.5388 | 210.2152 | 211.497 | 183.9637 | 184.935 | 184.1161 | 74.1054 | 74.3359 | 74.2546 | 75.61 | 75.6386 | 76.1941 | 21.5537 | 21.3326 | 21.1526 | 1.2244 | 1.4253 | 1.3989 | 1.7453 | 2.0865 | 86.2212 | 85.4827 | 85.6452 | 25.9342 | 26.4164 | 26.4108 | 26.4385 | 29.8578 | 29.7686 | 29.6787 | 27.3374 | 27.1385 | 27.5139 | 1.9117 | 1.8941 | 1.8606 | 1.8466 | 170.3776 | 171.9033 | 171.0744 | 171.6025 | 201.3058 | 202.6124 | 201.8391 | 200.2897 | 200.9652 | 201.5061 | 200.7868 | 201.8515 | 200.0367 | 200.6286 | 199.9383 | 201.6509 | 200.2157 | 201.3455 | 192.5661 | 192.1864 | 192.6156 | 214.0819 | 211.4244 | 211.8216 | 210.7527 | 211.1096 | 210.1364 | 179.8359 | 178.9393 | 181.5336 | 30.5956 | 30.5311 | 30.928 | 194.3187 | 194.8563 | 195.2655 | 215.2247 | 213.4955 | 214.481 | 213.8325 | 213.2737 | 213.851 | 182.0441 | 180.9149 | 180.9762 | 31.2741 | 31.0827 | 31.643 | 28.2064 | 27.6692 | 27.5663 | 23.5541 | 22.9075 | 23.2396 | 1.2654 | 1.2836 | 1.55 | 1.8736 | 2.0917 | 2.1546 | 82.7042 | 82.1155 | 81.4888 | 91.9118 | 92.3175 | 91.9847 | 194.9318 | 195.6006 | 196.4679 | 215.1084 | 216.1721 | 214.3456 | 214.4257 | 215.2081 | 214.3566 | 181.221 | 180.1475 | 181.7608 | 31.3086 | 30.9101 | 31.3611 | 213.419 | 212.7942 | 211.3186 | 212.3947 | 212.4331 | 212.7782
92 | Suction orifice plate SH | ºC | 7.9836 | 7.8811 | 7.8089 | 9.3361 | 8.8661 | 7.4575 | 9.6247 | 8.7056 | 8.1503 | 8.3497 | 8.7803 | 8.0415 | 10.7316 | 10.6215 | 10.5051 | 10.6294 | 10.736 | 11.0385 | 10.7893 | 10.788 | 10.7737 | 10.532 | 10.8155 | 10.9666 | 10.8917 | 10.8362 | 10.8515 | 9.0325 | 9.2807 | 9.3023 | 9.1132 | 8.983 | 8.7628 | 10.0333 | 9.7546 | 9.544 | 8.1322 | 7.8004 | 7.8274 | 7.9257 | 8.2738 | 8.687 | 8.5978 | 8.6356 | 8.3733 | 8.1102 | 8.4467 | 8.3172 | 8.1935 | 7.8371 | 7.7975 | 7.4622 | 8.3828 | 7.5691 | 8.8503 | 7.6437 | 7.6501 | 7.7317 | 7.8945 | 9.2079 | 9.9728 | 8.7993 | 9.1227 | 9.0304 | 11.0206 | 10.9916 | 10.9651 | 12.6415 | 12.4912 | 12.3824 | 11.4933 | 11.248 | 11.0599 | 10.8209 | 10.8126 | 10.8589 | 9.1229 | 9.0327 | 8.876 | 10.9984 | 10.4883 | 10.4394 | 9.7108 | 9.2029 | 9.067 | 8.5808 | 8.5581 | 8.5217 | 8.6141 | 8.5291 | 8.4427 | 10.6626 | 10.5991 | 10.4369 | 10.0699 | 9.9087 | 9.6951 | 10.4274 | 8.895 | 8.8723 | 8.8446 | 8.9246 | 8.9396 | 8.9878 | 9.1122 | 9.4598 | 8.7494 | 9.2006 | 8.3457 | 8.7809 | 8.7316 | 8.7455 | 9.4754 | 9.2736 | 9.0425 | 7.6547 | 7.7048 | 7.867 | 10.4654 | 10.3063 | 10.4112 | 10.7394 | 10.7469 | 10.7793 | 10.6009 | 10.9907 | 11.4071 | 10.5332 | 10.5271 | 10.4612 | 9.911 | 9.8649 | 8.685 | 8.5785 | 8.0168 | 9.2194 | 9.1392 | 9.0321 | 8.5834 | 9.0915 | 9.0901 | 9.2038 | 10.6528 | 10.7057 | 10.6792 | 9.8285 | 10.5008 | 10.5674 | 10.2991 | 8.3637 | 8.6173 | 8.9133 | 9.0584 | 7.8612 | 8.8909 | 9.1837 | 13.2253 | 13.6814 | 13.0551 | 15.9072 | 15.8482 | 15.8789 | 15.8579 | 15.7281 | 15.6197 | 15.6115 | 15.5306 | 8.6525 | 8.9106 | 8.964 | 7.7099 | 7.9897 | 8.7315 | 9.6773 | 9.8923 | 10.1241 | 7.6148 | 8.4072 | 7.7153 | 9.9174 | 9.7539 | 10.0362 | 7.9265 | 7.7237 | 7.5027 | 7.6957 | 7.4699 | 7.061 | 8.9635 | 8.5619 | 8.6561 | 7.7131 | 7.9784 | 7.9811 | 9.0605 | 9.0523 | 8.7932 | 10.6112 | 10.8724 | 11.7028 | 11.4721 | 11.0638 | 10.6505 | 10.0043 | 10.1685 | 10.176 | 10.3109 | 9.985 | 9.908 | 9.1033 | 9.0364 | 8.9942 | 9.7604 | 9.5543 | 9.0946 | 9.1546 | 8.0354 | 6.6767 | 7.4415 | 7.2475 | 7.3526 | 7.3824 | 7.1187 | 7.2273 | 9.241 | 10.5576 | 9.7032 | 11.1395 | 10.9949 | 10.7469 | 9.4973 | 9.4253 | 9.6932 | 9.7859 | 9.7182 | 8.9039
93 | Suction orifice plate gauge | ºC | 17.0656 | 17.0793 | 16.9595 | 11.9747 | 11.9714 | 11.9848 | 6.696 | 6.9152 | 6.8899 | 1.7482 | 1.7331 | 1.6916 | -3.3792 | -3.4131 | -3.4433 | 7.8513 | 7.8499 | 7.803 | 7.8947 | 7.9008 | 7.874 | 7.7909 | 7.7891 | 7.8461 | 7.8226 | 7.8768 | 7.8776 | 7.6011 | 7.582 | 7.6082 | 7.6779 | 7.6889 | 7.6713 | 7.5424 | 7.6432 | 7.6712 | 7.6081 | 7.6797 | 7.6838 | 7.7525 | 7.6362 | 7.7343 | 6.4137 | 6.3995 | 6.3698 | 6.422 | 6.4873 | 6.5587 | 6.5545 | 5.4759 | 5.4353 | 5.5232 | 3.3558 | 3.3602 | 3.3734 | 5.8193 | 5.8039 | 5.8119 | 5.6803 | 5.734 | 5.8021 | 6.446 | 6.3556 | 6.4041 | 6.5401 | 6.5294 | 6.4625 | 7.6427 | 7.7105 | 7.6806 | 7.5808 | 7.7313 | 7.7414 | 7.7497 | 7.6757 | 7.6341 | 7.996 | 7.9798 | 7.8468 | 7.9775 | 8.0173 | 7.9648 | 7.6814 | 7.7363 | 7.7225 | 7.6135 | 7.6221 | 7.672 | 7.6946 | 7.6716 | 7.7277 | 6.504 | 6.4226 | 6.3804 | 6.5001 | 6.4745 | 6.4281 | 6.4819 | 5.4213 | 5.4333 | 5.441 | 5.4486 | 5.4581 | 5.4676 | 5.5175 | 5.5307 | 3.3654 | 3.2904 | 3.2768 | 5.6898 | 5.7451 | 5.7014 | 5.7307 | 5.7109 | 5.7333 | 3.4163 | 3.4777 | 3.4279 | 6.5035 | 6.4886 | 6.4088 | 6.4943 | 6.4948 | 6.4636 | 7.7104 | 7.7284 | 7.7328 | 7.8422 | 7.8967 | 7.9963 | 8.017 | 7.9404 | 6.5807 | 6.5428 | 6.6224 | 7.7281 | 7.7316 | 7.7133 | 7.7838 | 7.7579 | 7.793 | 7.7718 | 6.1652 | 6.1302 | 6.2148 | 7.7939 | 8.0478 | 8.032 | 8.0369 | 5.3034 | 5.3969 | 5.4578 | 5.3706 | 5.6896 | 5.8032 | 5.8339 | 5.6846 | 5.7001 | 5.8633 | 5.7864 | 5.8322 | 5.7505 | 5.7345 | 5.7761 | 5.8253 | 5.8002 | 5.8231 | 3.5026 | 3.5408 | 3.4611 | 5.9061 | 5.8027 | 5.852 | 5.806 | 5.8072 | 5.8329 | 5.5818 | 5.4702 | 5.5749 | 7.7145 | 7.7231 | 7.5807 | 3.5101 | 3.537 | 3.5292 | 5.91 | 5.8333 | 5.8249 | 5.7961 | 5.8788 | 5.9358 | 5.6176 | 5.5361 | 5.5267 | 7.6633 | 7.6985 | 7.6504 | 7.7017 | 7.6697 | 7.6347 | 7.6791 | 7.6261 | 7.6628 | 7.8695 | 7.8813 | 8.0045 | 7.8225 | 7.8349 | 7.8137 | 6.3929 | 6.4374 | 6.4195 | 6.5751 | 6.5815 | 6.5901 | 3.4554 | 3.3986 | 3.3992 | 5.8117 | 5.7991 | 5.6967 | 5.7934 | 5.7752 | 5.7263 | 5.6475 | 5.5463 | 5.6038 | 7.6344 | 7.5927 | 7.6663 | 5.7797 | 5.7952 | 5.7197 | 5.7905 | 5.8473 | 5.8038
94 | Suction orifice plate enthalpy | KJ/kg | 415.9462 | 415.8555 | 415.7168 | 414.2372 | 413.7945 | 412.4801 | 411.3149 | 410.607 | 410.0829 | 407.1278 | 407.5039 | 406.8172 | 406.0318 | 405.914 | 405.7931 | 412.9423 | 413.0393 | 413.2883 | 413.1157 | 413.1183 | 413.0887 | 412.8158 | 413.075 | 413.2487 | 413.1656 | 413.1479 | 413.1624 | 411.3228 | 411.5392 | 411.5749 | 411.4435 | 411.3305 | 411.1174 | 412.206 | 412.0116 | 411.8352 | 410.4996 | 410.2374 | 410.2647 | 410.3964 | 410.6467 | 411.0858 | 410.2041 | 410.2301 | 409.9723 | 409.7634 | 410.1106 | 410.0355 | 409.9197 | 408.9414 | 408.8807 | 408.6284 | 408.1445 | 407.4133 | 408.5767 | 408.9728 | 408.9693 | 409.0487 | 409.1175 | 410.347 | 411.0852 | 410.4079 | 410.6484 | 410.5937 | 412.4947 | 412.4617 | 412.3962 | 414.66 | 414.5643 | 414.4459 | 413.5689 | 413.4365 | 413.2702 | 413.0558 | 413.0028 | 413.0198 | 411.6452 | 411.5524 | 411.3277 | 413.3586 | 412.9141 | 412.8371 | 411.9947 | 411.5613 | 411.4281 | 410.9152 | 410.8996 | 410.8962 | 410.9948 | 410.9028 | 410.8572 | 412.1456 | 412.0376 | 411.8635 | 411.602 | 411.439 | 411.2156 | 411.9173 | 409.8711 | 409.8578 | 409.8373 | 409.9148 | 409.9342 | 409.9839 | 410.1275 | 410.4518 | 408.4809 | 408.8414 | 408.0627 | 409.931 | 409.9198 | 409.9059 | 410.5885 | 410.3926 | 410.1959 | 407.5248 | 407.6074 | 407.7233 | 411.9652 | 411.8108 | 411.8576 | 412.2097 | 412.217 | 412.2273 | 412.8298 | 413.1986 | 413.5836 | 412.8483 | 412.876 | 412.8764 | 412.3831 | 412.294 | 410.3852 | 410.2648 | 409.799 | 411.5715 | 411.5 | 411.3904 | 411.0204 | 411.472 | 411.492 | 411.5837 | 411.9281 | 411.9548 | 411.9827 | 412.1713 | 412.9442 | 412.9958 | 412.7521 | 409.316 | 409.6036 | 409.9101 | 409.9888 | 409.0928 | 410.1004 | 410.3859 | 413.9709 | 414.3951 | 413.9281 | 416.4725 | 416.4481 | 416.4239 | 416.3946 | 416.3032 | 416.236 | 416.2125 | 416.1536 | 408.4777 | 408.7339 | 408.7331 | 409.0857 | 409.2784 | 409.9848 | 410.8185 | 411.015 | 411.2419 | 408.803 | 409.4571 | 408.8904 | 412.2046 | 412.0597 | 412.2321 | 407.8272 | 407.6605 | 407.4563 | 409.0751 | 408.8228 | 408.4444 | 410.1622 | 409.8464 | 409.967 | 408.9143 | 409.1066 | 409.1033 | 411.3862 | 411.4 | 411.1327 | 412.8339 | 413.054 | 413.7943 | 413.6101 | 413.2029 | 412.8462 | 412.379 | 412.5371 | 412.6191 | 412.6321 | 412.3401 | 412.2564 | 410.6535 | 410.6195 | 410.5699 | 411.3651 | 411.1806 | 410.7655 | 408.9015 | 407.8574 | 406.6315 | 408.7838 | 408.5991 | 408.6333 | 408.7188 | 408.4672 | 408.5368 | 410.3242 | 411.4599 | 410.7181 | 413.2774 | 413.1191 | 412.9368 | 410.6384 | 410.5824 | 410.7801 | 410.9079 | 410.8811 | 410.1125
95 | Suction orifice plate specific Vol | m3/kg | 0.041212 | 0.041172 | 0.04131 | 0.048719 | 0.048609 | 0.048241 | 0.057935 | 0.057257 | 0.057148 | 0.06803 | 0.068207 | 0.068061 | 0.082305 | 0.082362 | 0.082406 | 0.056042 | 0.056074 | 0.056243 | 0.056006 | 0.055994 | 0.05604 | 0.056127 | 0.056208 | 0.056144 | 0.056167 | 0.056052 | 0.056054 | 0.056066 | 0.05617 | 0.056127 | 0.055946 | 0.05589 | 0.055862 | 0.056451 | 0.056187 | 0.056077 | 0.055803 | 0.05558 | 0.05558 | 0.055482 | 0.055791 | 0.055725 | 0.058187 | 0.058225 | 0.058207 | 0.058031 | 0.058001 | 0.057827 | 0.0578 | 0.059809 | 0.059879 | 0.059604 | 0.064409 | 0.064144 | 0.064517 | 0.059071 | 0.059103 | 0.059111 | 0.059419 | 0.059696 | 0.059783 | 0.058182 | 0.058449 | 0.058329 | 0.05863 | 0.058643 | 0.058766 | 0.056977 | 0.056809 | 0.056835 | 0.05678 | 0.056433 | 0.056363 | 0.056282 | 0.056417 | 0.056507 | 0.055367 | 0.055372 | 0.055571 | 0.055911 | 0.0557 | 0.055782 | 0.056104 | 0.055864 | 0.055851 | 0.055918 | 0.055896 | 0.055794 | 0.055778 | 0.055797 | 0.05567 | 0.058599 | 0.05874 | 0.058776 | 0.058439 | 0.058443 | 0.058472 | 0.058576 | 0.060231 | 0.0602 | 0.060176 | 0.060184 | 0.06017 | 0.060165 | 0.060101 | 0.060176 | 0.064503 | 0.064808 | 0.06457 | 0.05966 | 0.059535 | 0.059626 | 0.059781 | 0.059761 | 0.059649 | 0.064049 | 0.063931 | 0.06409 | 0.058544 | 0.058528 | 0.058713 | 0.05864 | 0.058641 | 0.058711 | 0.056295 | 0.056368 | 0.056473 | 0.056033 | 0.055931 | 0.055731 | 0.055543 | 0.055671 | 0.05789 | 0.057932 | 0.057619 | 0.055883 | 0.055855 | 0.055859 | 0.055606 | 0.055793 | 0.055728 | 0.055799 | 0.059259 | 0.059343 | 0.059169 | 0.055929 | 0.055647 | 0.055694 | 0.055612 | 0.060312 | 0.060198 | 0.060163 | 0.060381 | 0.059391 | 0.059466 | 0.059491 | 0.060956 | 0.061055 | 0.060546 | 0.061512 | 0.061402 | 0.061578 | 0.061604 | 0.061482 | 0.061351 | 0.0614 | 0.061331 | 0.064173 | 0.06417 | 0.06436 | 0.058919 | 0.059205 | 0.059323 | 0.059689 | 0.059749 | 0.059765 | 0.059532 | 0.059989 | 0.059576 | 0.0561 | 0.056039 | 0.05638 | 0.06393 | 0.063809 | 0.063756 | 0.058907 | 0.058992 | 0.058889 | 0.059501 | 0.059221 | 0.059136 | 0.05949 | 0.059731 | 0.05975 | 0.055959 | 0.055892 | 0.055909 | 0.056314 | 0.056444 | 0.056736 | 0.056591 | 0.056578 | 0.056396 | 0.055839 | 0.055862 | 0.055638 | 0.056009 | 0.055897 | 0.055915 | 0.058372 | 0.058266 | 0.058289 | 0.058206 | 0.058135 | 0.057988 | 0.064432 | 0.064207 | 0.063778 | 0.059026 | 0.058994 | 0.059227 | 0.059045 | 0.059003 | 0.059132 | 0.059878 | 0.060465 | 0.060101 | 0.056583 | 0.056621 | 0.056416 | 0.059689 | 0.059638 | 0.059866 | 0.059752 | 0.059619 | 0.059469
96 | Suction orifice Plate pipe dia | m | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | 0.15
97 | Suction orifice plate orifice dia | m | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1
98 | Suction orifice plate Gamma (cp/cv) | - | 1.1904 | 1.1906 | 1.1906 | 1.1791 | 1.1799 | 1.1827 | 1.1711 | 1.1729 | 1.1738 | 1.1669 | 1.1663 | 1.1673 | 1.1582 | 1.1583 | 1.1584 | 1.1709 | 1.1708 | 1.1702 | 1.1707 | 1.1708 | 1.1707 | 1.171 | 1.1706 | 1.1704 | 1.1705 | 1.1706 | 1.1706 | 1.1733 | 1.1728 | 1.1728 | 1.1732 | 1.1735 | 1.1738 | 1.1715 | 1.1721 | 1.1725 | 1.1748 | 1.1755 | 1.1755 | 1.1754 | 1.1746 | 1.174 | 1.1724 | 1.1723 | 1.1727 | 1.1732 | 1.1727 | 1.1731 | 1.1733 | 1.1724 | 1.1724 | 1.1731 | 1.1688 | 1.1701 | 1.1681 | 1.1732 | 1.1732 | 1.1731 | 1.1726 | 1.1705 | 1.1694 | 1.1721 | 1.1714 | 1.1717 | 1.1686 | 1.1687 | 1.1686 | 1.1675 | 1.1678 | 1.168 | 1.1692 | 1.1698 | 1.1701 | 1.1705 | 1.1704 | 1.1703 | 1.1737 | 1.1738 | 1.1739 | 1.1705 | 1.1714 | 1.1714 | 1.1722 | 1.1732 | 1.1734 | 1.1741 | 1.1741 | 1.1742 | 1.1741 | 1.1742 | 1.1745 | 1.1692 | 1.1692 | 1.1694 | 1.1701 | 1.1703 | 1.1706 | 1.1695 | 1.1706 | 1.1707 | 1.1707 | 1.1706 | 1.1706 | 1.1705 | 1.1704 | 1.1698 | 1.1683 | 1.1675 | 1.1688 | 1.1711 | 1.1713 | 1.1712 | 1.1701 | 1.1704 | 1.1708 | 1.1701 | 1.1701 | 1.1697 | 1.1695 | 1.1697 | 1.1694 | 1.169 | 1.169 | 1.1689 | 1.1708 | 1.1702 | 1.1696 | 1.1711 | 1.1712 | 1.1714 | 1.1723 | 1.1723 | 1.1725 | 1.1726 | 1.1737 | 1.1731 | 1.1733 | 1.1734 | 1.1743 | 1.1734 | 1.1734 | 1.1732 | 1.1687 | 1.1686 | 1.1688 | 1.1722 | 1.1714 | 1.1713 | 1.1717 | 1.1713 | 1.171 | 1.1706 | 1.1703 | 1.1727 | 1.1711 | 1.1707 | 1.1643 | 1.1637 | 1.1648 | 1.1608 | 1.1609 | 1.1608 | 1.1608 | 1.161 | 1.1612 | 1.1612 | 1.1613 | 1.1686 | 1.1682 | 1.168 | 1.1732 | 1.1726 | 1.1714 | 1.1698 | 1.1695 | 1.1692 | 1.1729 | 1.1715 | 1.1728 | 1.1719 | 1.1722 | 1.1716 | 1.1697 | 1.1701 | 1.1704 | 1.1732 | 1.1735 | 1.1742 | 1.171 | 1.1717 | 1.1717 | 1.1728 | 1.1723 | 1.1722 | 1.1733 | 1.1734 | 1.1737 | 1.1708 | 1.1703 | 1.169 | 1.1694 | 1.17 | 1.1707 | 1.172 | 1.1717 | 1.1719 | 1.1714 | 1.172 | 1.1721 | 1.1715 | 1.1717 | 1.1717 | 1.1707 | 1.171 | 1.1718 | 1.1677 | 1.1694 | 1.1716 | 1.1736 | 1.1739 | 1.1735 | 1.1736 | 1.1741 | 1.1738 | 1.1703 | 1.1681 | 1.1695 | 1.1698 | 1.17 | 1.1705 | 1.1701 | 1.1702 | 1.1697 | 1.1696 | 1.1698 | 1.1711
99 | Suction flow Viscosity | N.S/m^2 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05 | 1e-05
100 | Suction orifice plate vol Flow | m^3/hr | 956.8732 | 959.4402 | 956.2754 | 952.1819 | 955.8294 | 951.6416 | 945.5176 | 945.0445 | 948.8108 | 933.4887 | 939.5597 | 932.3459 | 927.5628 | 927.7026 | 924.8018 | 73.1029 | 82.6374 | 79.3626 | 95.4321 | 89.8307 | 94.989 | 82.6284 | 80.1533 | 81.5346 | 95.2915 | 95.7753 | 98.1505 | 311.1411 | 310.8457 | 312.5279 | 311.0044 | 312.3519 | 310.6647 | 339.3917 | 340.7819 | 340.5919 | 338.8302 | 339.5582 | 340.372 | 359.9309 | 361.0563 | 361.74 | 578.5677 | 576.9695 | 579.2308 | 583.451 | 617.4627 | 616.3496 | 615.8933 | 881.4512 | 880.4557 | 880.7157 | 939.8849 | 939.059 | 940.0087 | 943.4292 | 947.1154 | 942.5467 | 942.7605 | 944.2994 | 947.8382 | 574.6581 | 573.8309 | 574.6278 | 610.2265 | 608.6315 | 609.0118 | 356.5127 | 353.5141 | 355.4337 | 306.2441 | 304.6454 | 305.7578 | 306.6587 | 305.8389 | 303.9101 | 82.7 | 82.6404 | 85.3794 | 104.7675 | 102.7379 | 105.3421 | 307.5694 | 307.4741 | 307.1227 | 334.4468 | 334.2507 | 337.661 | 336.5219 | 334.7497 | 335.0466 | 583.4045 | 585.0762 | 584.454 | 614.8399 | 609.8518 | 610.249 | 600.4497 | 864.8436 | 865.8893 | 865.9116 | 868.9769 | 864.8152 | 865.8486 | 864.3862 | 868.2314 | 923.2561 | 924.9799 | 922.1822 | 928.0772 | 927.373 | 930.9723 | 931.064 | 930.2241 | 932.0654 | 902.0713 | 903.5524 | 902.7213 | 555.6527 | 556.4233 | 556.9882 | 561.6205 | 561.7302 | 564.0836 | 295.7721 | 294.4516 | 293.487 | 70.6845 | 76.1736 | 75.3322 | 83.9721 | 91.8938 | 595.1832 | 592.89 | 591.8571 | 323.0684 | 325.9548 | 325.9324 | 325.3652 | 346.1992 | 345.4859 | 345.1844 | 341.4572 | 340.4612 | 342.2907 | 88.176 | 87.549 | 86.8096 | 86.4196 | 845.0474 | 847.9179 | 845.7364 | 848.468 | 908.4517 | 911.8905 | 910.4331 | 917.9765 | 920.1983 | 917.6681 | 923.2576 | 924.7921 | 922.0772 | 923.5643 | 921.1725 | 923.9756 | 921.1849 | 923.1526 | 922.8406 | 921.9794 | 924.2571 | 931.8863 | 928.5217 | 930.2994 | 930.8562 | 932.067 | 930.161 | 861.7824 | 862.9204 | 865.9745 | 351.3784 | 350.8211 | 354.1444 | 925.0953 | 925.457 | 926.0001 | 934.155 | 931.198 | 932.4256 | 935.8318 | 932.5448 | 933.1161 | 866.543 | 865.652 | 865.9273 | 354.7752 | 353.4854 | 356.6854 | 338.1214 | 335.2959 | 335.5387 | 309.9227 | 305.6289 | 307.3303 | 71.7296 | 72.2577 | 79.2161 | 87.3579 | 92.1952 | 93.5806 | 585.5386 | 582.9728 | 580.896 | 615.7726 | 616.7291 | 614.8665 | 930.0312 | 929.8977 | 928.7812 | 934.7856 | 936.7192 | 934.7056 | 933.5116 | 934.7915 | 934.0054 | 867.4639 | 869.1334 | 870.2708 | 356.9411 | 354.7977 | 356.7125 | 936.4167 | 934.7231 | 933.3509 | 934.7667 | 933.8577 | 933.3913
101 | Suction orifice plate mass Flow | kg/s | 6.4496 | 6.4731 | 6.4302 | 5.429 | 5.4621 | 5.4796 | 4.5334 | 4.5848 | 4.6118 | 3.8116 | 3.8264 | 3.8052 | 3.1305 | 3.1288 | 3.1174 | 0.36234 | 0.40937 | 0.39196 | 0.47332 | 0.44563 | 0.47084 | 0.40894 | 0.39612 | 0.4034 | 0.47127 | 0.47464 | 0.48639 | 1.5415 | 1.5372 | 1.5467 | 1.5442 | 1.5524 | 1.5448 | 1.6701 | 1.6848 | 1.6871 | 1.6866 | 1.697 | 1.7011 | 1.8021 | 1.7977 | 1.8032 | 2.762 | 2.7526 | 2.7642 | 2.7928 | 2.9571 | 2.9607 | 2.9599 | 4.0938 | 4.0844 | 4.1045 | 4.0535 | 4.0666 | 4.0472 | 4.4365 | 4.4514 | 4.4293 | 4.4073 | 4.394 | 4.4041 | 2.7436 | 2.7271 | 2.7365 | 2.8911 | 2.8829 | 2.8787 | 1.7381 | 1.7286 | 1.7371 | 1.4982 | 1.4996 | 1.5069 | 1.5135 | 1.5058 | 1.494 | 0.41491 | 0.41457 | 0.42678 | 0.52051 | 0.51236 | 0.52457 | 1.5228 | 1.5289 | 1.5275 | 1.6614 | 1.6611 | 1.6811 | 1.6759 | 1.6665 | 1.6718 | 2.7655 | 2.7668 | 2.7622 | 2.9225 | 2.8986 | 2.8991 | 2.8475 | 3.9886 | 3.9954 | 3.9971 | 4.0107 | 3.9925 | 3.9976 | 3.9951 | 4.0078 | 3.976 | 3.9646 | 3.9672 | 4.3212 | 4.3269 | 4.3371 | 4.3263 | 4.3238 | 4.3405 | 3.9123 | 3.9259 | 3.9126 | 2.6364 | 2.6408 | 2.6352 | 2.6604 | 2.6609 | 2.6688 | 1.4594 | 1.451 | 1.4436 | 0.35041 | 0.37831 | 0.37548 | 0.41995 | 0.45852 | 2.8559 | 2.8428 | 2.8533 | 1.6059 | 1.621 | 1.6208 | 1.6254 | 1.7236 | 1.7221 | 1.7184 | 1.6006 | 1.5937 | 1.6069 | 0.43793 | 0.43702 | 0.43297 | 0.43166 | 3.892 | 3.9126 | 3.9049 | 3.9033 | 4.2489 | 4.2596 | 4.2511 | 4.1833 | 4.1866 | 4.2102 | 4.1693 | 4.1837 | 4.1595 | 4.1644 | 4.1619 | 4.1834 | 4.1675 | 4.1811 | 3.9946 | 3.991 | 3.9891 | 4.3934 | 4.3565 | 4.3561 | 4.332 | 4.3332 | 4.3232 | 4.0211 | 3.9957 | 4.0377 | 1.7398 | 1.739 | 1.7448 | 4.0196 | 4.0288 | 4.0345 | 4.405 | 4.3848 | 4.3982 | 4.3689 | 4.3741 | 4.3831 | 4.0462 | 4.0257 | 4.0257 | 1.7611 | 1.7568 | 1.7722 | 1.6678 | 1.6501 | 1.6428 | 1.5213 | 1.5005 | 1.5137 | 0.35683 | 0.35931 | 0.39549 | 0.43326 | 0.45816 | 0.4649 | 2.7865 | 2.7793 | 2.7683 | 2.9387 | 2.9468 | 2.9454 | 4.0095 | 4.023 | 4.0452 | 4.3991 | 4.4106 | 4.3838 | 4.3917 | 4.4008 | 4.3876 | 4.0242 | 3.9928 | 4.0223 | 1.7523 | 1.7406 | 1.7564 | 4.3578 | 4.3537 | 4.3307 | 4.3456 | 4.351 | 4.3598
102
103
104 | Suction Temp | ºC | 25.0492 | 24.9605 | 24.7684 | 21.3108 | 20.8375 | 19.4422 | 16.3206 | 15.6208 | 15.0402 | 10.098 | 10.5134 | 9.7332 | 7.3524 | 7.2084 | 7.0618 | 18.4808 | 18.5859 | 18.8415 | 18.684 | 18.6889 | 18.6476 | 18.323 | 18.6046 | 18.8127 | 18.7143 | 18.7131 | 18.7292 | 16.6336 | 16.8627 | 16.9105 | 16.7911 | 16.6719 | 16.4341 | 17.5757 | 17.3977 | 17.2151 | 15.7404 | 15.4801 | 15.5112 | 15.6782 | 15.91 | 16.4212 | 15.0114 | 15.0351 | 14.7431 | 14.5322 | 14.934 | 14.876 | 14.748 | 13.313 | 13.2327 | 12.9854 | 11.7386 | 10.9293 | 12.2237 | 13.463 | 13.4539 | 13.5436 | 13.5748 | 14.9419 | 15.7748 | 15.2453 | 15.4783 | 15.4345 | 17.5607 | 17.521 | 17.4276 | 20.2842 | 20.2017 | 20.063 | 19.0741 | 18.9792 | 18.8013 | 18.5706 | 18.4883 | 18.493 | 17.1189 | 17.0125 | 16.7228 | 18.9759 | 18.5056 | 18.4042 | 17.3922 | 16.9391 | 16.7895 | 16.1943 | 16.1802 | 16.1937 | 16.3087 | 16.2008 | 16.1704 | 17.1666 | 17.0217 | 16.8172 | 16.5701 | 16.3831 | 16.1233 | 16.9093 | 14.3163 | 14.3056 | 14.2855 | 14.3732 | 14.3977 | 14.4554 | 14.6297 | 14.9905 | 12.1148 | 12.491 | 11.6225 | 14.4707 | 14.4767 | 14.447 | 15.2061 | 14.9845 | 14.7759 | 11.0711 | 11.1825 | 11.2949 | 16.9689 | 16.7949 | 16.82 | 17.2337 | 17.2418 | 17.2429 | 18.3113 | 18.719 | 19.14 | 18.3754 | 18.4238 | 18.4575 | 17.928 | 17.8053 | 15.2657 | 15.1213 | 14.6392 | 16.9474 | 16.8708 | 16.7454 | 16.3672 | 16.8494 | 16.8831 | 16.9756 | 16.818 | 16.8359 | 16.894 | 17.6224 | 18.5485 | 18.5994 | 18.336 | 13.6671 | 14.0142 | 14.3711 | 14.4289 | 13.5508 | 14.6941 | 15.0175 | 18.91 | 19.3815 | 18.9184 | 21.6936 | 21.6804 | 21.6293 | 21.5924 | 21.5042 | 21.445 | 21.4117 | 21.3538 | 12.1552 | 12.4514 | 12.4251 | 13.616 | 13.7924 | 14.5835 | 15.4833 | 15.6995 | 15.957 | 13.1966 | 13.8774 | 13.2902 | 17.6319 | 17.477 | 17.6169 | 11.4366 | 11.2606 | 11.0319 | 13.6057 | 13.3032 | 12.8859 | 14.7596 | 14.4407 | 14.5919 | 13.3308 | 13.5145 | 13.5078 | 16.7238 | 16.7508 | 16.4436 | 18.3129 | 18.5421 | 19.3375 | 19.1512 | 18.6899 | 18.3133 | 17.8738 | 18.0498 | 18.1805 | 18.1335 | 17.8199 | 17.7217 | 15.4962 | 15.4738 | 15.4137 | 16.3355 | 16.1358 | 15.6846 | 12.61 | 11.434 | 10.0759 | 13.2532 | 13.0466 | 13.0493 | 13.1758 | 12.8939 | 12.9535 | 14.8885 | 16.1038 | 15.307 | 18.7739 | 18.5876 | 18.4132 | 15.277 | 15.2205 | 15.4129 | 15.5764 | 15.5655 | 14.7076
105 | Suction Pressure | BarA | 4.8908 | 4.8901 | 4.8736 | 4.1496 | 4.1497 | 4.1475 | 3.4835 | 3.5021 | 3.4986 | 2.9254 | 2.9281 | 2.9249 | 2.4361 | 2.4323 | 2.4294 | 3.8522 | 3.849 | 3.8449 | 3.8544 | 3.8588 | 3.8543 | 3.8415 | 3.8428 | 3.8523 | 3.8478 | 3.8524 | 3.8511 | 3.794 | 3.7928 | 3.7991 | 3.8074 | 3.807 | 3.8043 | 3.7863 | 3.7985 | 3.8009 | 3.7934 | 3.802 | 3.8037 | 3.8084 | 3.7946 | 3.8045 | 3.5977 | 3.5977 | 3.5913 | 3.5993 | 3.5952 | 3.6062 | 3.6023 | 3.3771 | 3.3717 | 3.3812 | 3.1083 | 3.1091 | 3.1114 | 3.3808 | 3.3763 | 3.378 | 3.3679 | 3.3725 | 3.377 | 3.5968 | 3.5873 | 3.5884 | 3.6017 | 3.5943 | 3.5891 | 3.7889 | 3.7995 | 3.794 | 3.7862 | 3.8072 | 3.807 | 3.811 | 3.7996 | 3.7987 | 3.8575 | 3.8547 | 3.8411 | 3.8506 | 3.8567 | 3.8494 | 3.799 | 3.8079 | 3.8029 | 3.7896 | 3.7916 | 3.8008 | 3.7998 | 3.7963 | 3.8064 | 3.6017 | 3.5936 | 3.5869 | 3.5897 | 3.5944 | 3.587 | 3.594 | 3.3789 | 3.3815 | 3.3771 | 3.3791 | 3.3818 | 3.3835 | 3.3868 | 3.3888 | 3.1203 | 3.1137 | 3.1083 | 3.3788 | 3.3818 | 3.3794 | 3.38 | 3.378 | 3.3809 | 3.1144 | 3.1155 | 3.1128 | 3.5974 | 3.5923 | 3.5883 | 3.5973 | 3.5935 | 3.5906 | 3.8027 | 3.8042 | 3.8035 | 3.8404 | 3.8418 | 3.8577 | 3.8611 | 3.8468 | 3.5918 | 3.5918 | 3.5974 | 3.7965 | 3.8012 | 3.7992 | 3.8079 | 3.7993 | 3.8028 | 3.8017 | 3.6002 | 3.591 | 3.6037 | 3.8266 | 3.857 | 3.8543 | 3.8554 | 3.3572 | 3.3671 | 3.3747 | 3.365 | 3.3672 | 3.383 | 3.3887 | 3.3732 | 3.3736 | 3.3916 | 3.3847 | 3.3921 | 3.3787 | 3.3781 | 3.3858 | 3.3898 | 3.3829 | 3.3872 | 3.1149 | 3.1188 | 3.1122 | 3.384 | 3.3732 | 3.3782 | 3.3736 | 3.369 | 3.3743 | 3.3834 | 3.3709 | 3.3776 | 3.803 | 3.8043 | 3.788 | 3.1147 | 3.116 | 3.1191 | 3.3869 | 3.3778 | 3.3733 | 3.37 | 3.3797 | 3.3825 | 3.3777 | 3.373 | 3.3691 | 3.79 | 3.8016 | 3.7897 | 3.8016 | 3.8004 | 3.7965 | 3.8041 | 3.7984 | 3.7979 | 3.852 | 3.8523 | 3.8661 | 3.8482 | 3.8472 | 3.844 | 3.5865 | 3.5939 | 3.5897 | 3.6003 | 3.5993 | 3.5985 | 3.1162 | 3.1087 | 3.1058 | 3.3819 | 3.3775 | 3.3687 | 3.3765 | 3.3746 | 3.3702 | 3.3889 | 3.3777 | 3.381 | 3.792 | 3.7928 | 3.7994 | 3.378 | 3.3731 | 3.3674 | 3.374 | 3.3809 | 3.3759
106 | Suction SH | ºC | 10.0042 | 9.9201 | 9.8332 | 11.2851 | 10.8111 | 9.432 | 11.4288 | 10.5758 | 10.0236 | 10.1228 | 10.5129 | 9.7624 | 12.3236 | 12.2201 | 12.1061 | 10.6629 | 10.7922 | 11.0799 | 10.8494 | 10.8205 | 10.8135 | 10.5871 | 10.859 | 10.9945 | 10.9299 | 10.8939 | 10.9201 | 9.2627 | 9.5011 | 9.5001 | 9.3169 | 9.201 | 8.9837 | 10.265 | 9.9926 | 9.7912 | 8.3744 | 8.048 | 8.0656 | 8.1963 | 8.5344 | 8.9697 | 9.1889 | 9.2126 | 8.9719 | 8.6967 | 9.1314 | 8.9846 | 8.8883 | 9.3092 | 9.2742 | 8.9467 | 10.0784 | 9.2618 | 10.5352 | 9.4275 | 9.4569 | 9.5321 | 9.6483 | 10.9766 | 11.7718 | 9.4295 | 9.7396 | 9.6865 | 11.7056 | 11.726 | 11.674 | 12.9533 | 12.7888 | 12.6923 | 11.7635 | 11.5063 | 11.3301 | 11.0687 | 11.0747 | 11.0859 | 9.2609 | 9.1758 | 8.9897 | 11.1705 | 10.6531 | 10.6074 | 9.9831 | 9.4613 | 9.3503 | 8.8574 | 8.8284 | 8.7703 | 8.893 | 8.8127 | 8.7044 | 11.3115 | 11.2317 | 11.0813 | 10.8116 | 10.5869 | 10.387 | 11.1162 | 10.2972 | 10.2646 | 10.2818 | 10.352 | 10.3537 | 10.3973 | 10.5441 | 10.8877 | 10.3469 | 10.7823 | 9.9621 | 10.4527 | 10.4328 | 10.4233 | 11.178 | 10.9729 | 10.7394 | 9.3561 | 9.4578 | 9.5938 | 11.149 | 11.0158 | 11.073 | 11.4144 | 11.4532 | 11.477 | 10.8738 | 11.2698 | 11.6959 | 10.6476 | 10.6856 | 10.5975 | 10.0422 | 10.029 | 9.4905 | 9.3458 | 8.8189 | 9.5578 | 9.4444 | 9.3344 | 8.8894 | 9.4378 | 9.4443 | 9.5455 | 10.9755 | 11.067 | 11.0231 | 10.001 | 10.694 | 10.7658 | 10.494 | 9.8315 | 10.0948 | 10.3873 | 10.5276 | 9.6302 | 10.6404 | 10.9159 | 14.939 | 15.4072 | 14.7917 | 17.6256 | 17.5501 | 17.6117 | 17.58 | 17.4269 | 17.3341 | 17.3591 | 17.2641 | 10.4357 | 10.6962 | 10.7296 | 9.5537 | 9.8212 | 10.5705 | 11.509 | 11.7638 | 11.9763 | 9.1395 | 9.9261 | 9.2822 | 10.1917 | 10.0266 | 10.2927 | 9.7184 | 9.5313 | 9.2746 | 9.5186 | 9.2937 | 8.9144 | 10.8157 | 10.4146 | 10.5421 | 9.3214 | 9.5454 | 9.5714 | 9.3838 | 9.3217 | 9.1065 | 10.8836 | 11.1218 | 11.9472 | 11.7024 | 11.2851 | 10.9128 | 10.0575 | 10.2315 | 10.2563 | 10.3459 | 10.0403 | 9.9667 | 9.7641 | 9.6814 | 9.6553 | 10.4915 | 10.3002 | 9.8552 | 10.8786 | 9.7704 | 8.4378 | 9.2086 | 9.0391 | 9.1167 | 9.1771 | 8.9107 | 9.0079 | 10.7852 | 12.0946 | 11.2698 | 11.4184 | 11.2262 | 11.0012 | 11.2656 | 11.2507 | 11.491 | 11.5988 | 11.5299 | 10.7134
107 | Suction Gauge | ºC | 15.045 | 15.0404 | 14.9352 | 10.0257 | 10.0264 | 10.0102 | 4.8919 | 5.045 | 5.0166 | -0.024873 | 0.0005201 | -0.029269 | -4.9711 | -5.0117 | -5.0443 | 7.8179 | 7.7937 | 7.7616 | 7.8346 | 7.8684 | 7.8341 | 7.7359 | 7.7456 | 7.8182 | 7.7844 | 7.8192 | 7.8091 | 7.3709 | 7.3616 | 7.4104 | 7.4741 | 7.471 | 7.4504 | 7.3107 | 7.4051 | 7.424 | 7.366 | 7.4322 | 7.4456 | 7.4819 | 7.3756 | 7.4516 | 5.8226 | 5.8226 | 5.7712 | 5.8355 | 5.8026 | 5.8914 | 5.8597 | 4.0038 | 3.9585 | 4.0387 | 1.6602 | 1.6676 | 1.6885 | 4.0355 | 3.9971 | 4.0115 | 3.9265 | 3.9654 | 4.003 | 5.8159 | 5.7387 | 5.7481 | 5.855 | 5.795 | 5.7536 | 7.3309 | 7.4129 | 7.3707 | 7.3106 | 7.4729 | 7.4713 | 7.5019 | 7.4136 | 7.4071 | 7.8581 | 7.8367 | 7.733 | 7.8054 | 7.8525 | 7.7967 | 7.4091 | 7.4779 | 7.4393 | 7.337 | 7.3518 | 7.4234 | 7.4157 | 7.3881 | 7.4661 | 5.8551 | 5.79 | 5.7359 | 5.7585 | 5.7962 | 5.7363 | 5.7931 | 4.0191 | 4.041 | 4.0037 | 4.0212 | 4.044 | 4.0581 | 4.0857 | 4.1028 | 1.7679 | 1.7087 | 1.6604 | 4.018 | 4.0439 | 4.0237 | 4.0281 | 4.0116 | 4.0364 | 1.7149 | 1.7248 | 1.7011 | 5.8199 | 5.7791 | 5.747 | 5.8193 | 5.7885 | 5.7659 | 7.4376 | 7.4492 | 7.4441 | 7.7278 | 7.7381 | 7.86 | 7.8858 | 7.7763 | 5.7751 | 5.7756 | 5.8203 | 7.3896 | 7.4265 | 7.411 | 7.4778 | 7.4116 | 7.4388 | 7.4301 | 5.8425 | 5.7689 | 5.8709 | 7.6214 | 7.8545 | 7.8336 | 7.8419 | 3.8356 | 3.9195 | 3.9838 | 3.9014 | 3.9206 | 4.0538 | 4.1016 | 3.971 | 3.9743 | 4.1267 | 4.068 | 4.1303 | 4.0176 | 4.0123 | 4.0773 | 4.1109 | 4.0527 | 4.0896 | 1.7195 | 1.7552 | 1.6955 | 4.0623 | 3.9712 | 4.013 | 3.9743 | 3.9357 | 3.9807 | 4.0571 | 3.9514 | 4.0081 | 7.4402 | 7.4504 | 7.3242 | 1.7182 | 1.7293 | 1.7573 | 4.0871 | 4.0095 | 3.9715 | 3.9439 | 4.0261 | 4.0498 | 4.0094 | 3.9691 | 3.9364 | 7.34 | 7.4291 | 7.3371 | 7.4293 | 7.4202 | 7.3903 | 7.4488 | 7.4048 | 7.4005 | 7.8163 | 7.8183 | 7.9242 | 7.7876 | 7.7795 | 7.755 | 5.7321 | 5.7925 | 5.7584 | 5.844 | 5.8357 | 5.8295 | 1.7314 | 1.6637 | 1.6382 | 4.0446 | 4.0075 | 3.9326 | 3.9987 | 3.9832 | 3.9456 | 4.1033 | 4.0092 | 4.0372 | 7.3554 | 7.3613 | 7.412 | 4.0114 | 3.9698 | 3.9219 | 3.9776 | 4.0357 | 3.9942
108 | Suction Enthalpy | KJ/kg | 416.6953 | 416.6126 | 416.4678 | 414.8768 | 414.4376 | 413.1479 | 411.8455 | 411.167 | 410.6484 | 407.6077 | 407.9697 | 407.2851 | 406.4045 | 406.2886 | 406.1686 | 412.9525 | 413.0565 | 413.3009 | 413.134 | 413.1282 | 413.1008 | 412.8327 | 413.0883 | 413.2572 | 413.1772 | 413.1655 | 413.1833 | 411.3944 | 411.6075 | 411.6363 | 411.5069 | 411.3985 | 411.1866 | 412.2769 | 412.0848 | 411.9116 | 410.576 | 410.3161 | 410.3404 | 410.4824 | 410.7288 | 411.1744 | 410.3837 | 410.4053 | 410.1546 | 409.943 | 410.3191 | 410.2395 | 410.1324 | 409.3784 | 409.3189 | 409.0721 | 408.6197 | 407.8941 | 409.0457 | 409.5047 | 409.5076 | 409.5845 | 409.6371 | 410.8605 | 411.6019 | 410.5988 | 410.834 | 410.7913 | 412.6953 | 412.6765 | 412.6035 | 414.7517 | 414.6521 | 414.5375 | 413.6497 | 413.5144 | 413.3518 | 413.131 | 413.0822 | 413.0885 | 411.6885 | 411.5973 | 411.3634 | 413.411 | 412.9647 | 412.8886 | 412.0786 | 411.6417 | 411.5163 | 411.0019 | 410.9843 | 410.9743 | 411.0823 | 410.9918 | 410.9396 | 412.3366 | 412.2237 | 412.0534 | 411.8219 | 411.6407 | 411.4218 | 412.1205 | 410.2804 | 410.2645 | 410.257 | 410.3312 | 410.3468 | 410.395 | 410.5446 | 410.8656 | 408.9269 | 409.2793 | 408.5159 | 410.4202 | 410.4182 | 410.3971 | 411.0814 | 410.8859 | 410.6906 | 408.0078 | 408.1048 | 408.2118 | 412.1669 | 412.0205 | 412.0527 | 412.408 | 412.4243 | 412.4319 | 412.9127 | 413.283 | 413.6703 | 412.8833 | 412.9246 | 412.9183 | 412.4238 | 412.3448 | 410.6295 | 410.4979 | 410.0451 | 411.6766 | 411.5949 | 411.4846 | 411.1166 | 411.5799 | 411.6023 | 411.6899 | 412.023 | 412.0608 | 412.0838 | 412.2246 | 413.0035 | 413.0567 | 412.8122 | 409.7464 | 410.036 | 410.3399 | 410.4155 | 409.6171 | 410.6118 | 410.8904 | 414.4393 | 414.8638 | 414.4055 | 416.9257 | 416.8978 | 416.8806 | 416.8486 | 416.7523 | 416.6903 | 416.6752 | 416.6134 | 408.9761 | 409.2313 | 409.2239 | 409.6353 | 409.8208 | 410.5235 | 411.3467 | 411.5526 | 411.7725 | 409.2577 | 409.9033 | 409.3565 | 412.2889 | 412.1437 | 412.3106 | 408.3339 | 408.1734 | 407.9611 | 409.6189 | 409.3679 | 409.0017 | 410.702 | 410.3908 | 410.5206 | 409.3928 | 409.5704 | 409.5737 | 411.4868 | 411.4839 | 411.2306 | 412.9167 | 413.1295 | 413.8673 | 413.6792 | 413.2696 | 412.9258 | 412.3954 | 412.5565 | 412.644 | 412.6428 | 412.3572 | 412.2746 | 410.8522 | 410.8139 | 410.7693 | 411.5833 | 411.404 | 410.9949 | 409.3795 | 408.3465 | 407.1389 | 409.3125 | 409.1365 | 409.1607 | 409.2558 | 409.0055 | 409.0704 | 410.7734 | 411.8971 | 411.17 | 413.3614 | 413.1889 | 413.0139 | 411.1501 | 411.1108 | 411.2978 | 411.4298 | 411.4038 | 410.6409
109 | Suction specific volume | m3/kg | 0.044354 | 0.044341 | 0.044468 | 0.052375 | 0.052252 | 0.051925 | 0.062061 | 0.061492 | 0.061388 | 0.07294 | 0.07301 | 0.072827 | 0.087775 | 0.087862 | 0.087919 | 0.056113 | 0.056193 | 0.056331 | 0.056133 | 0.056063 | 0.056124 | 0.056244 | 0.0563 | 0.056203 | 0.056248 | 0.056174 | 0.056199 | 0.056557 | 0.05664 | 0.056549 | 0.05638 | 0.056353 | 0.056331 | 0.056947 | 0.056695 | 0.056604 | 0.056318 | 0.056105 | 0.056085 | 0.056054 | 0.056345 | 0.056325 | 0.059515 | 0.059521 | 0.059553 | 0.059346 | 0.059538 | 0.059319 | 0.059354 | 0.063295 | 0.063382 | 0.06311 | 0.068804 | 0.068519 | 0.068886 | 0.063264 | 0.063355 | 0.063347 | 0.063565 | 0.063887 | 0.064047 | 0.059598 | 0.059841 | 0.059807 | 0.060176 | 0.060303 | 0.060371 | 0.057649 | 0.057449 | 0.057502 | 0.057361 | 0.056985 | 0.05694 | 0.056811 | 0.056978 | 0.056993 | 0.055656 | 0.055672 | 0.055811 | 0.056274 | 0.056047 | 0.056137 | 0.056685 | 0.056413 | 0.056454 | 0.056507 | 0.056471 | 0.056322 | 0.056371 | 0.0564 | 0.056225 | 0.060063 | 0.06017 | 0.060235 | 0.060112 | 0.059972 | 0.060034 | 0.060131 | 0.063564 | 0.063508 | 0.063593 | 0.063577 | 0.063528 | 0.063511 | 0.063497 | 0.063565 | 0.068638 | 0.068919 | 0.068765 | 0.063614 | 0.063553 | 0.063593 | 0.063813 | 0.063786 | 0.063662 | 0.068438 | 0.068448 | 0.068549 | 0.060087 | 0.06013 | 0.060211 | 0.060164 | 0.060237 | 0.06029 | 0.056878 | 0.056965 | 0.057091 | 0.056275 | 0.056267 | 0.056018 | 0.055819 | 0.056017 | 0.059696 | 0.059654 | 0.059411 | 0.056604 | 0.056504 | 0.056502 | 0.056254 | 0.056529 | 0.056481 | 0.056525 | 0.059992 | 0.060165 | 0.059949 | 0.056295 | 0.056054 | 0.056112 | 0.056023 | 0.063817 | 0.063717 | 0.063668 | 0.063888 | 0.063572 | 0.063595 | 0.063576 | 0.065071 | 0.065204 | 0.064687 | 0.065657 | 0.065498 | 0.065764 | 0.065767 | 0.065578 | 0.065477 | 0.065612 | 0.065503 | 0.068781 | 0.068781 | 0.068933 | 0.063245 | 0.063522 | 0.063661 | 0.064029 | 0.06419 | 0.064157 | 0.06313 | 0.063597 | 0.063278 | 0.056685 | 0.05662 | 0.05693 | 0.068549 | 0.068462 | 0.068312 | 0.063182 | 0.063278 | 0.063243 | 0.063884 | 0.063585 | 0.063573 | 0.063287 | 0.063442 | 0.06352 | 0.056648 | 0.056465 | 0.056576 | 0.056896 | 0.056978 | 0.057261 | 0.057084 | 0.057052 | 0.056958 | 0.055951 | 0.055995 | 0.055807 | 0.056082 | 0.056014 | 0.056039 | 0.059862 | 0.059717 | 0.059778 | 0.059849 | 0.05981 | 0.059694 | 0.068897 | 0.068695 | 0.068316 | 0.063178 | 0.063205 | 0.063389 | 0.063266 | 0.063217 | 0.063327 | 0.063532 | 0.064131 | 0.063821 | 0.057182 | 0.057118 | 0.056961 | 0.063876 | 0.063961 | 0.064137 | 0.06405 | 0.063903 | 0.063745
110
111 | Discharge Temp | ºC | 76.6687 | 76.5849 | 76.4228 | 78.8962 | 78.4349 | 77.2688 | 80.8742 | 80.232 | 79.7171 | 83.792 | 83.7771 | 83.3901 | 90.8678 | 90.7344 | 90.6054 | 47.9543 | 47.9974 | 48.0748 | 47.4335 | 47.1388 | 47.0256 | 47.2552 | 47.3039 | 46.71 | 47.0215 | 46.9679 | 46.7681 | 52.8733 | 53.0544 | 53.2342 | 53.9749 | 53.9215 | 53.8645 | 54.6573 | 54.2959 | 54.3258 | 51.741 | 51.8007 | 51.8306 | 52.1554 | 52.5743 | 52.653 | 63.6603 | 63.581 | 63.4182 | 63.2056 | 64.0455 | 63.8848 | 63.6064 | 77.5141 | 77.4408 | 77.2263 | 82.4291 | 81.9144 | 82.8346 | 78.711 | 78.7044 | 78.7812 | 78.5828 | 79.6879 | 79.9545 | 64.9206 | 65.4558 | 65.7251 | 67.6261 | 67.6046 | 67.6164 | 56.3924 | 56.3225 | 56.2193 | 56.017 | 55.9235 | 55.7537 | 55.4961 | 55.3446 | 55.1113 | 45.7004 | 45.4766 | 45.3926 | 46.4671 | 46.0189 | 45.609 | 53.5322 | 53.2481 | 53.3954 | 52.6919 | 52.6848 | 52.5961 | 53.6881 | 53.541 | 53.3669 | 66.9299 | 66.7963 | 66.7029 | 66.5891 | 66.413 | 66.1839 | 67.2566 | 79.4 | 79.3899 | 79.3811 | 79.4592 | 79.4766 | 79.5019 | 79.6386 | 79.8189 | 83.6596 | 83.69 | 83.1033 | 80.6129 | 80.5601 | 80.7132 | 80.4026 | 80.0417 | 79.8318 | 82.6253 | 82.7389 | 82.8015 | 66.8161 | 66.7456 | 66.7452 | 67.1784 | 67.198 | 67.1985 | 55.9889 | 56.3751 | 56.574 | 46.7646 | 46.6674 | 46.5323 | 45.7305 | 45.2656 | 65.4899 | 65.4777 | 65.9108 | 53.5212 | 53.4746 | 53.3858 | 53.0156 | 53.6689 | 53.7036 | 53.7298 | 56.208 | 56.2506 | 56.3103 | 47.6678 | 48.0269 | 47.9808 | 47.9414 | 79.0585 | 79.3621 | 79.6115 | 79.6811 | 80.2055 | 80.973 | 81.2442 | 84.6134 | 84.8795 | 84.1783 | 81.3351 | 81.2728 | 80.9674 | 80.7776 | 80.4931 | 80.4914 | 80.2766 | 79.5949 | 81.6492 | 81.8133 | 81.7659 | 78.36 | 78.5664 | 79.1082 | 79.3911 | 79.5723 | 79.7772 | 77.2175 | 77.1545 | 76.8154 | 54.0542 | 53.963 | 53.9896 | 81.1123 | 80.8792 | 80.8373 | 77.4235 | 77.1664 | 76.8264 | 79.0837 | 78.7779 | 79.2053 | 76.5866 | 76.7418 | 76.5902 | 52.7574 | 52.5277 | 52.4436 | 54.6356 | 55.0605 | 55.1597 | 54.7452 | 54.0465 | 53.7595 | 46.5342 | 46.5135 | 46.384 | 46.505 | 45.5963 | 45.1859 | 64.4279 | 64.2532 | 64.3681 | 65.2223 | 64.9016 | 64.4856 | 82.3417 | 81.291 | 80.4547 | 78.0616 | 77.9128 | 77.841 | 77.0956 | 77.092 | 77.3296 | 78.4717 | 79.1191 | 78.5143 | 54.4239 | 54.1733 | 53.8665 | 79.6024 | 79.6789 | 79.8482 | 80.4132 | 80.318 | 79.6525
112 | Discharge Pressure | BarA | 13.7337 | 13.7439 | 13.7006 | 13.7346 | 13.7509 | 13.7397 | 13.7659 | 13.7313 | 13.704 | 13.7558 | 13.765 | 13.7664 | 13.7403 | 13.7196 | 13.7051 | 7.2692 | 7.2694 | 7.2729 | 7.2925 | 7.2785 | 7.2488 | 7.2709 | 7.2702 | 7.274 | 7.2894 | 7.265 | 7.258 | 8.4236 | 8.4283 | 8.4355 | 8.4498 | 8.4489 | 8.4585 | 8.4445 | 8.4798 | 8.4593 | 8.4249 | 8.4574 | 8.4622 | 8.4462 | 8.4796 | 8.4741 | 10.7415 | 10.702 | 10.7289 | 10.6971 | 10.7705 | 10.7579 | 10.7193 | 13.3548 | 13.3595 | 13.3857 | 13.7844 | 13.74 | 13.7451 | 13.362 | 13.3646 | 13.352 | 13.1727 | 13.1489 | 13.2108 | 10.7394 | 10.715 | 10.7405 | 10.6993 | 10.719 | 10.6929 | 8.4618 | 8.4893 | 8.4636 | 8.4292 | 8.4677 | 8.4714 | 8.4773 | 8.4653 | 8.4388 | 7.2964 | 7.2976 | 7.2541 | 7.2574 | 7.285 | 7.2595 | 8.4489 | 8.4733 | 8.4528 | 8.435 | 8.4315 | 8.4407 | 8.4481 | 8.4501 | 8.4633 | 10.7535 | 10.7405 | 10.7212 | 10.7149 | 10.7299 | 10.7144 | 10.7206 | 13.3851 | 13.3886 | 13.3936 | 13.3867 | 13.3856 | 13.3864 | 13.3784 | 13.3776 | 13.745 | 13.7197 | 13.7147 | 13.4178 | 13.3795 | 13.3704 | 13.2181 | 13.1762 | 13.1516 | 13.7187 | 13.746 | 13.7199 | 10.7201 | 10.7179 | 10.7487 | 10.7184 | 10.7094 | 10.7013 | 8.4341 | 8.457 | 8.4502 | 7.2563 | 7.2664 | 7.2934 | 7.3274 | 7.271 | 10.7071 | 10.697 | 10.7165 | 8.4371 | 8.4414 | 8.4467 | 8.4713 | 8.4527 | 8.4438 | 8.4403 | 8.4262 | 8.4255 | 8.434 | 7.3284 | 7.3412 | 7.3145 | 7.2958 | 13.3169 | 13.3768 | 13.3935 | 13.3714 | 13.3907 | 13.3788 | 13.3652 | 13.1906 | 13.1972 | 13.2068 | 13.3664 | 13.389 | 13.3506 | 13.3523 | 13.2343 | 13.2717 | 13.2391 | 13.1672 | 13.7284 | 13.7237 | 13.7373 | 13.3937 | 13.3318 | 13.3524 | 13.1849 | 13.1481 | 13.1656 | 13.421 | 13.3407 | 13.3763 | 8.4878 | 8.4893 | 8.4299 | 13.7673 | 13.7713 | 13.7562 | 13.2264 | 13.1938 | 13.1836 | 13.3636 | 13.372 | 13.3756 | 13.3576 | 13.334 | 13.3241 | 8.4772 | 8.4949 | 8.4357 | 8.4877 | 8.451 | 8.4772 | 8.4476 | 8.4216 | 8.4372 | 7.2724 | 7.2728 | 7.2681 | 7.2915 | 7.2806 | 7.2693 | 10.7296 | 10.6876 | 10.683 | 10.7049 | 10.7139 | 10.6824 | 13.7816 | 13.7425 | 13.773 | 13.4206 | 13.421 | 13.3788 | 13.2315 | 13.1645 | 13.1949 | 13.4541 | 13.3976 | 13.362 | 8.4305 | 8.487 | 8.4393 | 13.2092 | 13.2131 | 13.2024 | 13.405 | 13.4526 | 13.4653
113 | Discharge SH | ºC | 25.0201 | 24.9067 | 24.8711 | 27.245 | 26.7359 | 25.6027 | 29.1315 | 28.5905 | 28.1555 | 32.0789 | 32.037 | 31.6458 | 39.2 | 39.127 | 39.0407 | 19.9525 | 19.9945 | 20.0556 | 19.3217 | 19.093 | 19.1202 | 19.2454 | 19.2973 | 18.6858 | 18.9244 | 18.986 | 18.8193 | 19.7219 | 19.8828 | 20.0324 | 20.7128 | 20.663 | 20.5659 | 21.4174 | 20.9074 | 21.0236 | 18.584 | 18.5064 | 18.5164 | 18.9084 | 19.1865 | 19.2887 | 21.5928 | 21.6524 | 21.395 | 21.2945 | 21.8759 | 21.7593 | 21.6169 | 26.9862 | 26.899 | 26.6061 | 30.6324 | 30.2473 | 31.1527 | 28.1617 | 28.1471 | 28.2616 | 28.6018 | 29.779 | 29.8586 | 22.8601 | 23.4816 | 23.6609 | 25.7072 | 25.6162 | 25.72 | 23.0797 | 22.8942 | 22.8991 | 22.8417 | 22.5862 | 22.4006 | 22.1182 | 22.0169 | 21.8955 | 17.5703 | 17.3411 | 17.4621 | 18.5212 | 17.9426 | 17.6529 | 20.2737 | 19.887 | 20.1205 | 19.492 | 19.4996 | 19.3723 | 20.4333 | 20.2775 | 20.0479 | 24.8198 | 24.7321 | 24.7068 | 24.6152 | 24.3861 | 24.2117 | 25.2625 | 28.7816 | 28.7612 | 28.7373 | 28.836 | 28.8567 | 28.8797 | 29.0404 | 29.2228 | 31.978 | 32.0823 | 31.5104 | 29.897 | 29.9585 | 30.1387 | 30.2849 | 30.0503 | 29.9147 | 31.0208 | 31.0542 | 31.1932 | 24.8238 | 24.761 | 24.6522 | 25.192 | 25.2434 | 25.2726 | 22.7931 | 23.0824 | 23.31 | 18.8238 | 18.6786 | 18.4163 | 17.455 | 17.2553 | 23.5433 | 23.5668 | 23.9311 | 20.3127 | 20.2481 | 20.1366 | 19.6627 | 20.3947 | 20.4667 | 20.5079 | 23.0456 | 23.0911 | 23.1146 | 19.3874 | 19.6867 | 19.7657 | 19.8144 | 28.644 | 28.7683 | 28.9679 | 29.1037 | 29.5704 | 30.3734 | 30.6853 | 34.5785 | 34.8248 | 34.0946 | 30.7725 | 30.6428 | 30.4519 | 30.2572 | 30.3266 | 30.2124 | 30.0958 | 29.6308 | 30.0162 | 30.194 | 30.1069 | 27.7159 | 28.1072 | 28.5874 | 29.3735 | 29.6658 | 29.8178 | 26.4922 | 26.6689 | 26.2233 | 20.6321 | 20.5345 | 20.8115 | 29.3654 | 29.1206 | 29.123 | 27.2808 | 27.1218 | 26.8128 | 28.5295 | 28.1986 | 28.6154 | 26.0503 | 26.2762 | 26.1543 | 19.3798 | 19.0757 | 19.2409 | 21.2141 | 21.7933 | 21.7821 | 21.4923 | 20.9033 | 20.5507 | 18.5174 | 18.4945 | 18.3873 | 18.398 | 17.5406 | 17.1837 | 22.4022 | 22.3757 | 22.5068 | 23.2834 | 22.931 | 22.6264 | 30.553 | 29.6166 | 28.6912 | 27.3374 | 27.1873 | 27.2415 | 26.9376 | 27.136 | 27.282 | 27.6477 | 28.4635 | 27.9648 | 21.2429 | 20.7547 | 20.6487 | 29.5114 | 29.5762 | 29.7777 | 29.7355 | 29.4985 | 28.7954
114 | Discharge Gauge | ºC | 51.6485 | 51.6783 | 51.5516 | 51.6512 | 51.699 | 51.6661 | 51.7427 | 51.6415 | 51.5616 | 51.7131 | 51.7401 | 51.7443 | 51.6678 | 51.6074 | 51.5647 | 28.0018 | 28.0029 | 28.0193 | 28.1119 | 28.0458 | 27.9054 | 28.0098 | 28.0066 | 28.0243 | 28.0972 | 27.9819 | 27.9488 | 33.1514 | 33.1716 | 33.2018 | 33.2621 | 33.2585 | 33.2986 | 33.2398 | 33.3885 | 33.3022 | 33.157 | 33.2943 | 33.3142 | 33.247 | 33.3877 | 33.3644 | 42.0675 | 41.9286 | 42.0232 | 41.9111 | 42.1696 | 42.1255 | 41.9895 | 50.5279 | 50.5418 | 50.6202 | 51.7967 | 51.6671 | 51.6819 | 50.5493 | 50.5573 | 50.5196 | 49.9809 | 49.9089 | 50.0958 | 42.0605 | 41.9742 | 42.0643 | 41.9189 | 41.9884 | 41.8964 | 33.3127 | 33.4284 | 33.3203 | 33.1753 | 33.3374 | 33.3531 | 33.3778 | 33.3276 | 33.2157 | 28.1301 | 28.1355 | 27.9304 | 27.9459 | 28.0763 | 27.9561 | 33.2585 | 33.3611 | 33.2748 | 33.1999 | 33.1852 | 33.2237 | 33.2548 | 33.2635 | 33.3189 | 42.11 | 42.0642 | 41.9961 | 41.9739 | 42.0269 | 41.9722 | 41.9941 | 50.6184 | 50.6287 | 50.6438 | 50.6231 | 50.6199 | 50.6222 | 50.5983 | 50.596 | 51.6816 | 51.6077 | 51.5929 | 50.7159 | 50.6016 | 50.5745 | 50.1176 | 49.9914 | 49.9171 | 51.6045 | 51.6847 | 51.6083 | 41.9923 | 41.9847 | 42.093 | 41.9864 | 41.9546 | 41.9259 | 33.1958 | 33.2926 | 33.264 | 27.9408 | 27.9887 | 28.116 | 28.2755 | 28.0103 | 41.9466 | 41.9109 | 41.9798 | 33.2086 | 33.2265 | 33.2491 | 33.3529 | 33.2742 | 33.2369 | 33.2219 | 33.1624 | 33.1595 | 33.1957 | 28.2804 | 28.3402 | 28.2151 | 28.127 | 50.4144 | 50.5938 | 50.6435 | 50.5774 | 50.635 | 50.5996 | 50.5589 | 50.0349 | 50.0548 | 50.0837 | 50.5626 | 50.6299 | 50.5155 | 50.5203 | 50.1665 | 50.279 | 50.1808 | 49.9641 | 51.633 | 51.6193 | 51.659 | 50.6441 | 50.4592 | 50.5208 | 50.0177 | 49.9065 | 49.9594 | 50.7253 | 50.4856 | 50.5921 | 33.4221 | 33.4285 | 33.1781 | 51.7468 | 51.7586 | 51.7144 | 50.1428 | 50.0446 | 50.0136 | 50.5542 | 50.5793 | 50.5899 | 50.5363 | 50.4656 | 50.4359 | 33.3776 | 33.4519 | 33.2027 | 33.4215 | 33.2672 | 33.3777 | 33.253 | 33.1432 | 33.2089 | 28.0168 | 28.019 | 27.9967 | 28.1069 | 28.0557 | 28.0022 | 42.0257 | 41.8775 | 41.8613 | 41.9388 | 41.9706 | 41.8592 | 51.7887 | 51.6744 | 51.7636 | 50.7242 | 50.7255 | 50.5996 | 50.158 | 49.956 | 50.0477 | 50.824 | 50.6556 | 50.5495 | 33.1809 | 33.4186 | 33.2179 | 50.091 | 50.1027 | 50.0705 | 50.6778 | 50.8195 | 50.8571
115 | Discharge enthalpy | KJ/kg | 453.2091 | 453.0993 | 452.9898 | 455.6794 | 455.1422 | 453.8663 | 457.8179 | 457.1621 | 456.6357 | 461.0487 | 461.0186 | 460.5907 | 468.8219 | 468.7044 | 468.5834 | 434.1456 | 434.1882 | 434.2592 | 433.5814 | 433.3131 | 433.2559 | 433.4438 | 433.4937 | 432.8928 | 433.1752 | 433.1677 | 432.9813 | 436.9832 | 437.1598 | 437.3306 | 438.0624 | 438.0093 | 437.9337 | 438.7695 | 438.3365 | 438.4041 | 435.821 | 435.8214 | 435.8432 | 436.2061 | 436.5734 | 436.6645 | 444.0991 | 444.0835 | 443.8631 | 443.6923 | 444.459 | 444.3095 | 444.0804 | 454.7565 | 454.6683 | 454.3898 | 459.5053 | 459.0052 | 460.0112 | 456.0626 | 456.0512 | 456.1554 | 456.2179 | 457.4648 | 457.6614 | 445.4445 | 446.0554 | 446.298 | 448.3834 | 448.3281 | 448.3837 | 440.5108 | 440.3911 | 440.331 | 440.185 | 440.0218 | 439.8417 | 439.5681 | 439.4345 | 439.2435 | 431.8391 | 431.6126 | 431.6124 | 432.6814 | 432.1801 | 431.8186 | 437.6111 | 437.2757 | 437.4639 | 436.7764 | 436.7755 | 436.6678 | 437.7722 | 437.6179 | 437.4156 | 447.5552 | 447.4353 | 447.3686 | 447.2585 | 447.0464 | 446.8294 | 447.9567 | 456.784 | 456.7674 | 456.7499 | 456.8465 | 456.8674 | 456.8939 | 457.0566 | 457.2557 | 460.9192 | 460.9901 | 460.3526 | 458.0657 | 458.0665 | 458.2483 | 458.1407 | 457.8099 | 457.618 | 459.8206 | 459.9044 | 460.0126 | 447.4904 | 447.4194 | 447.3674 | 447.8774 | 447.9132 | 447.9272 | 440.1478 | 440.5014 | 440.7164 | 432.9809 | 432.8645 | 432.678 | 431.8097 | 431.4526 | 446.1049 | 446.1092 | 446.5359 | 437.6214 | 437.566 | 437.4652 | 437.041 | 437.7442 | 437.7958 | 437.829 | 440.3852 | 440.4299 | 440.4757 | 433.7484 | 434.0839 | 434.0876 | 434.0832 | 456.5149 | 456.7551 | 457.0032 | 457.114 | 457.6601 | 458.5204 | 458.8384 | 462.7759 | 463.056 | 462.2787 | 458.9361 | 458.8335 | 458.5571 | 458.3465 | 458.215 | 458.156 | 457.9708 | 457.335 | 458.7307 | 458.9187 | 458.8457 | 455.6264 | 455.9509 | 456.5142 | 457.0845 | 457.3396 | 457.5368 | 454.3236 | 454.3828 | 453.9516 | 438.0746 | 437.9785 | 438.1135 | 458.0786 | 457.815 | 457.7922 | 454.8611 | 454.6303 | 454.2731 | 456.4698 | 456.1204 | 456.5848 | 453.7293 | 453.9386 | 453.7874 | 436.7656 | 436.4973 | 436.5209 | 438.6698 | 439.1699 | 439.2245 | 438.8538 | 438.1866 | 437.865 | 432.72 | 432.6983 | 432.5778 | 432.6543 | 431.7653 | 431.3761 | 444.9373 | 444.8241 | 444.9542 | 445.8244 | 445.4681 | 445.0801 | 459.413 | 458.314 | 457.3433 | 455.2552 | 455.0904 | 455.0785 | 454.4925 | 454.5953 | 454.8081 | 455.6541 | 456.4557 | 455.8461 | 438.5561 | 438.198 | 437.9706 | 457.2784 | 457.3561 | 457.558 | 457.8661 | 457.6883 | 456.9369
116 | Discharge specific volume | m3/kg | 0.017117 | 0.017094 | 0.017146 | 0.017327 | 0.017258 | 0.017165 | 0.017464 | 0.017458 | 0.017453 | 0.017748 | 0.017733 | 0.017695 | 0.018407 | 0.018429 | 0.018441 | 0.031592 | 0.031597 | 0.031592 | 0.031393 | 0.031417 | 0.031549 | 0.031474 | 0.031485 | 0.031373 | 0.031344 | 0.031458 | 0.031462 | 0.027264 | 0.027272 | 0.027269 | 0.027318 | 0.027314 | 0.02727 | 0.027433 | 0.027249 | 0.027331 | 0.0271 | 0.026985 | 0.026972 | 0.027078 | 0.02701 | 0.027042 | 0.021575 | 0.021662 | 0.021577 | 0.021631 | 0.021549 | 0.021561 | 0.021623 | 0.017806 | 0.017791 | 0.017727 | 0.017579 | 0.017601 | 0.017678 | 0.017908 | 0.017903 | 0.017932 | 0.018212 | 0.018359 | 0.018279 | 0.021725 | 0.021847 | 0.021815 | 0.022133 | 0.022082 | 0.022148 | 0.027606 | 0.027492 | 0.027575 | 0.027679 | 0.027519 | 0.027482 | 0.027424 | 0.027448 | 0.027518 | 0.031101 | 0.03106 | 0.031264 | 0.031417 | 0.031208 | 0.031271 | 0.02726 | 0.027128 | 0.027226 | 0.027195 | 0.027208 | 0.02716 | 0.027285 | 0.027257 | 0.027182 | 0.02192 | 0.021937 | 0.021974 | 0.021977 | 0.02192 | 0.021932 | 0.022039 | 0.017936 | 0.017929 | 0.01792 | 0.017939 | 0.017942 | 0.017944 | 0.01797 | 0.017988 | 0.017753 | 0.017796 | 0.01775 | 0.017997 | 0.018055 | 0.018084 | 0.01831 | 0.018346 | 0.018368 | 0.0177 | 0.017667 | 0.017714 | 0.02199 | 0.021987 | 0.021911 | 0.022035 | 0.02206 | 0.02208 | 0.027657 | 0.027622 | 0.027675 | 0.03147 | 0.031404 | 0.031247 | 0.030953 | 0.031159 | 0.02187 | 0.021894 | 0.021895 | 0.027303 | 0.027281 | 0.027248 | 0.027103 | 0.027265 | 0.027303 | 0.02732 | 0.027717 | 0.027726 | 0.027701 | 0.031252 | 0.031245 | 0.031369 | 0.031457 | 0.018016 | 0.017946 | 0.017942 | 0.017985 | 0.018003 | 0.018095 | 0.018143 | 0.018752 | 0.018765 | 0.018684 | 0.01815 | 0.018106 | 0.018141 | 0.018121 | 0.018291 | 0.018228 | 0.018262 | 0.018319 | 0.017594 | 0.017617 | 0.017591 | 0.017823 | 0.017944 | 0.017962 | 0.018269 | 0.018349 | 0.018339 | 0.017669 | 0.017794 | 0.017703 | 0.027185 | 0.027167 | 0.027396 | 0.017484 | 0.017456 | 0.017475 | 0.01801 | 0.01804 | 0.018024 | 0.017941 | 0.017898 | 0.017933 | 0.017711 | 0.017765 | 0.017767 | 0.027045 | 0.026946 | 0.027158 | 0.027266 | 0.027464 | 0.027378 | 0.027433 | 0.027436 | 0.027336 | 0.031353 | 0.031347 | 0.03135 | 0.031253 | 0.031163 | 0.031155 | 0.021693 | 0.021776 | 0.0218 | 0.021845 | 0.021786 | 0.021815 | 0.017575 | 0.017539 | 0.017414 | 0.01775 | 0.017735 | 0.017798 | 0.01797 | 0.018082 | 0.018054 | 0.017735 | 0.017889 | 0.01789 | 0.027454 | 0.027205 | 0.027343 | 0.018248 | 0.018249 | 0.018283 | 0.017999 | 0.017912 | 0.017829
117
118 | Comp PR |  | 2.8081 | 2.8106 | 2.8112 | 3.3098 | 3.3137 | 3.3128 | 3.9518 | 3.9209 | 3.917 | 4.7022 | 4.701 | 4.7066 | 5.6403 | 5.6405 | 5.6414 | 1.887 | 1.8886 | 1.8916 | 1.892 | 1.8862 | 1.8807 | 1.8927 | 1.8919 | 1.8882 | 1.8944 | 1.8858 | 1.8847 | 2.2202 | 2.2222 | 2.2204 | 2.2193 | 2.2193 | 2.2234 | 2.2303 | 2.2324 | 2.2256 | 2.2209 | 2.2245 | 2.2247 | 2.2178 | 2.2346 | 2.2274 | 2.9857 | 2.9747 | 2.9875 | 2.972 | 2.9958 | 2.9831 | 2.9757 | 3.9545 | 3.9622 | 3.9589 | 4.4347 | 4.4193 | 4.4176 | 3.9523 | 3.9584 | 3.9527 | 3.9112 | 3.8988 | 3.912 | 2.9858 | 2.9869 | 2.9931 | 2.9706 | 2.9823 | 2.9793 | 2.2333 | 2.2343 | 2.2308 | 2.2263 | 2.2241 | 2.2252 | 2.2244 | 2.228 | 2.2215 | 1.8915 | 1.8932 | 1.8885 | 1.8847 | 1.8889 | 1.8859 | 2.224 | 2.2252 | 2.2227 | 2.2258 | 2.2238 | 2.2207 | 2.2233 | 2.2259 | 2.2235 | 2.9857 | 2.9888 | 2.989 | 2.9849 | 2.9852 | 2.987 | 2.9829 | 3.9614 | 3.9594 | 3.9661 | 3.9616 | 3.9581 | 3.9564 | 3.9502 | 3.9476 | 4.4051 | 4.4063 | 4.4123 | 3.9712 | 3.9563 | 3.9564 | 3.9107 | 3.9006 | 3.8899 | 4.405 | 4.4122 | 4.4076 | 2.98 | 2.9836 | 2.9955 | 2.9796 | 2.9802 | 2.9803 | 2.2179 | 2.2231 | 2.2217 | 1.8894 | 1.8914 | 1.8906 | 1.8977 | 1.8902 | 2.981 | 2.9781 | 2.979 | 2.2224 | 2.2207 | 2.2233 | 2.2247 | 2.2248 | 2.2204 | 2.2201 | 2.3405 | 2.3463 | 2.3404 | 1.9151 | 1.9033 | 1.8978 | 1.8924 | 3.9666 | 3.9728 | 3.9688 | 3.9737 | 3.9768 | 3.9547 | 3.9441 | 3.9104 | 3.9119 | 3.8939 | 3.9491 | 3.9471 | 3.9514 | 3.9526 | 3.9088 | 3.9152 | 3.9136 | 3.8873 | 4.4074 | 4.4003 | 4.414 | 3.958 | 3.9523 | 3.9526 | 3.9083 | 3.9026 | 3.9017 | 3.9667 | 3.9576 | 3.9603 | 2.2319 | 2.2315 | 2.2254 | 4.4201 | 4.4196 | 4.4103 | 3.9051 | 3.9061 | 3.9083 | 3.9655 | 3.9565 | 3.9543 | 3.9546 | 3.9532 | 3.9548 | 2.2367 | 2.2346 | 2.226 | 2.2327 | 2.2237 | 2.2329 | 2.2206 | 2.2171 | 2.2216 | 1.8879 | 1.8879 | 1.8799 | 1.8948 | 1.8924 | 1.8911 | 2.9917 | 2.9738 | 2.976 | 2.9733 | 2.9767 | 2.9685 | 4.4226 | 4.4207 | 4.4346 | 3.9684 | 3.9736 | 3.9716 | 3.9187 | 3.901 | 3.9152 | 3.9701 | 3.9665 | 3.9521 | 2.2232 | 2.2377 | 2.2212 | 3.9104 | 3.9173 | 3.9207 | 3.9731 | 3.9791 | 3.9886
119 | Comp PD |  | 8.8429 | 8.8538 | 8.827 | 9.585 | 9.6012 | 9.5922 | 10.2824 | 10.2292 | 10.2054 | 10.8304 | 10.8369 | 10.8415 | 11.3042 | 11.2873 | 11.2757 | 3.417 | 3.4204 | 3.428 | 3.4381 | 3.4197 | 3.3944 | 3.4294 | 3.4275 | 3.4217 | 3.4416 | 3.4126 | 3.4069 | 4.6295 | 4.6355 | 4.6363 | 4.6424 | 4.6419 | 4.6541 | 4.6583 | 4.6814 | 4.6584 | 4.6315 | 4.6555 | 4.6584 | 4.6378 | 4.685 | 4.6696 | 7.1438 | 7.1043 | 7.1376 | 7.0978 | 7.1753 | 7.1517 | 7.117 | 9.9777 | 9.9877 | 10.0045 | 10.6761 | 10.6309 | 10.6337 | 9.9811 | 9.9884 | 9.974 | 9.8048 | 9.7764 | 9.8339 | 7.1426 | 7.1277 | 7.1521 | 7.0976 | 7.1247 | 7.1038 | 4.6729 | 4.6898 | 4.6696 | 4.643 | 4.6604 | 4.6644 | 4.6663 | 4.6658 | 4.6401 | 3.4389 | 3.4429 | 3.413 | 3.4068 | 3.4282 | 3.4101 | 4.65 | 4.6654 | 4.6499 | 4.6454 | 4.64 | 4.6399 | 4.6482 | 4.6539 | 4.6569 | 7.1518 | 7.1469 | 7.1342 | 7.1252 | 7.1355 | 7.1274 | 7.1266 | 10.0062 | 10.0071 | 10.0166 | 10.0075 | 10.0038 | 10.0029 | 9.9916 | 9.9888 | 10.6247 | 10.6061 | 10.6064 | 10.039 | 9.9977 | 9.991 | 9.8381 | 9.7982 | 9.7707 | 10.6043 | 10.6306 | 10.6071 | 7.1227 | 7.1257 | 7.1604 | 7.1212 | 7.1159 | 7.1106 | 4.6314 | 4.6529 | 4.6467 | 3.4158 | 3.4246 | 3.4357 | 3.4663 | 3.4242 | 7.1153 | 7.1052 | 7.1191 | 4.6406 | 4.6401 | 4.6475 | 4.6635 | 4.6534 | 4.641 | 4.6386 | 4.826 | 4.8345 | 4.8304 | 3.5019 | 3.4841 | 3.4602 | 3.4404 | 9.9597 | 10.0097 | 10.0188 | 10.0064 | 10.0234 | 9.9958 | 9.9765 | 9.8174 | 9.8236 | 9.8151 | 9.9817 | 9.9969 | 9.9719 | 9.9742 | 9.8485 | 9.882 | 9.8562 | 9.7799 | 10.6135 | 10.6049 | 10.6251 | 10.0097 | 9.9586 | 9.9743 | 9.8113 | 9.7791 | 9.7913 | 10.0376 | 9.9698 | 9.9987 | 4.6848 | 4.685 | 4.6419 | 10.6526 | 10.6554 | 10.6371 | 9.8395 | 9.8161 | 9.8103 | 9.9936 | 9.9923 | 9.993 | 9.9799 | 9.961 | 9.9549 | 4.6872 | 4.6934 | 4.646 | 4.6861 | 4.6506 | 4.6807 | 4.6435 | 4.6232 | 4.6393 | 3.4204 | 3.4206 | 3.402 | 3.4432 | 3.4334 | 3.4253 | 7.1431 | 7.0936 | 7.0933 | 7.1046 | 7.1146 | 7.0838 | 10.6654 | 10.6339 | 10.6672 | 10.0387 | 10.0435 | 10.0101 | 9.855 | 9.7899 | 9.8247 | 10.0653 | 10.0199 | 9.981 | 4.6385 | 4.6942 | 4.6399 | 9.8312 | 9.84 | 9.835 | 10.031 | 10.0718 | 10.0894
120
121 | Discharge side partial condenser Pressure
122
123 | Oil Circuit
124 | Oil pressure pre filter | BarA | 1.4178 | 1.4172 | 1.4183 | 1.4097 | 1.4138 | 1.4101 | 1.4079 | 1.4087 | 1.4033 | 1.3982 | 1.4028 | 1.4017 | 1.3884 | 1.3878 | 1.3976 | 1.3787 | 1.3738 | 1.3754 | 1.372 | 1.3695 | 1.3821 | 1.3716 | 1.3793 | 1.3772 | 1.3866 | 1.3764 | 1.3739 | 1.397 | 1.3904 | 1.3974 | 1.4002 | 1.3869 | 1.3978 | 1.3825 | 1.3946 | 1.4029 | 1.3968 | 1.4013 | 1.3909 | 1.3816 | 1.4015 | 1.392 | 1.3817 | 1.3936 | 1.3862 | 1.3838 | 1.386 | 1.3888 | 1.3825 | 1.3814 | 1.3723 | 1.389 | 1.3716 | 1.3618 | 1.3592 | 1.3551 | 1.3517 | 1.3522 | 1.3463 | 1.3495 | 1.3572 | 1.2158 | 1.2164 | 1.2023 | 1.2079 | 1.2044 | 1.1998 | 1.2012 | 1.1976 | 1.2079 | 1.204 | 1.1869 | 1.1732 | 1.2083 | 1.209 | 1.2032 | 1.182 | 1.1908 | 1.1945 | 1.1816 | 1.1712 | 1.1769 | 1.1667 | 1.1556 | 1.1686 | 1.1584 | 1.163 | 1.1547 | 1.1606 | 1.1532 | 1.1561 | 1.1476 | 1.1666 | 1.1465 | 1.143 | 1.1435 | 1.1466 | 1.1243 | 1.1309 | 1.1396 | 1.1247 | 1.1212 | 1.117 | 1.1181 | 1.1227 | 1.1094 | 1.082 | 1.0847 | 1.0887 | 1.0733 | 1.0728 | 1.0741 | 1.0651 | 1.0669 | 1.0699 | 0.91052 | 0.93129 | 0.92282 | 0.91516 | 0.92679 | 0.92836 | 0.92679 | 0.93817 | 0.92998 | 0.8985 | 0.91869 | 0.91141 | 0.90095 | 0.91709 | 0.91281 | 0.89994 | 0.9025 | 0.9261 | 0.93016 | 0.92952 | 0.92121 | 0.91657 | 0.91577 | 0.93264 | 0.92574 | 0.91022 | 0.91568 | 0.90625 | 0.91928 | 0.90763 | 0.90292 | 0.89394 | 0.90489 | 0.90279 | 0.9189 | 0.92286 | 0.91737 | 0.91588 | 0.9168 | 0.9129 | 0.91852 | 0.90519 | 0.91281 | 0.91609 | 0.88559 | 0.88498 | 0.88389 | 0.88176 | 0.8919 | 0.87614 | 0.87399 | 0.87985 | 0.6283 | 0.62624 | 0.62551 | 0.60476 | 0.61187 | 0.61688 | 0.61235 | 0.61089 | 0.60354 | 0.6105 | 0.59755 | 0.60622 | 0.59709 | 0.59932 | 0.6013 | 1.3153 | 1.311 | 1.3154 | 1.3099 | 1.3001 | 1.3141 | 1.2917 | 1.2968 | 1.294 | 1.2985 | 1.2853 | 1.3012 | 1.2703 | 1.2699 | 1.2669 | 1.4928 | 1.4956 | 1.4845 | 1.4847 | 1.493 | 1.4872 | 1.4892 | 1.4912 | 1.4955 | 1.5056 | 1.4967 | 1.4897 | 1.4862 | 1.4874 | 1.4873 | 1.4798 | 1.4831 | 1.4824 | 1.4499 | 1.4513 | 1.4425 | 1.4483 | 1.4403 | 1.4353 | 1.4318 | 1.4318 | 1.4294 | 1.35 | 1.3615 | 1.3581 | 1.3264 | 1.3225 | 1.3178 | 1.6148 | 1.6174 | 1.6154 | 1.5892 | 1.589 | 1.582
125 | Oil pressure out filter | BarA | 13.7537 | 13.7843 | 13.7135 | 13.5732 | 13.5788 | 13.5531 | 13.4214 | 13.3976 | 13.3759 | 13.2888 | 13.2909 | 13.3075 | 13.1823 | 13.1672 | 13.1624 | 7.1148 | 7.1111 | 7.1047 | 7.1437 | 7.1325 | 7.107 | 7.132 | 7.1195 | 7.1294 | 7.1274 | 7.1221 | 7.1197 | 8.2558 | 8.2734 | 8.2637 | 8.2749 | 8.278 | 8.2899 | 8.2667 | 8.2957 | 8.2904 | 8.2416 | 8.2797 | 8.2846 | 8.2738 | 8.3072 | 8.296 | 10.4407 | 10.4048 | 10.4285 | 10.3919 | 10.4257 | 10.429 | 10.3719 | 12.9913 | 12.9853 | 13.0194 | 13.385 | 13.3387 | 13.3308 | 13.021 | 13.0243 | 12.9955 | 12.8288 | 12.7949 | 12.8429 | 10.3318 | 10.3334 | 10.358 | 10.3154 | 10.3145 | 10.286 | 8.2295 | 8.2504 | 8.2258 | 8.1367 | 8.1735 | 8.1776 | 8.2004 | 8.1419 | 8.129 | 7.0726 | 7.1045 | 7.0104 | 7.0514 | 7.0848 | 7.0579 | 8.2123 | 8.23 | 8.219 | 8.2035 | 8.2064 | 8.2146 | 8.1952 | 8.1869 | 8.2162 | 10.4047 | 10.3885 | 10.3603 | 10.3393 | 10.3528 | 10.3372 | 10.338 | 12.9722 | 12.9819 | 12.9745 | 12.9804 | 12.9856 | 12.9718 | 12.9867 | 12.9601 | 13.3032 | 13.2621 | 13.2544 | 13.002 | 12.9624 | 12.9438 | 12.7952 | 12.7402 | 12.7233 | 13.2001 | 13.2259 | 13.2142 | 10.3281 | 10.3341 | 10.3626 | 10.3341 | 10.3232 | 10.3246 | 8.203 | 8.237 | 8.2253 | 7.0717 | 7.0913 | 7.118 | 7.1549 | 7.1006 | 10.3118 | 10.2989 | 10.3176 | 8.2258 | 8.2302 | 8.2305 | 8.2644 | 8.2589 | 8.2439 | 8.2434 | 8.1861 | 8.1903 | 8.1908 | 7.1299 | 7.1645 | 7.1438 | 7.1282 | 12.8459 | 12.9072 | 12.9125 | 12.9008 | 12.9519 | 12.928 | 12.9337 | 12.729 | 12.7487 | 12.743 | 12.8739 | 12.915 | 12.8684 | 12.8634 | 12.761 | 12.7849 | 12.7565 | 12.6899 | 13.2905 | 13.3129 | 13.3063 | 13.1136 | 13.0541 | 13.0623 | 12.857 | 12.8454 | 12.8592 | 13.122 | 13.0064 | 13.0623 | 8.3176 | 8.3149 | 8.2616 | 13.3269 | 13.327 | 13.3208 | 12.8922 | 12.8451 | 12.8421 | 12.9918 | 13.0278 | 13.0137 | 12.9628 | 12.9271 | 12.9294 | 8.2856 | 8.2992 | 8.2471 | 8.3406 | 8.3013 | 8.3234 | 8.296 | 8.2667 | 8.2858 | 7.1031 | 7.0863 | 7.0961 | 7.0882 | 7.1131 | 7.1066 | 10.4289 | 10.3936 | 10.377 | 10.3956 | 10.3988 | 10.3812 | 13.378 | 13.3579 | 13.3662 | 13.1 | 13.0781 | 13.0447 | 12.9051 | 12.8445 | 12.8643 | 13.0584 | 12.9766 | 12.9731 | 8.2752 | 8.3348 | 8.2806 | 12.7796 | 12.7804 | 12.7777 | 12.9636 | 13.0022 | 13.0159
126 | Oil filter DP |  | -12.3359 | -12.3671 | -12.2952 | -12.1635 | -12.165 | -12.143 | -12.0135 | -11.9889 | -11.9726 | -11.8906 | -11.8881 | -11.9058 | -11.794 | -11.7795 | -11.7649 | -5.7361 | -5.7373 | -5.7293 | -5.7717 | -5.763 | -5.7248 | -5.7604 | -5.7402 | -5.7522 | -5.7408 | -5.7458 | -5.7458 | -6.8588 | -6.883 | -6.8663 | -6.8747 | -6.8911 | -6.8922 | -6.8842 | -6.901 | -6.8875 | -6.8448 | -6.8785 | -6.8937 | -6.8922 | -6.9057 | -6.904 | -9.0589 | -9.0112 | -9.0423 | -9.0081 | -9.0397 | -9.0402 | -8.9894 | -11.61 | -11.613 | -11.6305 | -12.0134 | -11.9769 | -11.9716 | -11.6659 | -11.6726 | -11.6433 | -11.4825 | -11.4454 | -11.4857 | -9.116 | -9.1171 | -9.1557 | -9.1075 | -9.1101 | -9.0862 | -7.0283 | -7.0528 | -7.0178 | -6.9328 | -6.9867 | -7.0045 | -6.9921 | -6.9329 | -6.9258 | -5.8906 | -5.9137 | -5.8159 | -5.8698 | -5.9136 | -5.8811 | -7.0457 | -7.0744 | -7.0504 | -7.0451 | -7.0434 | -7.06 | -7.0346 | -7.0338 | -7.0601 | -9.257 | -9.2219 | -9.2137 | -9.1963 | -9.2093 | -9.1906 | -9.2137 | -11.8412 | -11.8423 | -11.8498 | -11.8592 | -11.8685 | -11.8537 | -11.8641 | -11.8507 | -12.2212 | -12.1774 | -12.1657 | -11.9287 | -11.8895 | -11.8697 | -11.7301 | -11.6733 | -11.6534 | -12.2896 | -12.2947 | -12.2914 | -9.4129 | -9.4073 | -9.4342 | -9.4073 | -9.3851 | -9.3947 | -7.3045 | -7.3183 | -7.3139 | -6.1707 | -6.1742 | -6.2051 | -6.255 | -6.1981 | -9.3857 | -9.3688 | -9.3881 | -7.3046 | -7.3136 | -7.3147 | -7.3317 | -7.3332 | -7.3337 | -7.3278 | -7.2798 | -7.2711 | -7.2832 | -6.2269 | -6.2706 | -6.2389 | -6.2254 | -11.927 | -11.9843 | -11.9951 | -11.9849 | -12.0351 | -12.0151 | -12.0152 | -11.8238 | -11.8359 | -11.8269 | -11.9883 | -12.03 | -11.9846 | -11.9817 | -11.8691 | -11.9088 | -11.8825 | -11.8101 | -12.6622 | -12.6867 | -12.6807 | -12.5088 | -12.4423 | -12.4454 | -12.2447 | -12.2345 | -12.2557 | -12.5115 | -12.4089 | -12.456 | -7.7205 | -7.7156 | -7.6603 | -12.0116 | -12.016 | -12.0055 | -11.5823 | -11.545 | -11.5281 | -11.7001 | -11.731 | -11.7197 | -11.6643 | -11.6418 | -11.6282 | -7.0153 | -7.0292 | -6.9802 | -6.8478 | -6.8056 | -6.839 | -6.8113 | -6.7737 | -6.7986 | -5.6139 | -5.5951 | -5.6005 | -5.5827 | -5.6164 | -5.6168 | -8.9427 | -8.9062 | -8.8897 | -8.9158 | -8.9157 | -8.8987 | -11.9281 | -11.9067 | -11.9237 | -11.6517 | -11.6378 | -11.6095 | -11.4733 | -11.4127 | -11.4349 | -11.7085 | -11.6151 | -11.615 | -6.9488 | -7.0123 | -6.9628 | -11.1649 | -11.163 | -11.1623 | -11.3744 | -11.4133 | -11.434
127 | High Oil Filter DP warning
128 | Oil orifice plate Temp | ºC | 40.7921 | 40.6546 | 40.3874 | 40.5348 | 40.4462 | 40.3549 | 40.6436 | 39.7913 | 39.4147 | 39.802 | 39.3913 | 39.3952 | 40.225 | 40.0836 | 39.9408 | 16.6922 | 16.625 | 16.5061 | 16.0862 | 16.0184 | 15.9368 | 17.7019 | 17.64 | 17.6008 | 17.5067 | 17.4708 | 17.413 | 26.8286 | 26.9557 | 27.1538 | 27.3963 | 27.4766 | 27.5626 | 27.0967 | 26.8434 | 26.6569 | 26.4149 | 26.7394 | 27.5656 | 28.8275 | 29.2425 | 29.6643 | 32.6334 | 32.544 | 32.458 | 32.4803 | 32.5396 | 32.5281 | 32.8562 | 38.6698 | 38.5563 | 38.0194 | 41.2519 | 40.8887 | 39.1629 | 32.126 | 31.4642 | 30.5471 | 31.0461 | 28.369 | 26.383 | 31.7175 | 31.8898 | 31.898 | 30.4307 | 30.1481 | 30.0147 | 24.8227 | 24.7174 | 24.3974 | 23.3593 | 23.0792 | 22.7127 | 22.251 | 22.0818 | 22.005 | 19.4261 | 19.5224 | 19.6483 | 18.59 | 18.1689 | 17.5883 | 26.1989 | 26.0528 | 25.8626 | 26.2855 | 26.4289 | 26.5404 | 26.657 | 26.7897 | 27.0011 | 33.3966 | 33.4712 | 33.4535 | 32.9174 | 32.8211 | 32.6756 | 37.2602 | 41.3436 | 41.3477 | 41.2798 | 40.9855 | 40.976 | 40.9601 | 40.6978 | 40.1321 | 36.1842 | 35.2439 | 34.6642 | 26.6952 | 25.6215 | 24.4677 | 21.4709 | 19.9685 | 18.9235 | 41.7329 | 41.6097 | 41.5205 | 32.3824 | 32.2807 | 32.2552 | 31.3883 | 31.2228 | 31.1445 | 24.9212 | 25.064 | 25.1768 | 16.5444 | 16.4665 | 16.4009 | 16.1617 | 16.1241 | 30.5172 | 30.4709 | 30.8901 | 24.9111 | 24.9004 | 24.893 | 24.5651 | 24.7244 | 24.6987 | 24.6131 | 23.3695 | 23.2757 | 23.0251 | 18.9694 | 18.8393 | 18.7843 | 18.8262 | 43.0611 | 43.0568 | 42.9161 | 42.9186 | 43.1771 | 43.3292 | 43.3649 | 43.3368 | 42.8804 | 41.2072 | 36.5552 | 36.3188 | 35.7905 | 35.438 | 34.4068 | 33.7584 | 33.1812 | 32.4522 | 41.4939 | 41.2797 | 40.9057 | 38.6219 | 38.6503 | 38.6909 | 38.6359 | 38.4659 | 38.206 | 34.4619 | 33.2104 | 32.5343 | 18.0675 | 17.9035 | 17.738 | 36.3144 | 35.6583 | 35.0687 | 30.0558 | 29.2215 | 28.3415 | 22.3259 | 21.3972 | 20.8953 | 19.6278 | 18.9572 | 18.5365 | 14.9461 | 14.8862 | 14.8184 | 22.6244 | 22.443 | 22.7439 | 20.505 | 20.2009 | 19.8564 | 19.7192 | 19.7019 | 19.6793 | 19.5719 | 19.5581 | 19.5728 | 30.8866 | 30.818 | 30.7885 | 30.2571 | 30.4709 | 30.2027 | 40.8035 | 40.2832 | 40.2979 | 38.1685 | 37.8408 | 37.385 | 36.5859 | 36.095 | 35.3836 | 29.3898 | 28.8142 | 27.8532 | 16.9053 | 16.8412 | 16.8044 | 39.3221 | 39.1511 | 38.9259 | 37.5414 | 36.5293 | 35.4607
129 | Oil orifice plate Pressure | BarA | 13.7537 | 13.7843 | 13.7135 | 13.5732 | 13.5788 | 13.5531 | 13.4214 | 13.3976 | 13.3759 | 13.2888 | 13.2909 | 13.3075 | 13.1823 | 13.1672 | 13.1624 | 7.1148 | 7.1111 | 7.1047 | 7.1437 | 7.1325 | 7.107 | 7.132 | 7.1195 | 7.1294 | 7.1274 | 7.1221 | 7.1197 | 8.2558 | 8.2734 | 8.2637 | 8.2749 | 8.278 | 8.2899 | 8.2667 | 8.2957 | 8.2904 | 8.2416 | 8.2797 | 8.2846 | 8.2738 | 8.3072 | 8.296 | 10.4407 | 10.4048 | 10.4285 | 10.3919 | 10.4257 | 10.429 | 10.3719 | 12.9913 | 12.9853 | 13.0194 | 13.385 | 13.3387 | 13.3308 | 13.021 | 13.0243 | 12.9955 | 12.8288 | 12.7949 | 12.8429 | 10.3318 | 10.3334 | 10.358 | 10.3154 | 10.3145 | 10.286 | 8.2295 | 8.2504 | 8.2258 | 8.1367 | 8.1735 | 8.1776 | 8.2004 | 8.1419 | 8.129 | 7.0726 | 7.1045 | 7.0104 | 7.0514 | 7.0848 | 7.0579 | 8.2123 | 8.23 | 8.219 | 8.2035 | 8.2064 | 8.2146 | 8.1952 | 8.1869 | 8.2162 | 10.4047 | 10.3885 | 10.3603 | 10.3393 | 10.3528 | 10.3372 | 10.338 | 12.9722 | 12.9819 | 12.9745 | 12.9804 | 12.9856 | 12.9718 | 12.9867 | 12.9601 | 13.3032 | 13.2621 | 13.2544 | 13.002 | 12.9624 | 12.9438 | 12.7952 | 12.7402 | 12.7233 | 13.2001 | 13.2259 | 13.2142 | 10.3281 | 10.3341 | 10.3626 | 10.3341 | 10.3232 | 10.3246 | 8.203 | 8.237 | 8.2253 | 7.0717 | 7.0913 | 7.118 | 7.1549 | 7.1006 | 10.3118 | 10.2989 | 10.3176 | 8.2258 | 8.2302 | 8.2305 | 8.2644 | 8.2589 | 8.2439 | 8.2434 | 8.1861 | 8.1903 | 8.1908 | 7.1299 | 7.1645 | 7.1438 | 7.1282 | 12.8459 | 12.9072 | 12.9125 | 12.9008 | 12.9519 | 12.928 | 12.9337 | 12.729 | 12.7487 | 12.743 | 12.8739 | 12.915 | 12.8684 | 12.8634 | 12.761 | 12.7849 | 12.7565 | 12.6899 | 13.2905 | 13.3129 | 13.3063 | 13.1136 | 13.0541 | 13.0623 | 12.857 | 12.8454 | 12.8592 | 13.122 | 13.0064 | 13.0623 | 8.3176 | 8.3149 | 8.2616 | 13.3269 | 13.327 | 13.3208 | 12.8922 | 12.8451 | 12.8421 | 12.9918 | 13.0278 | 13.0137 | 12.9628 | 12.9271 | 12.9294 | 8.2856 | 8.2992 | 8.2471 | 8.3406 | 8.3013 | 8.3234 | 8.296 | 8.2667 | 8.2858 | 7.1031 | 7.0863 | 7.0961 | 7.0882 | 7.1131 | 7.1066 | 10.4289 | 10.3936 | 10.377 | 10.3956 | 10.3988 | 10.3812 | 13.378 | 13.3579 | 13.3662 | 13.1 | 13.0781 | 13.0447 | 12.9051 | 12.8445 | 12.8643 | 13.0584 | 12.9766 | 12.9731 | 8.2752 | 8.3348 | 8.2806 | 12.7796 | 12.7804 | 12.7777 | 12.9636 | 13.0022 | 13.0159
130 | Oil orifice plate DP | Bar | -0.003638 | -0.003716 | -0.003696 | -0.003698 | -0.003641 | -0.003658 | -0.003481 | -0.003515 | -0.003601 | -0.00339 | -0.003386 | -0.003413 | -0.00334 | -0.003425 | -0.003459 | 0.0024 | 0.002446 | 0.002389 | 0.002238 | 0.002355 | 0.002334 | 0.002063 | 0.002025 | 0.001903 | 0.001748 | 0.00152 | 0.001772 | -0.003833 | -0.004015 | -0.003997 | -0.003928 | -0.004032 | -0.004057 | -0.004011 | -0.003915 | -0.004031 | -0.004075 | -0.00407 | -0.004018 | -0.004062 | -0.004085 | -0.003936 | -0.00405 | -0.003987 | -0.004059 | -0.004064 | -0.003926 | -0.004031 | -0.004085 | -0.003814 | -0.003901 | -0.003844 | -0.003846 | -0.00374 | -0.00385 | -0.003636 | -0.003503 | -0.003652 | -0.003377 | -0.003425 | -0.003476 | -0.003964 | -0.004101 | -0.00406 | -0.004015 | -0.003903 | -0.003871 | -0.003902 | -0.004061 | -0.004073 | -0.003981 | -0.00408 | -0.003983 | -0.003647 | -0.003697 | -0.003797 | -0.002994 | -0.003814 | -0.003802 | -0.003855 | -0.003614 | -0.003618 | -0.003997 | -0.004024 | -0.004103 | -0.004089 | -0.004088 | -0.004075 | -0.0041 | -0.004095 | -0.004094 | -0.004049 | -0.003982 | -0.003946 | -0.004015 | -0.004097 | -0.003977 | -0.004006 | -0.003866 | -0.003883 | -0.003928 | -0.004047 | -0.004055 | -0.004141 | -0.00386 | -0.003867 | -0.003881 | -0.003756 | -0.003929 | -0.003617 | -0.003612 | -0.003509 | -0.003567 | -0.003456 | -0.003492 | -0.003926 | -0.004055 | -0.003996 | -0.003848 | -0.003888 | -0.003694 | -0.003799 | -0.003816 | -0.003851 | -0.003693 | -0.003756 | -0.003719 | -0.00363 | -0.003548 | -0.003597 | -0.003629 | -0.003566 | -0.00408 | -0.003829 | -0.004061 | -0.003951 | -0.003765 | -0.003781 | -0.003735 | -0.003795 | -0.00378 | -0.003838 | -0.003707 | -0.003752 | -0.003824 | -0.003608 | -0.003602 | -0.003634 | -0.003554 | -0.003822 | -0.00383 | -0.003744 | -0.003837 | -0.003792 | -0.003814 | -0.003814 | -0.003721 | -0.003794 | -0.003723 | -0.004021 | -0.00405 | -0.003947 | -0.003973 | -0.003955 | -0.004024 | -0.004003 | -0.004008 | -0.003798 | -0.003946 | -0.003973 | -0.003882 | -0.00386 | -0.003891 | -0.003911 | -0.003874 | -0.003747 | -0.003879 | -0.003868 | -0.003896 | -0.003598 | -0.003583 | -0.00359 | -0.003945 | -0.003954 | -0.00393 | -0.003865 | -0.003909 | -0.003793 | -0.003898 | -0.003821 | -0.003856 | -0.003925 | -0.003861 | -0.003746 | -0.00361 | -0.003639 | -0.003635 | -0.007724 | -0.007803 | -0.007699 | -0.007629 | -0.007555 | -0.007752 | -0.008664 | -0.008714 | -0.009337 | -0.008703 | -0.009099 | -0.009209 | -0.006575 | -0.006665 | -0.006587 | -0.006335 | -0.006317 | -0.0062 | -0.005584 | -0.005637 | -0.005542 | -0.00569 | -0.005617 | -0.005581 | -0.005621 | -0.005635 | -0.005471 | -0.005903 | -0.005926 | -0.005913 | -0.008688 | -0.008748 | -0.008667 | -0.004154 | -0.00401 | -0.00405 | -0.00409 | -0.004014 | -0.004035
131 | Oil Specific Volume | m3/kg | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985 | 0.000985
132 | oil orifice Plate pipe dia | m | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894 | 0.040894
133 | oil orifice plate orifice dia | m | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152 | 0.0152
134 | oil orifice plate Gamma (cp/cv) | - | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
135 | oil flow Viscosity | Pa.s | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125 | 0.0076125
136 | Oil orifice plate vol flow | m^3/hr | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.018874 | 0.019007 | 0.018842 | 0.018393 | 0.018743 | 0.018681 | 0.017848 | 0.017726 | 0.017324 | 0.017582 | 0.016771 | 0.017663 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
137 | Oil Density (manual input) | kg/m3 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000
138 | Oil orifice plate mass flow | kg/s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0052428 | 0.0052798 | 0.0052339 | 0.0051091 | 0.0052063 | 0.0051891 | 0.0049578 | 0.0049239 | 0.0048123 | 0.0048838 | 0.0046586 | 0.0049065 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
139
140 | Economiser
141 | Econ on/off |  | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | econ | econ | econ | econ | econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | econ | econ | econ | econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | econ | econ | econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | econ | econ | econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | econ | econ | econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ | non econ
142 | Econ flow meter temp | ºC | 21.2558 | 21.2081 | 21.1745 | 20.8263 | 20.7646 | 20.6499 | 20.3445 | 20.2453 | 20.1563 | 19.5587 | 19.4566 | 19.3985 | 18.8064 | 18.8039 | 18.7705 | 16.2135 | 16.1998 | 16.1716 | 15.962 | 15.9573 | 15.9064 | 16.8762 | 16.8481 | 16.824 | 16.7427 | 16.7122 | 16.6864 | 20.2822 | 20.2853 | 20.2947 | 20.3052 | 20.3371 | 20.3234 | 20.3603 | 20.3532 | 20.3469 | 20.4297 | 20.4537 | 20.5397 | 20.6495 | 20.6296 | 20.6726 | 20.8306 | 20.8493 | 20.8209 | 20.7947 | 20.6873 | 20.7126 | 20.6591 | 20.3165 | 20.2904 | 20.0562 | 19.0828 | 18.9286 | 18.5373 | 17.7225 | 17.5964 | 17.4583 | 17.0231 | 16.7869 | 16.6261 | 20.1535 | 20.0278 | 19.9371 | 19.5368 | 19.47 | 19.3929 | 18.4614 | 18.4495 | 18.3912 | 18.23 | 18.1992 | 18.1358 | 18.0441 | 18.0096 | 17.9529 | 17.222 | 17.1901 | 17.1633 | 16.6275 | 16.5101 | 16.3762 | 19.8748 | 19.8541 | 19.9038 | 19.9711 | 20.0154 | 20.0184 | 20.1064 | 20.165 | 20.1863 | 20.5085 | 20.5206 | 20.496 | 20.4816 | 20.4876 | 20.4556 | 20.5798 | 20.4911 | 20.4617 | 20.4527 | 20.314 | 20.3134 | 20.2445 | 20.1679 | 20.0281 | 18.6473 | 18.5668 | 18.421 | 17.626 | 17.5138 | 17.3988 | 17.1151 | 16.9485 | 16.8119 | 20.4248 | 20.3386 | 20.2922 | 19.1581 | 19.1341 | 19.0917 | 18.8376 | 18.791 | 18.7583 | 17.6398 | 17.6151 | 17.574 | 16.454 | 16.4191 | 16.3969 | 16.249 | 16.2016 | 19.3667 | 19.3183 | 19.2715 | 18.293 | 18.2607 | 18.2461 | 18.0021 | 17.8893 | 17.8928 | 17.8683 | 17.2925 | 17.2638 | 17.2338 | 16.4118 | 16.3593 | 16.3619 | 16.3501 | 22.7509 | 22.6864 | 22.669 | 22.6609 | 22.259 | 22.1419 | 22.1063 | 21.5907 | 21.4975 | 21.2153 | 22.2312 | 22.1809 | 22.1396 | 22.0743 | 22.0051 | 21.9113 | 21.866 | 21.7742 | 20.3673 | 20.2953 | 20.2134 | 19.6299 | 19.558 | 19.4647 | 19.3563 | 19.2454 | 19.1962 | 18.7113 | 18.5413 | 18.3979 | 16.5204 | 16.4726 | 16.4283 | 20.0736 | 19.9616 | 19.8733 | 19.3902 | 19.3205 | 19.2398 | 18.6629 | 18.5668 | 18.5253 | 18.3186 | 18.1914 | 18.0475 | 15.3278 | 15.2785 | 15.1971 | 16.9871 | 16.9418 | 16.845 | 16.3478 | 16.2808 | 16.2235 | 17.9042 | 17.9047 | 17.9032 | 17.8792 | 17.8524 | 17.8293 | 18.7127 | 18.6337 | 18.6054 | 18.1197 | 18.0648 | 18.0132 | 19.8962 | 19.6397 | 19.476 | 19.0832 | 19.0016 | 18.8722 | 18.5714 | 18.4379 | 18.2552 | 19.1342 | 19.1011 | 18.9822 | 17.1027 | 17.045 | 16.9975 | 19.8261 | 19.7168 | 19.6358 | 19.3129 | 19.2028 | 19.0622
143 | Econ flow meter Pressure | BarA | 8.6348 | 8.6285 | 8.6243 | 8.5484 | 8.5461 | 8.5221 | 8.4413 | 8.4223 | 8.4045 | 8.2906 | 8.2746 | 8.2558 | 8.1518 | 8.1516 | 8.1439 | 7.6883 | 7.6749 | 7.6756 | 7.6428 | 7.6336 | 7.6292 | 7.799 | 7.7922 | 7.7908 | 7.7675 | 7.7613 | 7.7582 | 8.455 | 8.4602 | 8.4635 | 8.4708 | 8.4702 | 8.4709 | 8.4768 | 8.4757 | 8.4799 | 8.4906 | 8.4938 | 8.5186 | 8.5293 | 8.5373 | 8.5389 | 8.5675 | 8.5767 | 8.5641 | 8.5601 | 8.544 | 8.5434 | 8.5276 | 8.4521 | 8.4365 | 8.3986 | 8.2005 | 8.1648 | 8.0863 | 7.9266 | 7.9036 | 7.8789 | 7.7947 | 7.7753 | 7.7435 | 8.4122 | 8.3863 | 8.3756 | 8.2964 | 8.2792 | 8.2753 | 8.102 | 8.0947 | 8.0819 | 8.0613 | 8.0515 | 8.0407 | 8.0219 | 8.0117 | 8.0032 | 7.8814 | 7.8635 | 7.8615 | 7.7608 | 7.7299 | 7.7267 | 8.3739 | 8.3785 | 8.3743 | 8.3887 | 8.3909 | 8.3951 | 8.4105 | 8.4154 | 8.4131 | 8.4665 | 8.4716 | 8.4632 | 8.4403 | 8.4471 | 8.4529 | 8.4622 | 8.437 | 8.4356 | 8.4334 | 8.4098 | 8.4042 | 8.3926 | 8.3812 | 8.3533 | 8.088 | 8.0736 | 8.0436 | 7.8913 | 7.8766 | 7.8545 | 7.7996 | 7.7697 | 7.7737 | 8.4721 | 8.4522 | 8.4436 | 8.234 | 8.2236 | 8.2227 | 8.1699 | 8.1704 | 8.1603 | 7.9611 | 7.9505 | 7.9479 | 7.7678 | 7.7624 | 7.7525 | 7.7264 | 7.718 | 8.3037 | 8.295 | 8.2789 | 8.0887 | 8.0956 | 8.0862 | 8.0374 | 8.024 | 8.0136 | 8.0114 | 7.8993 | 7.8961 | 7.8928 | 7.7666 | 7.7533 | 7.752 | 7.757 | 8.9966 | 8.9857 | 8.9795 | 8.9769 | 8.8824 | 8.8671 | 8.8562 | 8.7487 | 8.7354 | 8.6794 | 8.8807 | 8.8701 | 8.8601 | 8.8601 | 8.8366 | 8.8188 | 8.803 | 8.7805 | 8.4585 | 8.4446 | 8.4312 | 8.3059 | 8.2927 | 8.2723 | 8.2481 | 8.2316 | 8.2163 | 8.1345 | 8.0984 | 8.0683 | 7.744 | 7.7269 | 7.7258 | 8.4467 | 8.4234 | 8.4077 | 8.3 | 8.284 | 8.2754 | 8.1488 | 8.1331 | 8.1158 | 8.0749 | 8.0532 | 8.0264 | 7.5594 | 7.5504 | 7.5345 | 7.8341 | 7.8246 | 7.8102 | 7.7531 | 7.742 | 7.7261 | 8.0665 | 8.0632 | 8.0628 | 8.0669 | 8.0618 | 8.0629 | 8.1815 | 8.1701 | 8.1636 | 8.0727 | 8.0678 | 8.0516 | 8.4408 | 8.3876 | 8.3531 | 8.2698 | 8.2522 | 8.2204 | 8.1659 | 8.1342 | 8.0997 | 8.2913 | 8.2775 | 8.2599 | 7.9204 | 7.9024 | 7.8954 | 8.4482 | 8.4278 | 8.4046 | 8.3458 | 8.3168 | 8.2942
144 | Econ flow meter gauge | ºC | 34.0352 | 34.0093 | 33.9918 | 33.6757 | 33.6662 | 33.566 | 33.2263 | 33.1462 | 33.071 | 32.5864 | 32.5181 | 32.4375 | 31.9893 | 31.9883 | 31.9553 | 29.9384 | 29.8774 | 29.8808 | 29.7318 | 29.6901 | 29.6699 | 30.4365 | 30.4059 | 30.3994 | 30.2954 | 30.2674 | 30.2532 | 33.2839 | 33.3062 | 33.3199 | 33.3505 | 33.3479 | 33.3512 | 33.3759 | 33.3713 | 33.3888 | 33.4338 | 33.4471 | 33.5513 | 33.596 | 33.6296 | 33.636 | 33.7555 | 33.7941 | 33.7416 | 33.7249 | 33.6576 | 33.6548 | 33.589 | 33.272 | 33.2061 | 33.0461 | 32.1997 | 32.0458 | 31.7048 | 31.0042 | 30.9021 | 30.7927 | 30.417 | 30.33 | 30.1873 | 33.1036 | 32.9939 | 32.9486 | 32.6113 | 32.5375 | 32.5212 | 31.773 | 31.7414 | 31.6856 | 31.5957 | 31.5529 | 31.5059 | 31.4236 | 31.3787 | 31.3413 | 30.8037 | 30.724 | 30.7152 | 30.2651 | 30.1259 | 30.1117 | 32.941 | 32.9605 | 32.943 | 33.0039 | 33.0134 | 33.0309 | 33.0964 | 33.1169 | 33.1072 | 33.3326 | 33.3538 | 33.3188 | 33.2222 | 33.2509 | 33.2754 | 33.3143 | 33.2082 | 33.2022 | 33.1929 | 33.0932 | 33.0697 | 33.0203 | 32.9723 | 32.8538 | 31.7125 | 31.6497 | 31.5184 | 30.8476 | 30.7822 | 30.6841 | 30.4392 | 30.3052 | 30.3232 | 33.3559 | 33.2723 | 33.2362 | 32.344 | 32.2993 | 32.2955 | 32.0675 | 32.0698 | 32.0259 | 31.1564 | 31.1095 | 31.0982 | 30.2964 | 30.2721 | 30.2276 | 30.1104 | 30.0725 | 32.6425 | 32.6054 | 32.5363 | 31.7152 | 31.7453 | 31.7046 | 31.4915 | 31.4329 | 31.387 | 31.3774 | 30.8831 | 30.8691 | 30.8544 | 30.2913 | 30.2314 | 30.2253 | 30.2481 | 35.5125 | 35.4688 | 35.4438 | 35.4332 | 35.0513 | 34.9891 | 34.9445 | 34.5054 | 34.4509 | 34.2201 | 35.0441 | 35.0012 | 34.9607 | 34.9607 | 34.8649 | 34.7922 | 34.7278 | 34.6358 | 33.2986 | 33.2404 | 33.1838 | 32.6518 | 32.5954 | 32.5083 | 32.4043 | 32.3334 | 32.2677 | 31.9142 | 31.7574 | 31.6262 | 30.1895 | 30.1124 | 30.1077 | 33.2493 | 33.1507 | 33.0846 | 32.6266 | 32.5584 | 32.5216 | 31.9763 | 31.9083 | 31.833 | 31.6552 | 31.5604 | 31.4431 | 29.3512 | 29.3101 | 29.237 | 30.5932 | 30.5508 | 30.4864 | 30.2306 | 30.1805 | 30.1087 | 31.6187 | 31.6043 | 31.6023 | 31.6202 | 31.598 | 31.6028 | 32.1179 | 32.0684 | 32.0402 | 31.6455 | 31.6244 | 31.5535 | 33.2244 | 32.9991 | 32.853 | 32.4976 | 32.4221 | 32.2856 | 32.0504 | 31.9129 | 31.7631 | 32.5895 | 32.5303 | 32.4551 | 30.9764 | 30.8971 | 30.8659 | 33.2555 | 33.1693 | 33.0714 | 32.8218 | 32.6984 | 32.6019
145 | Econ flow meter enthalpy | KJ/kg | 229.2561 | 229.189 | 229.1416 | 228.6515 | 228.5648 | 228.4034 | 227.974 | 227.8347 | 227.7096 | 226.871 | 226.7278 | 226.6463 | 225.817 | 225.8134 | 225.7667 | 222.1992 | 222.18 | 222.1409 | 221.8495 | 221.8429 | 221.7721 | 223.1216 | 223.0824 | 223.0489 | 222.9356 | 222.8931 | 222.8572 | 227.8867 | 227.8911 | 227.9042 | 227.9192 | 227.9638 | 227.9447 | 227.9966 | 227.9865 | 227.9778 | 228.094 | 228.1277 | 228.2487 | 228.4029 | 228.3751 | 228.4355 | 228.6577 | 228.684 | 228.6441 | 228.6072 | 228.4562 | 228.4918 | 228.4164 | 227.9347 | 227.8981 | 227.5691 | 226.2039 | 225.988 | 225.4404 | 224.3016 | 224.1256 | 223.9328 | 223.3259 | 222.9971 | 222.7732 | 227.7058 | 227.5292 | 227.402 | 226.8404 | 226.7467 | 226.6386 | 225.3344 | 225.3178 | 225.2362 | 225.0109 | 224.9678 | 224.8792 | 224.751 | 224.7028 | 224.6237 | 223.6038 | 223.5592 | 223.5218 | 222.7753 | 222.6118 | 222.4256 | 227.3147 | 227.2856 | 227.3553 | 227.4498 | 227.512 | 227.5161 | 227.6397 | 227.7219 | 227.7518 | 228.2044 | 228.2214 | 228.1869 | 228.1665 | 228.175 | 228.1301 | 228.3045 | 228.1797 | 228.1385 | 228.1258 | 227.9309 | 227.9301 | 227.8333 | 227.7258 | 227.5293 | 225.594 | 225.4814 | 225.2775 | 224.1667 | 224.0102 | 223.8497 | 223.4541 | 223.2219 | 223.0318 | 228.087 | 227.9658 | 227.9006 | 226.3097 | 226.276 | 226.2166 | 225.8608 | 225.7956 | 225.7498 | 224.1866 | 224.1521 | 224.0948 | 222.5343 | 222.4857 | 222.4547 | 222.2489 | 222.183 | 226.6022 | 226.5344 | 226.4687 | 225.0991 | 225.0542 | 225.0337 | 224.6927 | 224.5352 | 224.5399 | 224.5058 | 223.7021 | 223.6621 | 223.6204 | 222.4756 | 222.4025 | 222.406 | 222.3897 | 231.3662 | 231.275 | 231.2503 | 231.2389 | 230.6711 | 230.5058 | 230.4556 | 229.7283 | 229.5969 | 229.1994 | 230.6319 | 230.5608 | 230.5025 | 230.4105 | 230.3128 | 230.1803 | 230.1165 | 229.987 | 228.0061 | 227.905 | 227.79 | 226.9708 | 226.87 | 226.7391 | 226.5871 | 226.4317 | 226.3628 | 225.6838 | 225.4461 | 225.2454 | 222.6262 | 222.5596 | 222.498 | 227.594 | 227.4368 | 227.3129 | 226.6352 | 226.5374 | 226.4243 | 225.6164 | 225.482 | 225.4238 | 225.1347 | 224.957 | 224.7559 | 220.9689 | 220.9004 | 220.7874 | 223.2763 | 223.2132 | 223.0783 | 222.3865 | 222.2934 | 222.2135 | 224.5565 | 224.5571 | 224.5549 | 224.5216 | 224.4841 | 224.4519 | 225.6863 | 225.5758 | 225.5363 | 224.8571 | 224.7805 | 224.7083 | 227.3453 | 226.9852 | 226.7557 | 226.2053 | 226.0909 | 225.9096 | 225.4887 | 225.3019 | 225.0465 | 226.2767 | 226.2303 | 226.0638 | 223.4381 | 223.3577 | 223.2916 | 227.247 | 227.0936 | 226.98 | 226.5273 | 226.373 | 226.1761
146 | Econ flow meter specific Vol | m3/kg | 0.00081818 | 0.00081806 | 0.00081798 | 0.00081713 | 0.00081698 | 0.0008167 | 0.00081596 | 0.00081572 | 0.00081551 | 0.00081407 | 0.00081382 | 0.00081369 | 0.00081227 | 0.00081227 | 0.00081219 | 0.00080619 | 0.00080616 | 0.0008061 | 0.00080561 | 0.0008056 | 0.00080548 | 0.00080773 | 0.00080766 | 0.00080761 | 0.00080742 | 0.00080735 | 0.00080729 | 0.0008158 | 0.00081581 | 0.00081583 | 0.00081586 | 0.00081594 | 0.0008159 | 0.00081599 | 0.00081597 | 0.00081596 | 0.00081616 | 0.00081622 | 0.00081642 | 0.00081669 | 0.00081664 | 0.00081675 | 0.00081713 | 0.00081718 | 0.00081711 | 0.00081705 | 0.00081678 | 0.00081685 | 0.00081672 | 0.00081589 | 0.00081583 | 0.00081526 | 0.00081293 | 0.00081257 | 0.00081164 | 0.00080972 | 0.00080942 | 0.0008091 | 0.00080808 | 0.00080752 | 0.00080715 | 0.0008155 | 0.0008152 | 0.00081498 | 0.00081401 | 0.00081386 | 0.00081367 | 0.00081145 | 0.00081142 | 0.00081128 | 0.0008109 | 0.00081083 | 0.00081068 | 0.00081046 | 0.00081038 | 0.00081025 | 0.00080853 | 0.00080846 | 0.00080839 | 0.00080715 | 0.00080688 | 0.00080656 | 0.00081482 | 0.00081477 | 0.00081489 | 0.00081506 | 0.00081516 | 0.00081517 | 0.00081538 | 0.00081553 | 0.00081558 | 0.00081636 | 0.00081639 | 0.00081633 | 0.00081631 | 0.00081632 | 0.00081624 | 0.00081654 | 0.00081633 | 0.00081626 | 0.00081624 | 0.0008159 | 0.0008159 | 0.00081573 | 0.00081555 | 0.00081521 | 0.00081191 | 0.00081171 | 0.00081137 | 0.0008095 | 0.00080923 | 0.00080896 | 0.0008083 | 0.00080791 | 0.00080758 | 0.00081615 | 0.00081595 | 0.00081583 | 0.0008131 | 0.00081305 | 0.00081295 | 0.00081234 | 0.00081223 | 0.00081215 | 0.00080951 | 0.00080945 | 0.00080935 | 0.00080673 | 0.00080665 | 0.0008066 | 0.00080626 | 0.00080615 | 0.00081359 | 0.00081348 | 0.00081337 | 0.00081104 | 0.00081096 | 0.00081093 | 0.00081035 | 0.00081009 | 0.0008101 | 0.00081004 | 0.00080869 | 0.00080862 | 0.00080855 | 0.00080663 | 0.00080651 | 0.00080652 | 0.00080649 | 0.00082185 | 0.00082169 | 0.00082164 | 0.00082162 | 0.00082063 | 0.00082034 | 0.00082025 | 0.00081898 | 0.00081875 | 0.00081806 | 0.00082056 | 0.00082044 | 0.00082034 | 0.00082017 | 0.00082 | 0.00081977 | 0.00081966 | 0.00081944 | 0.00081602 | 0.00081584 | 0.00081564 | 0.00081424 | 0.00081407 | 0.00081384 | 0.00081359 | 0.00081332 | 0.0008132 | 0.00081204 | 0.00081164 | 0.0008113 | 0.0008069 | 0.00080679 | 0.00080669 | 0.00081529 | 0.00081502 | 0.00081481 | 0.00081365 | 0.00081349 | 0.00081329 | 0.00081192 | 0.00081169 | 0.0008116 | 0.00081111 | 0.00081081 | 0.00081047 | 0.00080415 | 0.00080403 | 0.00080385 | 0.00080798 | 0.00080788 | 0.00080765 | 0.00080649 | 0.00080633 | 0.0008062 | 0.00081011 | 0.00081011 | 0.00081011 | 0.00081005 | 0.00080998 | 0.00080993 | 0.00081203 | 0.00081184 | 0.00081178 | 0.00081063 | 0.0008105 | 0.00081038 | 0.00081485 | 0.00081424 | 0.00081384 | 0.00081291 | 0.00081271 | 0.00081241 | 0.00081169 | 0.00081138 | 0.00081095 | 0.00081302 | 0.00081295 | 0.00081266 | 0.00080823 | 0.0008081 | 0.00080799 | 0.00081467 | 0.00081441 | 0.00081422 | 0.00081344 | 0.00081318 | 0.00081285
147 | Econ flow meter vol Flow | m^3/hr | 0.064297 | 0.76616 | -0.007497 | -0.036116 | -0.027314 | -0.044967 | -0.022593 | -0.024806 | -0.041476 | -0.030018 | -0.021905 | -0.027117 | -0.029674 | -0.01148 | -0.021462 | -0.005284 | 0.001502 | 0.007895 | -0.011283 | 0.000273 | 0.004108 | -0.012316 | -0.017676 | -0.006366 | -0.003514 | -0.016545 | -0.007349 | -0.03887 | -0.028051 | -0.039411 | -0.043787 | -0.037837 | -0.041132 | -0.026084 | -0.0341 | -0.036854 | -0.035034 | -0.029232 | -0.022839 | -0.043 | -0.031199 | -0.033608 | -0.040148 | -0.031149 | -0.038624 | -0.05013 | -0.044672 | -0.040886 | -0.034985 | 123.9109 | 123.9205 | 123.921 | -0.023478 | -0.022937 | -0.021954 | 0.19771 | 0.083376 | 0.055987 | -0.021806 | -0.007989 | -0.005136 | -0.025937 | -0.043148 | -0.031002 | -0.022691 | -0.036411 | -0.028543 | -0.029477 | -0.030018 | -0.008136 | -0.025593 | -0.025298 | -0.016643 | -0.028887 | -0.012808 | -0.012021 | -0.012168 | -0.040689 | -0.005235 | -0.012611 | -0.022937 | -0.003956 | -0.04541 | -0.021216 | -0.030412 | -0.047475 | -0.027412 | -0.035132 | -0.026035 | -0.033411 | -0.033805 | -0.033067 | -0.020429 | -0.043 | -0.031936 | -0.060654 | -0.03351 | -0.027166 | 30.7931 | 32.1068 | 29.751 | 41.5055 | 55.2093 | 43.9462 | 41.5772 | 39.9145 | -0.025396 | -0.027461 | -0.019594 | -0.021167 | -0.027068 | -0.012021 | -0.016496 | 0.008927 | -0.009169 | -0.024314 | -0.040247 | -0.038034 | -0.042902 | -0.01861 | -0.02633 | -0.035723 | -0.025347 | -0.016987 | -0.014627 | -0.006464 | -0.005874 | -0.002973 | 0.002338 | -0.005923 | -0.004497 | 0.003518 | -0.020479 | -0.025199 | -0.03705 | -0.004448 | -0.016545 | -0.022052 | -0.015955 | -0.028002 | -0.013496 | -0.018659 | -0.022888 | -0.021659 | -0.004596 | -0.004104 | -0.011529 | -0.009267 | -0.00848 | 35.002 | 29.0561 | 34.1746 | 30.6214 | -0.045016 | -0.039656 | -0.041427 | -0.031199 | -0.028789 | -0.038329 | -0.040148 | -0.047524 | -0.053769 | -0.035723 | -0.027855 | -0.059621 | -0.042509 | -0.023429 | -0.022691 | -0.033952 | -0.045016 | -0.010742 | -0.050868 | -0.024118 | -0.02515 | -0.036411 | -0.031641 | 29.5967 | 25.9915 | 29.7857 | 0.002043 | -0.012168 | -0.004104 | -0.043246 | -0.027215 | -0.03469 | -0.015512 | -0.017922 | 0.25583 | -0.023773 | -0.011234 | -0.027363 | 41.3327 | 41.3405 | 41.3113 | 0.006419 | -0.000612 | -0.008726 | -0.006267 | -0.00971 | -0.020577 | 0.008386 | 0.001404 | 0.004059 | -0.013889 | -0.00789 | -0.017135 | -0.027068 | -0.020036 | -0.004497 | -0.021413 | -0.02156 | -0.013791 | -0.009906 | -0.015414 | -0.027511 | -0.038919 | -0.013348 | -0.028543 | 1.1736 | 2.0966 | 1.7481 | -0.021511 | -0.005923 | -0.002924 | 38.8679 | 27.6776 | 27.6752 | -0.01802 | 0.004698 | -0.016004 | -0.029232 | -0.012562 | -0.021856 | -0.025347 | -0.02815 | -0.020184
148 | Econ flow meter mass Flow | kg/s | 0.021829 | 0.26015 | -0.0025459 | -0.012277 | -0.009287 | -0.015294 | -0.0076913 | -0.0084472 | -0.014127 | -0.010243 | -0.0074767 | -0.0092572 | -0.010148 | -0.0039259 | -0.0073403 | -0.0018206 | 0.00051754 | 0.0027206 | -0.0038904 | 9.4132e-05 | 0.0014167 | -0.0042355 | -0.0060793 | -0.0021896 | -0.0012089 | -0.0056925 | -0.0025287 | -0.013235 | -0.0095512 | -0.013419 | -0.014908 | -0.012881 | -0.014004 | -0.0088795 | -0.011608 | -0.012546 | -0.011924 | -0.0099483 | -0.0077707 | -0.014625 | -0.010612 | -0.01143 | -0.013648 | -0.010588 | -0.01313 | -0.017043 | -0.015192 | -0.013904 | -0.011899 | 42.1866 | 42.193 | 42.2226 | -0.0080224 | -0.0078411 | -0.0075136 | 0.067824 | 0.028613 | 0.019221 | -0.0074958 | -0.0027481 | -0.0017675 | -0.0088347 | -0.014703 | -0.010567 | -0.0077432 | -0.012427 | -0.0097443 | -0.010091 | -0.010276 | -0.0027857 | -0.008767 | -0.0086667 | -0.0057027 | -0.0099007 | -0.0043902 | -0.0041212 | -0.0041804 | -0.01398 | -0.0017988 | -0.00434 | -0.0078963 | -0.0013624 | -0.015481 | -0.0072331 | -0.010367 | -0.01618 | -0.009341 | -0.011972 | -0.0088694 | -0.01138 | -0.011514 | -0.011251 | -0.006951 | -0.014632 | -0.010867 | -0.020639 | -0.011404 | -0.0092415 | 10.4781 | 10.9261 | 10.1247 | 14.1308 | 18.7963 | 14.9648 | 14.1613 | 13.6006 | -0.0086888 | -0.0093975 | -0.0067081 | -0.0072634 | -0.0092914 | -0.0041277 | -0.005669 | 0.0030693 | -0.0031538 | -0.0082753 | -0.013702 | -0.01295 | -0.014656 | -0.0063581 | -0.0089968 | -0.012215 | -0.0086686 | -0.00581 | -0.0050192 | -0.0022182 | -0.002016 | -0.0010237 | 0.00080511 | -0.0020398 | -0.0015493 | 0.0012122 | -0.006992 | -0.0086047 | -0.012653 | -0.0015234 | -0.0056671 | -0.0075537 | -0.0054691 | -0.0096019 | -0.0046277 | -0.0063985 | -0.0078618 | -0.0074403 | -0.001579 | -0.0014133 | -0.0039708 | -0.0031917 | -0.0029207 | 11.8304 | 9.8226 | 11.5536 | 10.3526 | -0.015238 | -0.013428 | -0.014029 | -0.010582 | -0.0097672 | -0.013015 | -0.013591 | -0.01609 | -0.018207 | -0.012099 | -0.009436 | -0.020202 | -0.014406 | -0.0079421 | -0.0077242 | -0.01156 | -0.015331 | -0.0036646 | -0.017357 | -0.0082318 | -0.0085868 | -0.012436 | -0.010808 | 10.1242 | 8.8954 | 10.1982 | 0.00070331 | -0.0041894 | -0.0014132 | -0.014734 | -0.0092755 | -0.011826 | -0.0052957 | -0.0061198 | 0.087378 | -0.0081333 | -0.0038445 | -0.0093653 | 14.1551 | 14.163 | 14.1589 | 0.0022173 | -0.00021143 | -0.0030154 | -0.0021545 | -0.0033387 | -0.0070771 | 0.0028884 | 0.00048367 | 0.0013985 | -0.0047624 | -0.0027054 | -0.0058754 | -0.009282 | -0.0068712 | -0.0015423 | -0.0073249 | -0.0073769 | -0.0047191 | -0.0033945 | -0.0052828 | -0.0094301 | -0.013267 | -0.0045537 | -0.0097422 | 0.40102 | 0.7166 | 0.59769 | -0.0073615 | -0.0020278 | -0.0010016 | 13.2796 | 9.4572 | 9.4597 | -0.0061932 | 0.0016149 | -0.005502 | -0.0099672 | -0.0042846 | -0.0074564 | -0.0086556 | -0.0096158 | -0.0068976
149 | Econ @ comp temp | ºC | 21.2558 | 21.2081 | 21.1745 | 20.8263 | 20.7646 | 20.6499 | 20.3445 | 20.2453 | 20.1563 | 19.5587 | 19.4566 | 19.3985 | 18.8064 | 18.8039 | 18.7705 | 16.2135 | 16.1998 | 16.1716 | 15.962 | 15.9573 | 15.9064 | 16.8762 | 16.8481 | 16.824 | 16.7427 | 16.7122 | 16.6864 | 20.2822 | 20.2853 | 20.2947 | 20.3052 | 20.3371 | 20.3234 | 20.3603 | 20.3532 | 20.3469 | 20.4297 | 20.4537 | 20.5397 | 20.6495 | 20.6296 | 20.6726 | 20.8306 | 20.8493 | 20.8209 | 20.7947 | 20.6873 | 20.7126 | 20.6591 | 20.3165 | 20.2904 | 20.0562 | 19.0828 | 18.9286 | 18.5373 | 17.7225 | 17.5964 | 17.4583 | 17.0231 | 16.7869 | 16.6261 | 20.1535 | 20.0278 | 19.9371 | 19.5368 | 19.47 | 19.3929 | 18.4614 | 18.4495 | 18.3912 | 18.23 | 18.1992 | 18.1358 | 18.0441 | 18.0096 | 17.9529 | 17.222 | 17.1901 | 17.1633 | 16.6275 | 16.5101 | 16.3762 | 19.8748 | 19.8541 | 19.9038 | 19.9711 | 20.0154 | 20.0184 | 20.1064 | 20.165 | 20.1863 | 20.5085 | 20.5206 | 20.496 | 20.4816 | 20.4876 | 20.4556 | 20.5798 | 20.4911 | 20.4617 | 20.4527 | 20.314 | 20.3134 | 20.2445 | 20.1679 | 20.0281 | 18.6473 | 18.5668 | 18.421 | 17.626 | 17.5138 | 17.3988 | 17.1151 | 16.9485 | 16.8119 | 20.4248 | 20.3386 | 20.2922 | 19.1581 | 19.1341 | 19.0917 | 18.8376 | 18.791 | 18.7583 | 17.6398 | 17.6151 | 17.574 | 16.454 | 16.4191 | 16.3969 | 16.249 | 16.2016 | 19.3667 | 19.3183 | 19.2715 | 18.293 | 18.2607 | 18.2461 | 18.0021 | 17.8893 | 17.8928 | 17.8683 | 17.2925 | 17.2638 | 17.2338 | 16.4118 | 16.3593 | 16.3619 | 16.3501 | 22.7509 | 22.6864 | 22.669 | 22.6609 | 22.259 | 22.1419 | 22.1063 | 21.5907 | 21.4975 | 21.2153 | 22.2312 | 22.1809 | 22.1396 | 22.0743 | 22.0051 | 21.9113 | 21.866 | 21.7742 | 20.3673 | 20.2953 | 20.2134 | 19.6299 | 19.558 | 19.4647 | 19.3563 | 19.2454 | 19.1962 | 18.7113 | 18.5413 | 18.3979 | 16.5204 | 16.4726 | 16.4283 | 20.0736 | 19.9616 | 19.8733 | 19.3902 | 19.3205 | 19.2398 | 18.6629 | 18.5668 | 18.5253 | 18.3186 | 18.1914 | 18.0475 | 15.3278 | 15.2785 | 15.1971 | 16.9871 | 16.9418 | 16.845 | 16.3478 | 16.2808 | 16.2235 | 17.9042 | 17.9047 | 17.9032 | 17.8792 | 17.8524 | 17.8293 | 18.7127 | 18.6337 | 18.6054 | 18.1197 | 18.0648 | 18.0132 | 19.8962 | 19.6397 | 19.476 | 19.0832 | 19.0016 | 18.8722 | 18.5714 | 18.4379 | 18.2552 | 19.1342 | 19.1011 | 18.9822 | 17.1027 | 17.045 | 16.9975 | 19.8261 | 19.7168 | 19.6358 | 19.3129 | 19.2028 | 19.0622
150 | Econ @ comp Pressure | BarA | 8.6348 | 8.6285 | 8.6243 | 8.5484 | 8.5461 | 8.5221 | 8.4413 | 8.4223 | 8.4045 | 8.2906 | 8.2746 | 8.2558 | 8.1518 | 8.1516 | 8.1439 | 7.6883 | 7.6749 | 7.6756 | 7.6428 | 7.6336 | 7.6292 | 7.799 | 7.7922 | 7.7908 | 7.7675 | 7.7613 | 7.7582 | 8.455 | 8.4602 | 8.4635 | 8.4708 | 8.4702 | 8.4709 | 8.4768 | 8.4757 | 8.4799 | 8.4906 | 8.4938 | 8.5186 | 8.5293 | 8.5373 | 8.5389 | 8.5675 | 8.5767 | 8.5641 | 8.5601 | 8.544 | 8.5434 | 8.5276 | 8.4521 | 8.4365 | 8.3986 | 8.2005 | 8.1648 | 8.0863 | 7.9266 | 7.9036 | 7.8789 | 7.7947 | 7.7753 | 7.7435 | 8.4122 | 8.3863 | 8.3756 | 8.2964 | 8.2792 | 8.2753 | 8.102 | 8.0947 | 8.0819 | 8.0613 | 8.0515 | 8.0407 | 8.0219 | 8.0117 | 8.0032 | 7.8814 | 7.8635 | 7.8615 | 7.7608 | 7.7299 | 7.7267 | 8.3739 | 8.3785 | 8.3743 | 8.3887 | 8.3909 | 8.3951 | 8.4105 | 8.4154 | 8.4131 | 8.4665 | 8.4716 | 8.4632 | 8.4403 | 8.4471 | 8.4529 | 8.4622 | 8.437 | 8.4356 | 8.4334 | 8.4098 | 8.4042 | 8.3926 | 8.3812 | 8.3533 | 8.088 | 8.0736 | 8.0436 | 7.8913 | 7.8766 | 7.8545 | 7.7996 | 7.7697 | 7.7737 | 8.4721 | 8.4522 | 8.4436 | 8.234 | 8.2236 | 8.2227 | 8.1699 | 8.1704 | 8.1603 | 7.9611 | 7.9505 | 7.9479 | 7.7678 | 7.7624 | 7.7525 | 7.7264 | 7.718 | 8.3037 | 8.295 | 8.2789 | 8.0887 | 8.0956 | 8.0862 | 8.0374 | 8.024 | 8.0136 | 8.0114 | 7.8993 | 7.8961 | 7.8928 | 7.7666 | 7.7533 | 7.752 | 7.757 | 8.9966 | 8.9857 | 8.9795 | 8.9769 | 8.8824 | 8.8671 | 8.8562 | 8.7487 | 8.7354 | 8.6794 | 8.8807 | 8.8701 | 8.8601 | 8.8601 | 8.8366 | 8.8188 | 8.803 | 8.7805 | 8.4585 | 8.4446 | 8.4312 | 8.3059 | 8.2927 | 8.2723 | 8.2481 | 8.2316 | 8.2163 | 8.1345 | 8.0984 | 8.0683 | 7.744 | 7.7269 | 7.7258 | 8.4467 | 8.4234 | 8.4077 | 8.3 | 8.284 | 8.2754 | 8.1488 | 8.1331 | 8.1158 | 8.0749 | 8.0532 | 8.0264 | 7.5594 | 7.5504 | 7.5345 | 7.8341 | 7.8246 | 7.8102 | 7.7531 | 7.742 | 7.7261 | 8.0665 | 8.0632 | 8.0628 | 8.0669 | 8.0618 | 8.0629 | 8.1815 | 8.1701 | 8.1636 | 8.0727 | 8.0678 | 8.0516 | 8.4408 | 8.3876 | 8.3531 | 8.2698 | 8.2522 | 8.2204 | 8.1659 | 8.1342 | 8.0997 | 8.2913 | 8.2775 | 8.2599 | 7.9204 | 7.9024 | 7.8954 | 8.4482 | 8.4278 | 8.4046 | 8.3458 | 8.3168 | 8.2942
151 | Econ @ comp SH | ºC | -12.7794 | -12.8012 | -12.8173 | -12.8494 | -12.9017 | -12.9162 | -12.8819 | -12.9009 | -12.9147 | -13.0276 | -13.0615 | -13.039 | -13.1829 | -13.1844 | -13.1849 | -13.7249 | -13.6776 | -13.7092 | -13.7698 | -13.7328 | -13.7635 | -13.5603 | -13.5578 | -13.5754 | -13.5527 | -13.5552 | -13.5668 | -13.0017 | -13.0208 | -13.0252 | -13.0453 | -13.0109 | -13.0278 | -13.0155 | -13.0181 | -13.0419 | -13.0041 | -12.9934 | -13.0115 | -12.9466 | -13 | -12.9634 | -12.9249 | -12.9448 | -12.9206 | -12.9301 | -12.9702 | -12.9422 | -12.9299 | -12.9556 | -12.9157 | -12.9899 | -13.1169 | -13.1171 | -13.1675 | -13.2817 | -13.3056 | -13.3344 | -13.3939 | -13.5431 | -13.5612 | -12.9501 | -12.9662 | -13.0115 | -13.0745 | -13.0674 | -13.1283 | -13.3117 | -13.2919 | -13.2944 | -13.3657 | -13.3538 | -13.3701 | -13.3796 | -13.3691 | -13.3884 | -13.5817 | -13.5339 | -13.5519 | -13.6376 | -13.6158 | -13.7355 | -13.0662 | -13.1064 | -13.0392 | -13.0328 | -12.9979 | -13.0125 | -12.9901 | -12.9519 | -12.9209 | -12.8241 | -12.8332 | -12.8227 | -12.7406 | -12.7633 | -12.8198 | -12.7345 | -12.7171 | -12.7405 | -12.7402 | -12.7793 | -12.7563 | -12.7758 | -12.8044 | -12.8258 | -13.0652 | -13.0829 | -13.0974 | -13.2217 | -13.2684 | -13.2853 | -13.3241 | -13.3567 | -13.5113 | -12.9311 | -12.9337 | -12.944 | -13.1859 | -13.1652 | -13.2038 | -13.2299 | -13.2788 | -13.2676 | -13.5166 | -13.4944 | -13.5242 | -13.8423 | -13.8529 | -13.8307 | -13.8614 | -13.871 | -13.2758 | -13.2872 | -13.2648 | -13.4222 | -13.4846 | -13.4585 | -13.4894 | -13.5436 | -13.4942 | -13.5091 | -13.5907 | -13.6053 | -13.6205 | -13.8795 | -13.8721 | -13.8635 | -13.8981 | -12.7616 | -12.7823 | -12.7749 | -12.7722 | -12.7923 | -12.8472 | -12.8382 | -12.9147 | -12.9534 | -13.0048 | -12.8129 | -12.8204 | -12.8211 | -12.8864 | -12.8598 | -12.881 | -12.8617 | -12.8616 | -12.9313 | -12.9451 | -12.9704 | -13.0219 | -13.0374 | -13.0437 | -13.0481 | -13.088 | -13.0715 | -13.203 | -13.2161 | -13.2283 | -13.6691 | -13.6399 | -13.6795 | -13.1757 | -13.189 | -13.2112 | -13.2364 | -13.2379 | -13.2818 | -13.3135 | -13.3415 | -13.3077 | -13.3367 | -13.369 | -13.3956 | -14.0234 | -14.0316 | -14.04 | -13.6061 | -13.6089 | -13.6414 | -13.8828 | -13.8996 | -13.8852 | -13.7144 | -13.6996 | -13.6991 | -13.741 | -13.7457 | -13.7735 | -13.4053 | -13.4347 | -13.4347 | -13.5257 | -13.5595 | -13.5403 | -13.3281 | -13.3595 | -13.377 | -13.4144 | -13.4206 | -13.4134 | -13.479 | -13.475 | -13.5079 | -13.4553 | -13.4292 | -13.4729 | -13.8737 | -13.8521 | -13.8684 | -13.4294 | -13.4525 | -13.4356 | -13.5089 | -13.4956 | -13.5396
152 | Econ @ comp gauge | ºC | 34.0352 | 34.0093 | 33.9918 | 33.6757 | 33.6662 | 33.566 | 33.2263 | 33.1462 | 33.071 | 32.5864 | 32.5181 | 32.4375 | 31.9893 | 31.9883 | 31.9553 | 29.9384 | 29.8774 | 29.8808 | 29.7318 | 29.6901 | 29.6699 | 30.4365 | 30.4059 | 30.3994 | 30.2954 | 30.2674 | 30.2532 | 33.2839 | 33.3062 | 33.3199 | 33.3505 | 33.3479 | 33.3512 | 33.3759 | 33.3713 | 33.3888 | 33.4338 | 33.4471 | 33.5513 | 33.596 | 33.6296 | 33.636 | 33.7555 | 33.7941 | 33.7416 | 33.7249 | 33.6576 | 33.6548 | 33.589 | 33.272 | 33.2061 | 33.0461 | 32.1997 | 32.0458 | 31.7048 | 31.0042 | 30.9021 | 30.7927 | 30.417 | 30.33 | 30.1873 | 33.1036 | 32.9939 | 32.9486 | 32.6113 | 32.5375 | 32.5212 | 31.773 | 31.7414 | 31.6856 | 31.5957 | 31.5529 | 31.5059 | 31.4236 | 31.3787 | 31.3413 | 30.8037 | 30.724 | 30.7152 | 30.2651 | 30.1259 | 30.1117 | 32.941 | 32.9605 | 32.943 | 33.0039 | 33.0134 | 33.0309 | 33.0964 | 33.1169 | 33.1072 | 33.3326 | 33.3538 | 33.3188 | 33.2222 | 33.2509 | 33.2754 | 33.3143 | 33.2082 | 33.2022 | 33.1929 | 33.0932 | 33.0697 | 33.0203 | 32.9723 | 32.8538 | 31.7125 | 31.6497 | 31.5184 | 30.8476 | 30.7822 | 30.6841 | 30.4392 | 30.3052 | 30.3232 | 33.3559 | 33.2723 | 33.2362 | 32.344 | 32.2993 | 32.2955 | 32.0675 | 32.0698 | 32.0259 | 31.1564 | 31.1095 | 31.0982 | 30.2964 | 30.2721 | 30.2276 | 30.1104 | 30.0725 | 32.6425 | 32.6054 | 32.5363 | 31.7152 | 31.7453 | 31.7046 | 31.4915 | 31.4329 | 31.387 | 31.3774 | 30.8831 | 30.8691 | 30.8544 | 30.2913 | 30.2314 | 30.2253 | 30.2481 | 35.5125 | 35.4688 | 35.4438 | 35.4332 | 35.0513 | 34.9891 | 34.9445 | 34.5054 | 34.4509 | 34.2201 | 35.0441 | 35.0012 | 34.9607 | 34.9607 | 34.8649 | 34.7922 | 34.7278 | 34.6358 | 33.2986 | 33.2404 | 33.1838 | 32.6518 | 32.5954 | 32.5083 | 32.4043 | 32.3334 | 32.2677 | 31.9142 | 31.7574 | 31.6262 | 30.1895 | 30.1124 | 30.1077 | 33.2493 | 33.1507 | 33.0846 | 32.6266 | 32.5584 | 32.5216 | 31.9763 | 31.9083 | 31.833 | 31.6552 | 31.5604 | 31.4431 | 29.3512 | 29.3101 | 29.237 | 30.5932 | 30.5508 | 30.4864 | 30.2306 | 30.1805 | 30.1087 | 31.6187 | 31.6043 | 31.6023 | 31.6202 | 31.598 | 31.6028 | 32.1179 | 32.0684 | 32.0402 | 31.6455 | 31.6244 | 31.5535 | 33.2244 | 32.9991 | 32.853 | 32.4976 | 32.4221 | 32.2856 | 32.0504 | 31.9129 | 31.7631 | 32.5895 | 32.5303 | 32.4551 | 30.9764 | 30.8971 | 30.8659 | 33.2555 | 33.1693 | 33.0714 | 32.8218 | 32.6984 | 32.6019
153 | Econ @ comp enthalpy | KJ/kg | 229.2561 | 229.189 | 229.1416 | 228.6515 | 228.5648 | 228.4034 | 227.974 | 227.8347 | 227.7096 | 226.871 | 226.7278 | 226.6463 | 225.817 | 225.8134 | 225.7667 | 222.1992 | 222.18 | 222.1409 | 221.8495 | 221.8429 | 221.7721 | 223.1216 | 223.0824 | 223.0489 | 222.9356 | 222.8931 | 222.8572 | 227.8867 | 227.8911 | 227.9042 | 227.9192 | 227.9638 | 227.9447 | 227.9966 | 227.9865 | 227.9778 | 228.094 | 228.1277 | 228.2487 | 228.4029 | 228.3751 | 228.4355 | 228.6577 | 228.684 | 228.6441 | 228.6072 | 228.4562 | 228.4918 | 228.4164 | 227.9347 | 227.8981 | 227.5691 | 226.2039 | 225.988 | 225.4404 | 224.3016 | 224.1256 | 223.9328 | 223.3259 | 222.9971 | 222.7732 | 227.7058 | 227.5292 | 227.402 | 226.8404 | 226.7467 | 226.6386 | 225.3344 | 225.3178 | 225.2362 | 225.0109 | 224.9678 | 224.8792 | 224.751 | 224.7028 | 224.6237 | 223.6038 | 223.5592 | 223.5218 | 222.7753 | 222.6118 | 222.4256 | 227.3147 | 227.2856 | 227.3553 | 227.4498 | 227.512 | 227.5161 | 227.6397 | 227.7219 | 227.7518 | 228.2044 | 228.2214 | 228.1869 | 228.1665 | 228.175 | 228.1301 | 228.3045 | 228.1797 | 228.1385 | 228.1258 | 227.9309 | 227.9301 | 227.8333 | 227.7258 | 227.5293 | 225.594 | 225.4814 | 225.2775 | 224.1667 | 224.0102 | 223.8497 | 223.4541 | 223.2219 | 223.0318 | 228.087 | 227.9658 | 227.9006 | 226.3097 | 226.276 | 226.2166 | 225.8608 | 225.7956 | 225.7498 | 224.1866 | 224.1521 | 224.0948 | 222.5343 | 222.4857 | 222.4547 | 222.2489 | 222.183 | 226.6022 | 226.5344 | 226.4687 | 225.0991 | 225.0542 | 225.0337 | 224.6927 | 224.5352 | 224.5399 | 224.5058 | 223.7021 | 223.6621 | 223.6204 | 222.4756 | 222.4025 | 222.406 | 222.3897 | 231.3662 | 231.275 | 231.2503 | 231.2389 | 230.6711 | 230.5058 | 230.4556 | 229.7283 | 229.5969 | 229.1994 | 230.6319 | 230.5608 | 230.5025 | 230.4105 | 230.3128 | 230.1803 | 230.1165 | 229.987 | 228.0061 | 227.905 | 227.79 | 226.9708 | 226.87 | 226.7391 | 226.5871 | 226.4317 | 226.3628 | 225.6838 | 225.4461 | 225.2454 | 222.6262 | 222.5596 | 222.498 | 227.594 | 227.4368 | 227.3129 | 226.6352 | 226.5374 | 226.4243 | 225.6164 | 225.482 | 225.4238 | 225.1347 | 224.957 | 224.7559 | 220.9689 | 220.9004 | 220.7874 | 223.2763 | 223.2132 | 223.0783 | 222.3865 | 222.2934 | 222.2135 | 224.5565 | 224.5571 | 224.5549 | 224.5216 | 224.4841 | 224.4519 | 225.6863 | 225.5758 | 225.5363 | 224.8571 | 224.7805 | 224.7083 | 227.3453 | 226.9852 | 226.7557 | 226.2053 | 226.0909 | 225.9096 | 225.4887 | 225.3019 | 225.0465 | 226.2767 | 226.2303 | 226.0638 | 223.4381 | 223.3577 | 223.2916 | 227.247 | 227.0936 | 226.98 | 226.5273 | 226.373 | 226.1761
154 | Econ @ comp specific Vol | m3/kg | 0.00081818 | 0.00081806 | 0.00081798 | 0.00081713 | 0.00081698 | 0.0008167 | 0.00081596 | 0.00081572 | 0.00081551 | 0.00081407 | 0.00081382 | 0.00081369 | 0.00081227 | 0.00081227 | 0.00081219 | 0.00080619 | 0.00080616 | 0.0008061 | 0.00080561 | 0.0008056 | 0.00080548 | 0.00080773 | 0.00080766 | 0.00080761 | 0.00080742 | 0.00080735 | 0.00080729 | 0.0008158 | 0.00081581 | 0.00081583 | 0.00081586 | 0.00081594 | 0.0008159 | 0.00081599 | 0.00081597 | 0.00081596 | 0.00081616 | 0.00081622 | 0.00081642 | 0.00081669 | 0.00081664 | 0.00081675 | 0.00081713 | 0.00081718 | 0.00081711 | 0.00081705 | 0.00081678 | 0.00081685 | 0.00081672 | 0.00081589 | 0.00081583 | 0.00081526 | 0.00081293 | 0.00081257 | 0.00081164 | 0.00080972 | 0.00080942 | 0.0008091 | 0.00080808 | 0.00080752 | 0.00080715 | 0.0008155 | 0.0008152 | 0.00081498 | 0.00081401 | 0.00081386 | 0.00081367 | 0.00081145 | 0.00081142 | 0.00081128 | 0.0008109 | 0.00081083 | 0.00081068 | 0.00081046 | 0.00081038 | 0.00081025 | 0.00080853 | 0.00080846 | 0.00080839 | 0.00080715 | 0.00080688 | 0.00080656 | 0.00081482 | 0.00081477 | 0.00081489 | 0.00081506 | 0.00081516 | 0.00081517 | 0.00081538 | 0.00081553 | 0.00081558 | 0.00081636 | 0.00081639 | 0.00081633 | 0.00081631 | 0.00081632 | 0.00081624 | 0.00081654 | 0.00081633 | 0.00081626 | 0.00081624 | 0.0008159 | 0.0008159 | 0.00081573 | 0.00081555 | 0.00081521 | 0.00081191 | 0.00081171 | 0.00081137 | 0.0008095 | 0.00080923 | 0.00080896 | 0.0008083 | 0.00080791 | 0.00080758 | 0.00081615 | 0.00081595 | 0.00081583 | 0.0008131 | 0.00081305 | 0.00081295 | 0.00081234 | 0.00081223 | 0.00081215 | 0.00080951 | 0.00080945 | 0.00080935 | 0.00080673 | 0.00080665 | 0.0008066 | 0.00080626 | 0.00080615 | 0.00081359 | 0.00081348 | 0.00081337 | 0.00081104 | 0.00081096 | 0.00081093 | 0.00081035 | 0.00081009 | 0.0008101 | 0.00081004 | 0.00080869 | 0.00080862 | 0.00080855 | 0.00080663 | 0.00080651 | 0.00080652 | 0.00080649 | 0.00082185 | 0.00082169 | 0.00082164 | 0.00082162 | 0.00082063 | 0.00082034 | 0.00082025 | 0.00081898 | 0.00081875 | 0.00081806 | 0.00082056 | 0.00082044 | 0.00082034 | 0.00082017 | 0.00082 | 0.00081977 | 0.00081966 | 0.00081944 | 0.00081602 | 0.00081584 | 0.00081564 | 0.00081424 | 0.00081407 | 0.00081384 | 0.00081359 | 0.00081332 | 0.0008132 | 0.00081204 | 0.00081164 | 0.0008113 | 0.0008069 | 0.00080679 | 0.00080669 | 0.00081529 | 0.00081502 | 0.00081481 | 0.00081365 | 0.00081349 | 0.00081329 | 0.00081192 | 0.00081169 | 0.0008116 | 0.00081111 | 0.00081081 | 0.00081047 | 0.00080415 | 0.00080403 | 0.00080385 | 0.00080798 | 0.00080788 | 0.00080765 | 0.00080649 | 0.00080633 | 0.0008062 | 0.00081011 | 0.00081011 | 0.00081011 | 0.00081005 | 0.00080998 | 0.00080993 | 0.00081203 | 0.00081184 | 0.00081178 | 0.00081063 | 0.0008105 | 0.00081038 | 0.00081485 | 0.00081424 | 0.00081384 | 0.00081291 | 0.00081271 | 0.00081241 | 0.00081169 | 0.00081138 | 0.00081095 | 0.00081302 | 0.00081295 | 0.00081266 | 0.00080823 | 0.0008081 | 0.00080799 | 0.00081467 | 0.00081441 | 0.00081422 | 0.00081344 | 0.00081318 | 0.00081285
155 | Econ @ comp vol Flow | m^3/hr | 0.064297 | 0.76616 | -0.007497 | -0.036116 | -0.027314 | -0.044967 | -0.022593 | -0.024806 | -0.041476 | -0.030018 | -0.021905 | -0.027117 | -0.029674 | -0.01148 | -0.021462 | -0.005284 | 0.001502 | 0.007895 | -0.011283 | 0.000273 | 0.004108 | -0.012316 | -0.017676 | -0.006366 | -0.003514 | -0.016545 | -0.007349 | -0.03887 | -0.028051 | -0.039411 | -0.043787 | -0.037837 | -0.041132 | -0.026084 | -0.0341 | -0.036854 | -0.035034 | -0.029232 | -0.022839 | -0.043 | -0.031199 | -0.033608 | -0.040148 | -0.031149 | -0.038624 | -0.05013 | -0.044672 | -0.040886 | -0.034985 | 123.9109 | 123.9205 | 123.921 | -0.023478 | -0.022937 | -0.021954 | 0.19771 | 0.083376 | 0.055987 | -0.021806 | -0.007989 | -0.005136 | -0.025937 | -0.043148 | -0.031002 | -0.022691 | -0.036411 | -0.028543 | -0.029477 | -0.030018 | -0.008136 | -0.025593 | -0.025298 | -0.016643 | -0.028887 | -0.012808 | -0.012021 | -0.012168 | -0.040689 | -0.005235 | -0.012611 | -0.022937 | -0.003956 | -0.04541 | -0.021216 | -0.030412 | -0.047475 | -0.027412 | -0.035132 | -0.026035 | -0.033411 | -0.033805 | -0.033067 | -0.020429 | -0.043 | -0.031936 | -0.060654 | -0.03351 | -0.027166 | 30.7931 | 32.1068 | 29.751 | 41.5055 | 55.2093 | 43.9462 | 41.5772 | 39.9145 | -0.025396 | -0.027461 | -0.019594 | -0.021167 | -0.027068 | -0.012021 | -0.016496 | 0.008927 | -0.009169 | -0.024314 | -0.040247 | -0.038034 | -0.042902 | -0.01861 | -0.02633 | -0.035723 | -0.025347 | -0.016987 | -0.014627 | -0.006464 | -0.005874 | -0.002973 | 0.002338 | -0.005923 | -0.004497 | 0.003518 | -0.020479 | -0.025199 | -0.03705 | -0.004448 | -0.016545 | -0.022052 | -0.015955 | -0.028002 | -0.013496 | -0.018659 | -0.022888 | -0.021659 | -0.004596 | -0.004104 | -0.011529 | -0.009267 | -0.00848 | 35.002 | 29.0561 | 34.1746 | 30.6214 | -0.045016 | -0.039656 | -0.041427 | -0.031199 | -0.028789 | -0.038329 | -0.040148 | -0.047524 | -0.053769 | -0.035723 | -0.027855 | -0.059621 | -0.042509 | -0.023429 | -0.022691 | -0.033952 | -0.045016 | -0.010742 | -0.050868 | -0.024118 | -0.02515 | -0.036411 | -0.031641 | 29.5967 | 25.9915 | 29.7857 | 0.002043 | -0.012168 | -0.004104 | -0.043246 | -0.027215 | -0.03469 | -0.015512 | -0.017922 | 0.25583 | -0.023773 | -0.011234 | -0.027363 | 41.3327 | 41.3405 | 41.3113 | 0.006419 | -0.000612 | -0.008726 | -0.006267 | -0.00971 | -0.020577 | 0.008386 | 0.001404 | 0.004059 | -0.013889 | -0.00789 | -0.017135 | -0.027068 | -0.020036 | -0.004497 | -0.021413 | -0.02156 | -0.013791 | -0.009906 | -0.015414 | -0.027511 | -0.038919 | -0.013348 | -0.028543 | 1.1736 | 2.0966 | 1.7481 | -0.021511 | -0.005923 | -0.002924 | 38.8679 | 27.6776 | 27.6752 | -0.01802 | 0.004698 | -0.016004 | -0.029232 | -0.012562 | -0.021856 | -0.025347 | -0.02815 | -0.020184
156 | assumed approach of econ liquid to econ gauge | ºC | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
157 | target superheat economiser port | ºC | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
158 | Liquid injection
159 | LI flow meter Temp | ºC | 19.9976 | 19.9571 | 19.9165 | 19.604 | 19.5857 | 19.4733 | 19.204 | 19.1215 | 19.0863 | 18.6193 | 18.5451 | 18.502 | 18.1762 | 18.1454 | 18.1113 | 16.1854 | 16.1827 | 16.1556 | 16.0152 | 15.9686 | 15.9338 | 16.8788 | 16.8624 | 16.8162 | 16.7861 | 16.719 | 16.7132 | 19.8074 | 19.7908 | 19.8266 | 19.8231 | 19.8121 | 19.82 | 19.8146 | 19.8123 | 19.7875 | 19.8428 | 19.8347 | 19.8826 | 19.9294 | 19.9439 | 19.9657 | 20.0031 | 19.9982 | 19.9548 | 19.9075 | 19.7527 | 19.7094 | 19.7109 | 19.3662 | 19.3065 | 19.1384 | 18.3278 | 18.1551 | 17.8645 | 17.2403 | 17.1464 | 17.0547 | 16.688 | 16.5026 | 16.3961 | 19.548 | 19.4774 | 19.3849 | 19.1152 | 19.0285 | 19.0063 | 18.2818 | 18.3 | 18.2472 | 18.1184 | 18.0892 | 18.0361 | 17.9758 | 17.9264 | 17.8939 | 17.3273 | 17.3199 | 17.2655 | 16.8168 | 16.7405 | 16.5886 | 19.3445 | 19.3337 | 19.3353 | 19.3593 | 19.3535 | 19.3783 | 19.4165 | 19.4233 | 19.4224 | 19.5129 | 19.5116 | 19.5024 | 19.4119 | 19.3997 | 19.4176 | 19.3965 | 19.2768 | 19.2536 | 19.2455 | 19.1201 | 19.1091 | 19.0841 | 19.0339 | 18.8962 | 17.8546 | 17.7969 | 17.7177 | 17.1293 | 17.0588 | 16.9646 | 16.7477 | 16.5877 | 16.519 | 19.4298 | 19.3557 | 19.3329 | 18.4754 | 18.4856 | 18.4406 | 18.2724 | 18.2217 | 18.2061 | 17.4242 | 17.3995 | 17.376 | 16.5334 | 16.5028 | 16.4883 | 16.3958 | 16.367 | 18.8189 | 18.7613 | 18.7005 | 17.9405 | 17.9163 | 17.9122 | 17.7416 | 17.6518 | 17.6321 | 17.5962 | 17.1716 | 17.1395 | 17.1223 | 16.4162 | 16.3613 | 16.3399 | 16.3208 | 21.7071 | 21.6477 | 21.6439 | 21.6178 | 21.2944 | 21.238 | 21.2058 | 20.8601 | 20.7562 | 20.5337 | 21.2526 | 21.2336 | 21.1573 | 21.1121 | 21.0328 | 20.9965 | 20.91 | 20.8537 | 19.2982 | 19.2382 | 19.1841 | 18.6755 | 18.6427 | 18.5464 | 18.4656 | 18.4145 | 18.3534 | 17.9906 | 17.8531 | 17.7346 | 16.3038 | 16.2771 | 16.256 | 18.9888 | 18.927 | 18.8385 | 18.47 | 18.3757 | 18.3022 | 17.6191 | 17.5737 | 17.4959 | 17.3445 | 17.2379 | 17.1583 | 15.1456 | 15.1224 | 15.0586 | 16.6793 | 16.6592 | 16.5676 | 16.2276 | 16.1804 | 16.1308 | 17.6817 | 17.667 | 17.6517 | 17.666 | 17.6471 | 17.6128 | 17.8378 | 17.8023 | 17.7745 | 17.4083 | 17.3497 | 17.2824 | 18.8091 | 18.6361 | 18.5005 | 18.2075 | 18.1209 | 18.0216 | 17.7946 | 17.6877 | 17.5445 | 18.3109 | 18.2849 | 18.2005 | 16.8673 | 16.8071 | 16.7826 | 18.641 | 18.577 | 18.5099 | 18.2821 | 18.1983 | 18.0989
160 | LI flow meter pressure - Not working correctly. | BarA | 1.6851 | 1.6815 | 1.6804 | 1.6757 | 1.6738 | 1.6702 | 1.667 | 1.6603 | 1.6584 | 1.6533 | 1.654 | 1.6488 | 1.6381 | 1.6391 | 1.6393 | 1.6086 | 1.6071 | 1.6124 | 1.6034 | 1.605 | 1.6011 | 1.6267 | 1.6264 | 1.6272 | 1.6211 | 1.6273 | 1.6232 | 1.6839 | 1.6818 | 1.6867 | 1.6866 | 1.6866 | 1.6882 | 1.6907 | 1.6834 | 1.6872 | 1.6833 | 1.6879 | 1.6885 | 1.6872 | 1.6835 | 1.6892 | 1.6843 | 1.6887 | 1.6893 | 1.6846 | 1.6827 | 1.6833 | 1.6843 | 1.6692 | 1.6679 | 1.6692 | 1.6509 | 1.6477 | 1.6354 | 1.625 | 1.6255 | 1.6233 | 1.6168 | 1.6158 | 1.6108 | 1.6789 | 1.6802 | 1.6729 | 1.6678 | 1.6664 | 1.6649 | 1.6581 | 1.6544 | 1.6579 | 1.6592 | 1.6562 | 1.6536 | 1.6579 | 1.6561 | 1.6506 | 1.6425 | 1.6402 | 1.6418 | 1.6357 | 1.6347 | 1.6307 | 1.694 | 1.6889 | 1.6899 | 1.6927 | 1.696 | 1.6922 | 1.6973 | 1.6954 | 1.6946 | 1.6921 | 1.6983 | 1.6977 | 1.6997 | 1.6912 | 1.6948 | 1.6922 | 1.6877 | 1.6931 | 1.6869 | 1.6794 | 1.6812 | 1.6848 | 1.681 | 1.6769 | 1.6521 | 1.6499 | 1.6468 | 1.6389 | 1.6326 | 1.6371 | 1.6325 | 1.6278 | 1.6233 | 1.7331 | 1.7269 | 1.7301 | 1.7234 | 1.7215 | 1.7137 | 1.7126 | 1.7116 | 1.7137 | 1.6964 | 1.6938 | 1.6963 | 1.6834 | 1.6805 | 1.6803 | 1.6859 | 1.6796 | 1.7336 | 1.726 | 1.7303 | 1.7136 | 1.717 | 1.7248 | 1.7116 | 1.7125 | 1.7111 | 1.7122 | 1.703 | 1.696 | 1.7028 | 1.6913 | 1.6924 | 1.6905 | 1.6904 | 1.7809 | 1.7825 | 1.7794 | 1.7771 | 1.7711 | 1.7741 | 1.7715 | 1.7635 | 1.7618 | 1.759 | 1.788 | 1.7862 | 1.7842 | 1.7834 | 1.7846 | 1.7837 | 1.7808 | 1.7773 | 1.7478 | 1.7488 | 1.7472 | 1.7381 | 1.7338 | 1.7334 | 1.7305 | 1.7293 | 1.7304 | 1.7225 | 1.72 | 1.7174 | 1.6974 | 1.6932 | 1.6948 | 1.7633 | 1.7619 | 1.7621 | 1.7501 | 1.7498 | 1.7505 | 1.7325 | 1.7341 | 1.7328 | 1.7266 | 1.7283 | 1.7201 | 1.6859 | 1.6854 | 1.6849 | 1.7314 | 1.7322 | 1.728 | 1.7227 | 1.7185 | 1.719 | 1.7588 | 1.7576 | 1.7603 | 1.7633 | 1.7629 | 1.7586 | 1.7626 | 1.7589 | 1.756 | 1.7516 | 1.7471 | 1.746 | 1.7735 | 1.7669 | 1.7649 | 1.7583 | 1.7565 | 1.7568 | 1.7478 | 1.745 | 1.7452 | 1.7611 | 1.7591 | 1.7617 | 1.7302 | 1.7359 | 1.7374 | 1.8106 | 1.8055 | 1.8029 | 1.8007 | 1.7953 | 1.8005
161 | LI flow meter gauge | ºC | -14.3325 | -14.3843 | -14.4006 | -14.4676 | -14.4957 | -14.5481 | -14.5947 | -14.6932 | -14.7212 | -14.7957 | -14.7855 | -14.8613 | -15.0193 | -15.004 | -15.001 | -15.4582 | -15.4809 | -15.4014 | -15.5366 | -15.5122 | -15.5711 | -15.1883 | -15.1925 | -15.1812 | -15.2717 | -15.1798 | -15.2408 | -14.3486 | -14.3804 | -14.3089 | -14.3098 | -14.3097 | -14.287 | -14.2514 | -14.3566 | -14.3008 | -14.3573 | -14.2915 | -14.2824 | -14.3016 | -14.3544 | -14.2732 | -14.3431 | -14.28 | -14.2709 | -14.3395 | -14.3667 | -14.3573 | -14.3428 | -14.5622 | -14.582 | -14.5629 | -14.83 | -14.8773 | -15.0598 | -15.2139 | -15.2055 | -15.2382 | -15.3356 | -15.3505 | -15.4256 | -14.4216 | -14.4034 | -14.509 | -14.5826 | -14.6038 | -14.6257 | -14.7242 | -14.7784 | -14.7278 | -14.7084 | -14.7525 | -14.7904 | -14.7277 | -14.7546 | -14.8346 | -14.9542 | -14.9884 | -14.9647 | -15.0554 | -15.0693 | -15.1292 | -14.2037 | -14.2771 | -14.2628 | -14.2217 | -14.1742 | -14.2298 | -14.1563 | -14.183 | -14.1944 | -14.2302 | -14.142 | -14.1507 | -14.122 | -14.2436 | -14.1921 | -14.2292 | -14.294 | -14.217 | -14.3062 | -14.4148 | -14.389 | -14.3365 | -14.3911 | -14.451 | -14.8127 | -14.8452 | -14.8905 | -15.008 | -15.1001 | -15.0338 | -15.1026 | -15.1715 | -15.2392 | -13.6446 | -13.7332 | -13.6884 | -13.7833 | -13.8101 | -13.9207 | -13.9363 | -13.951 | -13.9209 | -14.1684 | -14.2061 | -14.1697 | -14.357 | -14.3989 | -14.402 | -14.3207 | -14.412 | -13.6383 | -13.7455 | -13.6854 | -13.9228 | -13.8734 | -13.7635 | -13.9512 | -13.9382 | -13.9579 | -13.9426 | -14.0734 | -14.1742 | -14.0767 | -14.2424 | -14.2266 | -14.2535 | -14.2547 | -12.9759 | -12.9533 | -12.9963 | -13.0282 | -13.1123 | -13.07 | -13.107 | -13.2175 | -13.2412 | -13.2804 | -12.8781 | -12.9031 | -12.9298 | -12.9409 | -12.9254 | -12.9367 | -12.977 | -13.0253 | -13.4378 | -13.4232 | -13.4465 | -13.5749 | -13.6352 | -13.6409 | -13.6813 | -13.699 | -13.6828 | -13.7949 | -13.8316 | -13.8675 | -14.1548 | -14.215 | -14.1921 | -13.221 | -13.2405 | -13.237 | -13.405 | -13.4099 | -13.4001 | -13.6533 | -13.6305 | -13.6498 | -13.7374 | -13.7128 | -13.8298 | -14.3206 | -14.3275 | -14.3349 | -13.6688 | -13.6574 | -13.717 | -13.7921 | -13.8518 | -13.8458 | -13.2832 | -13.3 | -13.2621 | -13.2202 | -13.2264 | -13.2869 | -13.2309 | -13.2819 | -13.323 | -13.3849 | -13.4478 | -13.4627 | -13.0783 | -13.17 | -13.1982 | -13.2899 | -13.3164 | -13.3122 | -13.4374 | -13.4776 | -13.4739 | -13.2519 | -13.2788 | -13.2436 | -13.6869 | -13.6053 | -13.5837 | -12.5676 | -12.6369 | -12.6727 | -12.7034 | -12.7765 | -12.7049
162 | LI flow meter enthalpy | KJ/kg | 418.9628 | 418.9352 | 418.9026 | 418.6439 | 418.6321 | 418.543 | 418.3187 | 418.2616 | 418.2353 | 417.8459 | 417.7809 | 417.7545 | 417.4978 | 417.4693 | 417.4398 | 415.8598 | 415.8607 | 415.8265 | 415.7257 | 415.6827 | 415.6612 | 416.4133 | 416.3999 | 416.359 | 416.3459 | 416.2759 | 416.2794 | 418.8019 | 418.792 | 418.8128 | 418.8099 | 418.8005 | 418.8041 | 418.7945 | 418.8072 | 418.7781 | 418.8335 | 418.8173 | 418.8572 | 418.9 | 418.9198 | 418.9272 | 418.969 | 418.9561 | 418.9176 | 418.8865 | 418.7575 | 418.719 | 418.7182 | 418.4531 | 418.4048 | 418.2581 | 417.6012 | 417.4601 | 417.237 | 416.7253 | 416.6441 | 416.5703 | 416.2711 | 416.1151 | 416.0348 | 418.5895 | 418.5265 | 418.4618 | 418.241 | 418.1696 | 418.1536 | 417.5472 | 417.5703 | 417.5181 | 417.4053 | 417.3864 | 417.3463 | 417.286 | 417.2475 | 417.2308 | 416.7635 | 416.762 | 416.7122 | 416.3419 | 416.2788 | 416.1576 | 418.3847 | 418.3857 | 418.385 | 418.3998 | 418.3883 | 418.4173 | 418.4398 | 418.4493 | 418.4501 | 418.5328 | 418.5193 | 418.5126 | 418.431 | 418.4376 | 418.4457 | 418.4328 | 418.3392 | 418.3086 | 418.3141 | 418.2218 | 418.2088 | 418.18 | 418.1447 | 418.0351 | 417.1942 | 417.1495 | 417.0881 | 416.602 | 416.5547 | 416.465 | 416.2896 | 416.1628 | 416.1136 | 418.3788 | 418.3278 | 418.3019 | 417.58 | 417.5926 | 417.5699 | 417.4279 | 417.3867 | 417.369 | 416.7352 | 416.7195 | 416.6942 | 416.001 | 415.9809 | 415.9689 | 415.8783 | 415.8668 | 417.8537 | 417.8197 | 417.7589 | 417.1418 | 417.114 | 417.0946 | 416.9756 | 416.8968 | 416.8829 | 416.8499 | 416.5055 | 416.4926 | 416.4638 | 415.8844 | 415.8352 | 415.8209 | 415.8047 | 420.2427 | 420.1883 | 420.1911 | 420.1731 | 419.9065 | 419.8518 | 419.8294 | 419.5474 | 419.4613 | 419.2755 | 419.8369 | 419.8242 | 419.7622 | 419.7249 | 419.6543 | 419.6246 | 419.556 | 419.5144 | 418.2362 | 418.1826 | 418.1395 | 417.7216 | 417.7021 | 417.6204 | 417.5569 | 417.5157 | 417.4609 | 417.1663 | 417.0538 | 416.9576 | 415.7758 | 415.7616 | 415.7404 | 417.9392 | 417.8889 | 417.8124 | 417.5207 | 417.4405 | 417.3761 | 416.8276 | 416.7854 | 416.7216 | 416.6048 | 416.5099 | 416.4589 | 414.8117 | 414.7929 | 414.7396 | 416.0256 | 416.0067 | 415.9371 | 415.6576 | 415.626 | 415.5828 | 416.8269 | 416.8169 | 416.7982 | 416.8043 | 416.789 | 416.7685 | 416.9531 | 416.9301 | 416.9123 | 416.6077 | 416.5668 | 416.5113 | 417.764 | 417.6289 | 417.5166 | 417.2788 | 417.2084 | 417.1226 | 416.9464 | 416.8607 | 416.7375 | 417.3619 | 417.3435 | 417.266 | 416.189 | 416.1256 | 416.1014 | 417.544 | 417.4993 | 417.447 | 417.256 | 417.1949 | 417.0989
163 | LI flow meter specific Vol | m3/kg | 0.13654 | 0.13682 | 0.1369 | 0.13712 | 0.13728 | 0.13752 | 0.13765 | 0.13819 | 0.13833 | 0.13852 | 0.13842 | 0.13885 | 0.13961 | 0.1395 | 0.13947 | 0.14116 | 0.14129 | 0.1408 | 0.14154 | 0.14137 | 0.1417 | 0.13991 | 0.13993 | 0.13983 | 0.14036 | 0.13977 | 0.14014 | 0.13653 | 0.13671 | 0.13631 | 0.13632 | 0.13631 | 0.13618 | 0.13597 | 0.13658 | 0.13625 | 0.1366 | 0.13622 | 0.13619 | 0.13633 | 0.13664 | 0.13618 | 0.13661 | 0.13624 | 0.13616 | 0.13653 | 0.13661 | 0.13653 | 0.13645 | 0.13755 | 0.13763 | 0.13743 | 0.13857 | 0.13875 | 0.13968 | 0.14027 | 0.14016 | 0.14031 | 0.14069 | 0.14068 | 0.14108 | 0.13682 | 0.13668 | 0.13724 | 0.13753 | 0.13761 | 0.13773 | 0.13791 | 0.13825 | 0.13792 | 0.13773 | 0.13798 | 0.13817 | 0.13777 | 0.1379 | 0.13836 | 0.13876 | 0.13896 | 0.13879 | 0.13908 | 0.13912 | 0.1394 | 0.13545 | 0.13587 | 0.13578 | 0.13556 | 0.13528 | 0.13562 | 0.13521 | 0.13537 | 0.13544 | 0.13569 | 0.13518 | 0.13523 | 0.13501 | 0.13571 | 0.13542 | 0.13562 | 0.13593 | 0.13548 | 0.13599 | 0.13655 | 0.1364 | 0.13608 | 0.13637 | 0.13664 | 0.13821 | 0.13837 | 0.13859 | 0.13897 | 0.13948 | 0.13903 | 0.13932 | 0.13965 | 0.14002 | 0.13231 | 0.13277 | 0.1325 | 0.13259 | 0.13275 | 0.13335 | 0.13335 | 0.1334 | 0.13323 | 0.13422 | 0.13442 | 0.1342 | 0.13483 | 0.13505 | 0.13506 | 0.13455 | 0.13506 | 0.13195 | 0.13253 | 0.13216 | 0.1331 | 0.1328 | 0.13218 | 0.13315 | 0.13303 | 0.13313 | 0.13303 | 0.13354 | 0.1341 | 0.13354 | 0.13411 | 0.13399 | 0.13413 | 0.13413 | 0.12977 | 0.12962 | 0.12985 | 0.13001 | 0.13031 | 0.13005 | 0.13023 | 0.13067 | 0.13075 | 0.13085 | 0.12901 | 0.12913 | 0.12924 | 0.12928 | 0.12915 | 0.1292 | 0.12937 | 0.12961 | 0.13108 | 0.13097 | 0.13107 | 0.13152 | 0.13184 | 0.13183 | 0.13201 | 0.13208 | 0.13196 | 0.1324 | 0.13254 | 0.13268 | 0.13355 | 0.13388 | 0.13373 | 0.12973 | 0.1298 | 0.12974 | 0.13047 | 0.13045 | 0.13036 | 0.13141 | 0.13126 | 0.13133 | 0.13174 | 0.13154 | 0.13216 | 0.13387 | 0.1339 | 0.13391 | 0.13101 | 0.13093 | 0.13122 | 0.13146 | 0.13177 | 0.13171 | 0.1294 | 0.12948 | 0.12926 | 0.12904 | 0.12907 | 0.12938 | 0.12919 | 0.12945 | 0.12966 | 0.12981 | 0.13013 | 0.13018 | 0.12885 | 0.12927 | 0.12935 | 0.1297 | 0.1298 | 0.12973 | 0.1303 | 0.13047 | 0.13038 | 0.12955 | 0.12968 | 0.12945 | 0.13121 | 0.13072 | 0.13059 | 0.12602 | 0.12636 | 0.12651 | 0.12656 | 0.12691 | 0.12648
164 | LI flow meter vol Flow | m^3/hr | 0.5215 | 0.52143 | 0.5229 | 0.52276 | 0.52041 | 0.52379 | 0.52125 | 0.51932 | 0.52194 | 0.52248 | 0.52357 | 0.52149 | 0.52087 | 0.52206 | 0.52314 | 0.52195 | 0.52278 | 0.52194 | 0.5234 | 0.52155 | 0.52218 | 0.5196 | 0.52034 | 0.52441 | 0.52248 | 0.52221 | 0.5244 | 0.52262 | 0.5214 | 0.52117 | 0.52186 | 0.52201 | 0.52363 | 0.52001 | 0.52309 | 0.5217 | 0.52114 | 0.52081 | 0.5241 | 0.51992 | 0.5227 | 0.52199 | 0.51909 | 0.52184 | 0.51934 | 0.5219 | 0.52291 | 0.52028 | 0.52302 | 0.52138 | 0.52345 | 0.51933 | 0.52037 | 0.52298 | 0.5212 | 0.52047 | 0.52194 | 0.52207 | 0.52077 | 0.5228 | 0.52026 | 0.52097 | 0.52228 | 0.51856 | 0.52383 | 0.51913 | 0.5219 | 0.52213 | 0.51969 | 0.52445 | 0.52287 | 0.52214 | 0.51881 | 0.52234 | 0.5214 | 0.52309 | 0.51901 | 0.52345 | 0.52259 | 0.52245 | 0.52425 | 2.1308 | 0.52363 | 0.52213 | 0.52231 | 0.51894 | 0.52252 | 0.52322 | 0.52084 | 0.52169 | 0.52331 | 0.52161 | 0.51954 | 0.52028 | 0.52225 | 0.51986 | 0.52168 | 0.52169 | 0.52185 | 0.51922 | 0.51902 | 0.52214 | 0.52263 | 0.52283 | 0.5233 | 0.52062 | 0.52139 | 0.52232 | 0.52261 | 0.52145 | 0.52158 | 0.52163 | 0.52302 | 0.52431 | 0.52138 | 0.52242 | 0.52038 | 0.5213 | 0.5199 | 0.52089 | 0.52049 | 0.52335 | 0.52231 | 0.52328 | 0.52227 | 0.5238 | 0.52209 | 0.52245 | 0.52199 | 0.52256 | 0.52208 | 0.51901 | 0.51943 | 0.52385 | 0.52362 | 0.52067 | 0.52138 | 0.52129 | 0.52197 | 0.52215 | 0.51988 | 0.52255 | 0.52247 | 0.52298 | 0.52265 | 0.5209 | 0.52151 | 0.52401 | 0.51914 | 0.5229 | 0.52214 | 0.5195 | 0.5228 | 0.5209 | 0.52272 | 0.5207 | 0.5215 | 0.52287 | 0.52322 | 0.52429 | 0.52376 | 0.52382 | 0.52088 | 0.52394 | 0.52282 | 0.52108 | 0.52184 | 0.52135 | 0.52159 | 0.51999 | 0.5222 | 0.52415 | 0.52191 | 0.52189 | 0.52089 | 0.5219 | 0.5234 | 0.52135 | 0.52375 | 0.5242 | 0.52244 | 0.52114 | 0.52244 | 0.51929 | 0.52193 | 0.52172 | 0.5215 | 0.52307 | 0.51997 | 0.52144 | 0.52251 | 0.52156 | 0.52188 | 0.52084 | 0.52181 | 0.52297 | 0.52365 | 0.52049 | 0.5225 | 0.52299 | 0.52258 | 0.52229 | 0.52073 | 0.52067 | 0.51994 | 0.52312 | 0.52106 | 0.52084 | 0.52164 | 0.5203 | 0.52059 | 0.52417 | 0.52014 | 0.52067 | 0.52106 | 0.52118 | 0.52294 | 0.52445 | 0.52109 | 0.52138 | 0.52066 | 0.52039 | 0.52342 | 0.52174 | 0.52093 | 0.52204 | 0.52173 | 0.52371 | 0.52104 | 0.52378 | 0.52293 | 0.5208 | 0.52315 | 0.52233 | 0.52189 | 0.52176
165 | LI flow meter mass Flow | kg/s | 0.0010609 | 0.0010586 | 0.001061 | 0.001059 | 0.0010531 | 0.001058 | 0.0010519 | 0.0010439 | 0.0010481 | 0.0010477 | 0.0010507 | 0.0010433 | 0.0010363 | 0.0010395 | 0.001042 | 0.0010271 | 0.0010278 | 0.0010297 | 0.0010272 | 0.0010248 | 0.0010236 | 0.0010316 | 0.001033 | 0.0010417 | 0.001034 | 0.0010378 | 0.0010395 | 0.0010633 | 0.0010594 | 0.001062 | 0.0010634 | 0.0010638 | 0.0010681 | 0.0010623 | 0.0010638 | 0.0010636 | 0.0010597 | 0.0010621 | 0.001069 | 0.0010594 | 0.0010626 | 0.0010647 | 0.0010555 | 0.001064 | 0.0010595 | 0.0010618 | 0.0010633 | 0.0010585 | 0.0010648 | 0.0010529 | 0.0010565 | 0.0010497 | 0.0010432 | 0.001047 | 0.0010365 | 0.0010307 | 0.0010344 | 0.0010336 | 0.0010282 | 0.0010323 | 0.0010244 | 0.0010577 | 0.0010615 | 0.0010495 | 0.001058 | 0.0010479 | 0.0010526 | 0.0010516 | 0.0010442 | 0.0010563 | 0.0010545 | 0.0010512 | 0.001043 | 0.0010532 | 0.0010503 | 0.0010502 | 0.001039 | 0.0010464 | 0.001046 | 0.0010435 | 0.0010467 | 0.0042462 | 0.0010739 | 0.0010675 | 0.0010685 | 0.0010634 | 0.0010729 | 0.0010717 | 0.00107 | 0.0010705 | 0.0010733 | 0.0010678 | 0.0010676 | 0.0010688 | 0.0010745 | 0.0010641 | 0.0010701 | 0.0010685 | 0.0010664 | 0.0010646 | 0.0010602 | 0.0010622 | 0.0010644 | 0.0010673 | 0.0010659 | 0.0010584 | 0.0010479 | 0.0010486 | 0.0010474 | 0.0010423 | 0.0010387 | 0.0010422 | 0.0010428 | 0.0010429 | 0.0010343 | 0.0010968 | 0.0010887 | 0.0010928 | 0.0010892 | 0.00109 | 0.0010842 | 0.0010902 | 0.0010876 | 0.001091 | 0.0010809 | 0.0010824 | 0.0010806 | 0.0010764 | 0.0010736 | 0.0010747 | 0.0010779 | 0.0010675 | 0.0010934 | 0.001098 | 0.0011006 | 0.0010867 | 0.0010905 | 0.0010955 | 0.0010889 | 0.0010903 | 0.0010847 | 0.0010912 | 0.0010868 | 0.0010833 | 0.0010872 | 0.0010789 | 0.0010812 | 0.0010852 | 0.0010751 | 0.0011193 | 0.001119 | 0.0011113 | 0.001117 | 0.0011104 | 0.0011165 | 0.0011106 | 0.0011086 | 0.0011109 | 0.0011107 | 0.0011289 | 0.0011267 | 0.0011259 | 0.0011192 | 0.0011269 | 0.0011241 | 0.0011188 | 0.0011184 | 0.0011048 | 0.0011062 | 0.001102 | 0.0011029 | 0.0011043 | 0.0010997 | 0.0010982 | 0.0010955 | 0.0010986 | 0.0010981 | 0.0010927 | 0.0010966 | 0.0010903 | 0.001084 | 0.0010825 | 0.0011187 | 0.0011113 | 0.0011175 | 0.0011107 | 0.0011105 | 0.0011146 | 0.0010991 | 0.0011035 | 0.0011052 | 0.0010997 | 0.001102 | 0.0010947 | 0.0010827 | 0.0010849 | 0.0010862 | 0.0011036 | 0.0011085 | 0.0011071 | 0.0011042 | 0.001101 | 0.0010982 | 0.0011177 | 0.0011154 | 0.0011241 | 0.0011216 | 0.001121 | 0.00112 | 0.0011187 | 0.0011171 | 0.001123 | 0.001113 | 0.0011114 | 0.0011119 | 0.0011235 | 0.0011237 | 0.0011262 | 0.001116 | 0.0011157 | 0.0011148 | 0.0011094 | 0.0011144 | 0.0011116 | 0.001117 | 0.0011182 | 0.0011196 | 0.0011088 | 0.0011072 | 0.0011142 | 0.0011527 | 0.0011449 | 0.0011486 | 0.0011464 | 0.0011423 | 0.0011459
166 | LI on/off | - | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI | no LI
167
168
169 | Electrical Data
170 | Power input |  | 292.3456 | 291.0933 | 291.2538 | 274.3867 | 275.0303 | 272.963 | 261.06 | 260.4595 | 261.7583 | 253.0442 | 250.3067 | 250.7951 | 243.1942 | 242.2472 | 240.992 | 19.6327 | 19.0735 | 19.5051 | 20.5655 | 20.4138 | 20.5025 | 19.815 | 19.0676 | 19.5561 | 19.969 | 20.2063 | 20.7082 | 52.0438 | 52.4021 | 51.8934 | 54.6473 | 54.988 | 54.5901 | 58.7237 | 58.8791 | 59.0996 | 56.3391 | 56.2233 | 57.0856 | 59.3721 | 59.2069 | 59.4785 | 115.547 | 115.4643 | 116.2837 | 116.8157 | 126.4314 | 126.0191 | 125.7056 | 228.5681 | 230.489 | 229.3761 | 253.8824 | 254.116 | 255.0061 | 254.3421 | 254.149 | 253.995 | 251.2872 | 251.4931 | 253.7185 | 119.4992 | 118.79 | 119.4309 | 127.5683 | 128.006 | 127.5888 | 59.1581 | 59.7945 | 59.2685 | 54.1841 | 53.9606 | 54.4708 | 54.5679 | 54.1843 | 54.205 | 19.3043 | 19.9726 | 19.6288 | 20.6619 | 20.0945 | 21.2378 | 52.6734 | 52.8096 | 52.7737 | 57.2978 | 56.5406 | 57.2907 | 59.5372 | 59.1441 | 59.3426 | 122.3535 | 121.1635 | 121.5595 | 128.6453 | 128.3336 | 128.7511 | 126.3583 | 229.86 | 229.8192 | 229.788 | 229.7588 | 230.2063 | 230.3415 | 228.8473 | 230.1678 | 255.5948 | 256.0513 | 254.6313 | 252.0243 | 254.8569 | 257.0034 | 251.7677 | 252.3911 | 249.7002 | 248.1303 | 253.0356 | 250.7873 | 116.0362 | 116.253 | 116.5996 | 117.7818 | 117.9755 | 117.775 | 52.2129 | 51.8846 | 51.9135 | 19.3076 | 18.9079 | 19.4552 | 20.8503 | 19.9527 | 126.2066 | 126.4329 | 126.5345 | 55.8506 | 56.3042 | 57.0558 | 56.9312 | 59.386 | 59.4363 | 59.0296 | 59.8121 | 60.4708 | 60.3824 | 20.7578 | 20.9116 | 20.5648 | 20.537 | 226.7017 | 227.1654 | 226.3685 | 225.8979 | 250.1444 | 250.5474 | 251.8222 | 247.958 | 248.6345 | 248.3697 | 253.0415 | 251.1063 | 250.9324 | 251.6663 | 249.521 | 250.653 | 248.8685 | 248.8877 | 249.8527 | 250.2379 | 250.1678 | 250.0491 | 252.4685 | 253.5992 | 250.4028 | 249.5629 | 249.7189 | 227.605 | 226.5059 | 227.0164 | 59.1048 | 58.9568 | 58.5944 | 251.6153 | 252.1751 | 250.4415 | 250.3699 | 250.0738 | 249.3838 | 252.2843 | 252.7251 | 250.7308 | 226.7294 | 225.7125 | 226.1696 | 58.7229 | 58.9279 | 58.1343 | 56.0385 | 55.5897 | 56.3449 | 51.8491 | 52.0769 | 51.9873 | 19.7068 | 19.8131 | 19.7217 | 20.5707 | 21.0419 | 20.5815 | 117.4799 | 118.1851 | 117.2627 | 127.4955 | 126.3336 | 126.6961 | 249.9693 | 246.878 | 248.761 | 251.2586 | 249.6893 | 248.3999 | 248.9689 | 247.7815 | 249.3591 | 225.4875 | 225.4563 | 223.8227 | 58.3426 | 59.0402 | 58.3082 | 250.4776 | 253.801 | 249.7197 | 254.0856 | 254.7866 | 252.6337
171 | Amps phase 1 |  | 465.1295 | 464.8799 | 465.8368 | 437.4373 | 437.676 | 436.8455 | 416.5579 | 417.0422 | 415.9942 | 402.7699 | 397.7957 | 400.1176 | 389.0216 | 390.2095 | 387.0678 | 42.586 | 41.959 | 42.5356 | 45.3282 | 44.7879 | 44.038 | 42.6811 | 42.1287 | 42.2137 | 43.8151 | 43.3754 | 43.6574 | 99.2111 | 98.9238 | 98.3653 | 102.3643 | 102.9821 | 102.4508 | 106.7071 | 105.5787 | 105.2498 | 102.7369 | 102.9341 | 103.6481 | 104.978 | 105.5759 | 106.0849 | 192.6172 | 193.5763 | 192.5488 | 195.5211 | 206.7732 | 208.264 | 207.1958 | 369.7401 | 370.321 | 370.494 | 407.8381 | 407.2542 | 409.3835 | 409.7164 | 405.5536 | 406.4679 | 398.9392 | 405.7748 | 409.4698 | 197.2947 | 195.4498 | 197.3222 | 211.1828 | 208.877 | 210.4298 | 107.5964 | 106.9401 | 105.8934 | 100.6003 | 100.9459 | 101.1183 | 100.8844 | 101.1716 | 100.58 | 41.196 | 41.9138 | 40.9422 | 44.0314 | 43.6532 | 44.268 | 100.0473 | 100.38 | 98.9103 | 104.9581 | 104.3297 | 104.139 | 106.6916 | 106.7099 | 105.8669 | 199.0384 | 201.7561 | 201.35 | 208.8348 | 210.6616 | 208.1948 | 208.9447 | 367.1387 | 366.6719 | 369.4891 | 366.4696 | 366.1901 | 369.475 | 367.8917 | 371.4444 | 410.3301 | 409.7719 | 405.7678 | 403.7374 | 406.6094 | 411.0409 | 401.9374 | 404.1312 | 401.8522 | 402.7253 | 404.2369 | 399.5616 | 193.9173 | 195.5197 | 193.944 | 194.6697 | 197.6336 | 194.3211 | 98.5969 | 98.2443 | 97.7495 | 42.4155 | 41.7892 | 42.6723 | 44.2199 | 43.9915 | 208.5746 | 204.8336 | 208.2424 | 104.0913 | 105.5597 | 105.3829 | 104.5507 | 107.3508 | 107.072 | 106.3972 | 106.4333 | 108.8735 | 107.9682 | 44.8417 | 44.1796 | 43.6032 | 44.4289 | 359.6462 | 360.3393 | 359.8021 | 360.1237 | 399.3037 | 401.4624 | 403.23 | 397.5884 | 398.5031 | 398.1938 | 403.9355 | 401.7544 | 400.4796 | 401.166 | 395.7559 | 398.2029 | 397.6313 | 393.9594 | 399.9829 | 400.6167 | 402.3714 | 403.8621 | 407.6304 | 410.6779 | 402.6581 | 403.8256 | 405.5116 | 364.8774 | 367.6853 | 365.4373 | 104.3809 | 104.141 | 102.6989 | 405.2731 | 405.2249 | 406.6244 | 398.846 | 400.5182 | 398.1597 | 403.2951 | 406.8945 | 403.5141 | 363.4616 | 361.5596 | 364.7188 | 106.2106 | 105.6429 | 103.9087 | 105.7443 | 105.7645 | 106.3692 | 100.2501 | 100.0857 | 99.2755 | 41.9809 | 42.1843 | 41.7606 | 44.2636 | 44.2237 | 43.6761 | 196.7158 | 198.2908 | 197.806 | 208.0993 | 208.3936 | 209.2083 | 401.1018 | 395.487 | 399.3512 | 402.4721 | 400.7401 | 398.0508 | 402.9233 | 399.3172 | 403.7615 | 359.0219 | 355.6795 | 354.856 | 106.6884 | 106.7749 | 106.9056 | 401.6338 | 405.6702 | 401.1818 | 405.4443 | 407.9586 | 403.714
172 | Amps phase 2 |  | 470.4061 | 469.462 | 468.8062 | 444.6569 | 446.6448 | 442.2544 | 422.0802 | 421.7105 | 422.262 | 410.938 | 405.8891 | 407.5797 | 397.4424 | 392.2914 | 390.2926 | 41.5347 | 40.3505 | 41.0147 | 43.0164 | 42.9556 | 42.6223 | 41.637 | 40.8221 | 42.4374 | 42.3453 | 42.6942 | 43.5303 | 96.2361 | 96.872 | 96.0853 | 100.4163 | 100.415 | 100.3219 | 107.169 | 105.9392 | 107.2016 | 103.9149 | 103.5846 | 105.1416 | 107.094 | 108.0093 | 107.6386 | 193.831 | 193.2374 | 196.0472 | 196.3883 | 212.3971 | 214.8407 | 210.6771 | 373.8894 | 377.7656 | 374.6856 | 411.6951 | 413.7926 | 416.4415 | 414.2729 | 415.6543 | 413.9488 | 400.2747 | 409.3585 | 412.4362 | 198.6702 | 199.0956 | 198.8477 | 213.0151 | 212.7122 | 212.6876 | 106.8506 | 108.5871 | 108.1186 | 100.6098 | 100.3306 | 101.1104 | 100.4599 | 101.196 | 100.4843 | 40.4575 | 41.5605 | 41.8341 | 43.2225 | 42.1086 | 44.0294 | 96.7844 | 97.7352 | 97.8312 | 103.5112 | 103.1312 | 104.5794 | 106.6256 | 107.0409 | 106.6489 | 203.3994 | 200.8406 | 203.0793 | 218.5591 | 212.8844 | 218.5082 | 213.8986 | 376.0741 | 374.7724 | 374.1692 | 374.5448 | 375.9294 | 378.0917 | 373.1916 | 373.0183 | 417.7165 | 418.0971 | 415.3696 | 408.9479 | 414.5864 | 415.5608 | 407.6325 | 408.5392 | 404.5109 | 402.5404 | 407.6571 | 398.3239 | 193.5027 | 194.1531 | 193.5975 | 195.0374 | 194.955 | 196.6561 | 95.6895 | 94.2544 | 95.2375 | 40.6576 | 40.0611 | 40.6095 | 42.6161 | 42.5085 | 212.0752 | 214.1322 | 211.9313 | 102.4169 | 103.498 | 104.5391 | 103.5562 | 106.6613 | 106.6509 | 106.4423 | 108.6787 | 109.6532 | 109.6073 | 42.2657 | 42.6891 | 42.9878 | 42.0057 | 360.675 | 362.6841 | 361.0677 | 361.5934 | 401.3242 | 401.2519 | 404.2058 | 400.6199 | 403.5039 | 406.406 | 405.4187 | 402.1727 | 400.6845 | 405.5304 | 399.7079 | 400.6594 | 397.746 | 397.3638 | 409.7689 | 408.4648 | 408.2861 | 408.4448 | 412.7133 | 411.8164 | 408.4937 | 407.3052 | 406.1302 | 373.5324 | 373.2789 | 373.7141 | 109.3896 | 110.8564 | 110.6567 | 408.3448 | 407.8336 | 408.4459 | 403.2173 | 404.5591 | 402.7563 | 409.642 | 410.0972 | 405.764 | 368.2458 | 366.5143 | 367.0172 | 107.0224 | 107.3984 | 107.3946 | 104.5636 | 103.2648 | 103.713 | 97.6098 | 97.4012 | 97.9645 | 41.9747 | 41.1678 | 41.5665 | 43.634 | 44.1199 | 43.9461 | 196.3658 | 201.0224 | 198.5457 | 216.4825 | 214.8778 | 212.9872 | 408.5803 | 401.9716 | 405.7374 | 409.0298 | 404.5637 | 407.0818 | 408.4728 | 406.1868 | 407.5453 | 362.8136 | 364.6181 | 360.7411 | 109.0842 | 108.8817 | 107.3377 | 408.0427 | 413.5165 | 406.282 | 414.4395 | 413.8753 | 411.3238
173 | Amps phase 3 |  | 479.598 | 476.627 | 480.4009 | 451.6568 | 452.8101 | 448.6098 | 428.2346 | 426.3165 | 430.6196 | 416.5557 | 414.7835 | 414.9971 | 400.4448 | 399.7036 | 399.485 | 46.9588 | 44.8174 | 46.3839 | 47.7854 | 47.6115 | 47.7711 | 45.8222 | 44.7294 | 46.1016 | 47.5227 | 48.0086 | 47.6129 | 101.5233 | 102.0923 | 101.6451 | 105.7403 | 107.4222 | 106.453 | 113.5903 | 115.5237 | 115.5291 | 109.0844 | 109.8393 | 111.8412 | 115.0265 | 115.4759 | 115.5088 | 192.9976 | 193.2785 | 193.145 | 193.1752 | 210.3529 | 203.8685 | 207.9169 | 377.7567 | 380.9294 | 380.1367 | 417.1368 | 420.1509 | 418.0718 | 418.5641 | 420.6229 | 419.9131 | 406.0162 | 416.5298 | 417.374 | 198.6858 | 196.5078 | 198.3565 | 208.2475 | 207.9318 | 205.3157 | 114.8394 | 115.4956 | 115.3265 | 105.4149 | 105.8118 | 105.7619 | 106.5637 | 105.523 | 106.4277 | 43.0202 | 43.9333 | 43.7925 | 46.3432 | 45.8141 | 46.4298 | 103.444 | 103.2821 | 103.8839 | 112.8296 | 109.581 | 111.4662 | 115.7532 | 115.2437 | 115.8268 | 202.926 | 197.9886 | 197.1766 | 210.2579 | 211.3018 | 210.9482 | 207.2708 | 382.1381 | 382.3322 | 382.2426 | 380.3893 | 381.0325 | 379.596 | 377.4726 | 382.7531 | 419.7683 | 419.9897 | 419.3864 | 415.2794 | 419.1771 | 421.2502 | 412.9662 | 415.6606 | 411.067 | 409.0878 | 413.2569 | 409.0923 | 194.5562 | 194.0718 | 192.1757 | 193.1728 | 194.2406 | 193.6759 | 101.5948 | 101.4753 | 101.95 | 45.1977 | 44.2658 | 44.9619 | 47.2288 | 45.6918 | 206.4048 | 208.3821 | 207.6377 | 109.7312 | 108.5938 | 111.418 | 111.6057 | 117.0289 | 117.0718 | 117.5792 | 118.2015 | 117.4265 | 118.7652 | 46.6779 | 46.9874 | 46.6503 | 45.8407 | 370.4674 | 371.1904 | 369.545 | 367.5979 | 409.0742 | 411.7742 | 413.4091 | 410.0592 | 409.8034 | 408.9916 | 412.9295 | 410.6845 | 411.023 | 411.1498 | 410.317 | 412.18 | 409.9423 | 411.1288 | 411.7937 | 409.6749 | 413.5101 | 412.5161 | 417.0324 | 417.5754 | 414.3751 | 408.7112 | 410.6759 | 376.8148 | 375.249 | 375.9045 | 114.9691 | 113.116 | 112.1962 | 411.8212 | 412.9598 | 410.2328 | 407.0776 | 405.5102 | 408.1494 | 414.9767 | 414.1667 | 412.1024 | 373.7148 | 373.1971 | 371.5716 | 112.1357 | 113.7607 | 112.0673 | 109.5875 | 108.6506 | 109.4506 | 102.3868 | 102.0043 | 102.3327 | 45.3689 | 44.4895 | 44.5868 | 46.2517 | 46.259 | 46.4724 | 194.1053 | 198.2338 | 197.0615 | 211.5869 | 208.4117 | 209.7799 | 411.5932 | 404.3425 | 409.9918 | 415.2467 | 409.9733 | 407.3631 | 413.3945 | 412.0783 | 412.8414 | 368.4577 | 369.1425 | 368.5876 | 115.024 | 115.579 | 114.4309 | 413.1285 | 416.0854 | 408.6791 | 417.7939 | 419.5932 | 416.514
174 | Voltage Phase 1 |  | 388.2641 | 387.5511 | 386.9174 | 387.7073 | 387.4836 | 387.6315 | 388.9334 | 388.3397 | 389.2479 | 388.2533 | 388.1513 | 386.7704 | 386.3423 | 387.1246 | 386.7847 | 388.4051 | 388.6947 | 388.5928 | 389.117 | 389.2523 | 389.0602 | 389.5085 | 390.2503 | 390.4623 | 390.0238 | 391.6401 | 391.7716 | 393.81 | 394.7434 | 393.7436 | 394.4654 | 393.6258 | 394.1695 | 395.1822 | 394.5129 | 394.7791 | 393.8401 | 393.6881 | 392.6435 | 393.0159 | 392.3616 | 393.5795 | 383.9394 | 383.481 | 383.3707 | 382.9747 | 380.8294 | 381.8098 | 381.0662 | 385.5022 | 386.0101 | 385.6754 | 386.0428 | 385.6537 | 386.6274 | 385.4451 | 385.1793 | 385.8975 | 394.4695 | 385.4119 | 385.6476 | 385.735 | 385.1328 | 384.3926 | 383.1533 | 386.387 | 386.29 | 393.3895 | 393.2566 | 392.8126 | 392.4107 | 392.1945 | 392.5252 | 392.59 | 391.3191 | 391.7668 | 392.815 | 393.0038 | 392.2923 | 391.7883 | 392.8479 | 393.6353 | 391.1621 | 391.4827 | 391.6231 | 394.8878 | 395.919 | 395.5744 | 395.6564 | 395.4878 | 395.7836 | 386.4995 | 387.2161 | 386.209 | 383.9177 | 383.451 | 383.5436 | 380.266 | 387.0678 | 387.1141 | 386.715 | 388.3051 | 388.6003 | 386.9339 | 388.0573 | 386.8793 | 386.1083 | 387.2325 | 387.2848 | 387.661 | 387.3199 | 389.1295 | 389.3866 | 388.0535 | 387.9746 | 386.0808 | 390.3037 | 393.3854 | 384.4915 | 382.6445 | 387.1941 | 388.041 | 386.3311 | 385.9894 | 392.2217 | 392.497 | 393.0242 | 393.0669 | 392.8805 | 392.1883 | 392.9397 | 392.9462 | 385.4534 | 385.9318 | 385.4666 | 391.3109 | 392.0096 | 392.3896 | 391.8893 | 391.1028 | 391.6318 | 391.0598 | 389.1586 | 388.2585 | 388.0193 | 391.5457 | 391.7004 | 391.6513 | 391.6281 | 394.1862 | 394.0377 | 394.0753 | 393.7108 | 390.3849 | 390.0565 | 390.0321 | 387.9602 | 387.6589 | 386.748 | 391.1575 | 391.2625 | 391.8539 | 391.0021 | 390.918 | 390.7022 | 390.0443 | 390.6852 | 386.2664 | 387.7201 | 386.4187 | 385.6258 | 386.2263 | 386.3082 | 385.8322 | 386.313 | 386.077 | 387.1243 | 384.8367 | 385.8713 | 389.9212 | 390.6934 | 390.4132 | 388.0284 | 387.7968 | 385.5854 | 391.2403 | 390.3618 | 390.6406 | 388.0632 | 387.6086 | 388.1396 | 388.5059 | 389.1731 | 388.4681 | 392.7734 | 392.2895 | 392.4039 | 389.1583 | 388.4236 | 388.9763 | 386.8425 | 387.427 | 388.3141 | 394.2373 | 392.8414 | 394.1276 | 394.1279 | 393.7126 | 393.8521 | 384.4383 | 382.4084 | 382.4591 | 380.6678 | 380.8088 | 380.7841 | 385.9788 | 388.4112 | 386.6851 | 387.3548 | 388.1031 | 385.9949 | 383.6124 | 383.9015 | 383.8327 | 393.0576 | 393.307 | 392.1948 | 393.6078 | 394.125 | 393.3839 | 387.068 | 387.3742 | 387.6238 | 387.2894 | 387.2281 | 387.8787
175 | Voltage Phase 2 |  | 386.1162 | 386.7173 | 385.7052 | 384.607 | 384.7304 | 384.5691 | 386.1375 | 383.432 | 386.4496 | 385.2595 | 384.0411 | 384.9908 | 383.5101 | 382.5452 | 382.7686 | 389.7695 | 389.6612 | 389.8767 | 390.6935 | 390.7328 | 390.2552 | 389.9034 | 391.1307 | 390.639 | 391.3562 | 392.4185 | 392.1262 | 391.8075 | 392.4583 | 391.7868 | 392.6043 | 391.5729 | 392.4397 | 393.8799 | 393.8447 | 394.2563 | 392.5451 | 392.3977 | 392.6408 | 392.4468 | 392.3472 | 393.2294 | 391.9056 | 390.4816 | 391.5342 | 390.4335 | 389.286 | 389.964 | 389.7982 | 381.7107 | 381.4735 | 382.4637 | 385.0928 | 383.965 | 384.1287 | 383.8629 | 383.2989 | 384.0186 | 390.6887 | 382.502 | 383.1293 | 393.9749 | 393.4142 | 392.2578 | 390.9904 | 394.8124 | 394.7076 | 392.6014 | 392.91 | 392.6588 | 391.0334 | 390.9886 | 390.7425 | 391.3545 | 389.3866 | 390.6586 | 394.0321 | 394.265 | 393.2913 | 392.836 | 394.2957 | 394.9097 | 389.1173 | 388.9279 | 389.3839 | 393.8973 | 394.2282 | 394.0718 | 394.6437 | 394.13 | 394.9829 | 394.5494 | 394.8925 | 393.8838 | 392.0005 | 392.5687 | 392.052 | 388.3751 | 381.3617 | 382.4113 | 380.4896 | 383.0838 | 382.5013 | 382.6371 | 382.0497 | 381.9776 | 382.4868 | 383.7468 | 384.1285 | 383.8503 | 385.13 | 385.1713 | 385.1044 | 383.2865 | 383.0254 | 381.8683 | 386.4217 | 387.2332 | 392.6136 | 391.3571 | 394.3681 | 395.2393 | 393.9332 | 393.6915 | 390.1962 | 390.1006 | 390.6992 | 393.2138 | 392.9273 | 392.4963 | 393.7762 | 393.3405 | 393.7981 | 393.7752 | 393.8197 | 389.7375 | 389.7364 | 390.5642 | 389.8905 | 390.2445 | 390.8649 | 390.3955 | 388.7134 | 387.4984 | 387.3201 | 392.7039 | 393.0231 | 392.7546 | 392.6679 | 389.1196 | 386.8175 | 386.186 | 386.4724 | 386.8192 | 384.3913 | 384.1288 | 383.4532 | 381.8725 | 383.0827 | 387.6346 | 385.6198 | 386.3508 | 385.4752 | 384.74 | 385.4522 | 384.3005 | 384.2383 | 384.4596 | 384.53 | 382.136 | 382.6006 | 380.7853 | 382.1909 | 381.5777 | 382.6405 | 382.0448 | 382.3062 | 379.0173 | 380.6895 | 389.8078 | 390.872 | 390.9857 | 385.1261 | 386.0327 | 383.0533 | 387.1915 | 386.4386 | 385.0125 | 385.0146 | 384.1147 | 383.7226 | 384.1563 | 382.2769 | 383.7354 | 392.2608 | 391.4256 | 392.2731 | 386.9452 | 386.1435 | 386.5744 | 384.1817 | 385.0788 | 386.017 | 394.5173 | 393.1307 | 394.3738 | 394.4861 | 393.8972 | 394.4909 | 392.2379 | 389.9401 | 390.2834 | 388.3575 | 388.4059 | 388.4544 | 383.8016 | 384.6028 | 384.0892 | 383.3555 | 384.4915 | 384.8742 | 380.9635 | 380.8886 | 381.7089 | 386.5121 | 386.6692 | 386.2132 | 392.8599 | 393.3441 | 392.0817 | 383.3045 | 384.9562 | 384.4667 | 385.0195 | 384.72 | 386.0963
176 | Voltage Phase 3 |  | 379.1138 | 378.9259 | 377.6324 | 378.3299 | 378.3192 | 378.2905 | 379.3436 | 379.4761 | 379.6882 | 379.214 | 378.9702 | 377.5803 | 377.8619 | 377.9436 | 378.0915 | 388.9507 | 388.8455 | 389.296 | 390.3522 | 389.9539 | 389.0529 | 388.7398 | 389.7605 | 389.0869 | 390.2733 | 390.7001 | 390.5761 | 393.0031 | 393.3387 | 392.3907 | 391.6277 | 391.6095 | 391.2347 | 391.2354 | 390.9169 | 390.7461 | 389.7799 | 390.2195 | 388.9201 | 388.9171 | 388.3301 | 389.4741 | 388.0332 | 387.1348 | 388.4244 | 387.8673 | 387.8373 | 388.9896 | 389.0546 | 377.1345 | 378.0223 | 377.2223 | 377.6215 | 377.0165 | 378.1057 | 377.3684 | 377.8238 | 377.0073 | 385.1087 | 376.6192 | 376.9174 | 391.2808 | 391.6155 | 390.5056 | 391.4287 | 393.5194 | 393.2478 | 389.2656 | 388.8925 | 388.3023 | 388.5757 | 388.3694 | 388.6977 | 388.6993 | 387.3777 | 388.3758 | 392.0933 | 392.26 | 391.281 | 391.1024 | 392.7999 | 392.9307 | 389.6655 | 389.4943 | 389.5616 | 392.2081 | 392.6364 | 392.5833 | 391.8213 | 391.5823 | 391.8355 | 390.504 | 389.7223 | 390.6406 | 390.1956 | 391.4757 | 389.4873 | 388.5945 | 378.2448 | 378.4693 | 378.7195 | 380.1138 | 379.8886 | 378.0668 | 379.1275 | 377.8041 | 377.9981 | 378.4664 | 378.1517 | 378.7359 | 378.3372 | 379.3531 | 380.1629 | 379.5038 | 378.6259 | 376.8959 | 380.4741 | 383.6371 | 389.4464 | 388.6583 | 390.8068 | 391.7011 | 390.6139 | 392.7518 | 390.3921 | 391.5788 | 391.7321 | 392.6519 | 391.7614 | 391.829 | 392.9538 | 392.1305 | 392.1866 | 391.8255 | 391.5054 | 388.5952 | 389.0021 | 389.4646 | 388.8311 | 387.4098 | 388.0265 | 387.5187 | 385.4316 | 384.5835 | 384.5211 | 392.9779 | 392.6905 | 392.4282 | 392.4696 | 384.3642 | 385.4394 | 385.7145 | 384.8034 | 381.5387 | 381.4186 | 380.8696 | 379.7609 | 380.144 | 378.1388 | 381.3724 | 382.0777 | 382.6908 | 382.0544 | 383.4097 | 383.0437 | 382.4328 | 383.8591 | 376.816 | 378.1704 | 377.0081 | 376.334 | 376.3874 | 376.6089 | 377.3972 | 376.5607 | 376.067 | 377.8738 | 375.5023 | 377.1144 | 385.2007 | 385.8763 | 385.6395 | 377.9299 | 378.2784 | 375.522 | 381.5492 | 380.4007 | 380.6953 | 378.4195 | 378.381 | 377.9886 | 379.1902 | 380.4515 | 379.6748 | 388.3934 | 387.6425 | 387.5642 | 386.1824 | 385.7353 | 386.064 | 385.3956 | 386.3858 | 387.1795 | 393.0236 | 391.7246 | 393.1274 | 392.8652 | 391.8794 | 392.5566 | 388.8506 | 386.3064 | 387.4751 | 388.7902 | 387.4941 | 388.4305 | 377.1754 | 378.5501 | 377.6105 | 377.6129 | 378.8078 | 377.4156 | 375.1075 | 375.1915 | 375.0409 | 385.1267 | 385.8653 | 384.0839 | 389.409 | 390.002 | 390.1587 | 377.7938 | 378.6241 | 378.7119 | 378.1399 | 378.0881 | 378.6528
177 | Power Factor |  | 0.983 | 0.98353 | 0.98329 | 0.98388 | 0.98323 | 0.98377 | 0.98408 | 0.98396 | 0.98403 | 0.98422 | 0.98439 | 0.98468 | 0.9851 | 0.98439 | 0.98426 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.98654 | 0.98739 | 0.98659 | 0.98698 | 0.98727 | 0.98656 | 0.98671 | 0.98778 | 0.98852 | 0.98688 | 0.98644 | 0.98797 | 0.98866 | 0.98816 | 0.98819 | 0.98774 | 0.98838 | 0.98839 | 0.98861 | 0.98787 | 0.98767 | 0.98741 | 0.98564 | 0.98517 | 0.98528 | 0.98526 | 0.9854 | 0.98461 | 0.98472 | 0.98457 | 0.98451 | 0.98413 | 0.98383 | 0.98422 | 0.98755 | 0.98744 | 0.98699 | 0.98699 | 0.98712 | 0.9867 | 0.98768 | 0.98686 | 0.98799 | 0.9873 | 0.98733 | 0.98751 | 0.98775 | 0.98724 | 0.98721 | 1 | 1 | 1 | 1 | 1 | 1 | 0.98655 | 0.98532 | 0.98654 | 0.98696 | 0.98601 | 0.98688 | 0.98784 | 0.98756 | 0.98743 | 0.98783 | 0.98774 | 0.98748 | 0.98748 | 0.98699 | 0.98715 | 0.98667 | 0.9852 | 0.98551 | 0.98462 | 0.98521 | 0.98478 | 0.98558 | 0.9848 | 0.98503 | 0.98369 | 0.9837 | 0.98407 | 0.98406 | 0.98416 | 0.98374 | 0.98414 | 0.98354 | 0.98404 | 0.98406 | 0.98393 | 0.98405 | 0.98781 | 0.98767 | 0.98838 | 0.98855 | 0.988 | 0.98771 | 0.98723 | 0.98696 | 0.98691 | 1 | 1 | 1 | 1 | 1 | 0.98669 | 0.98647 | 0.98684 | 0.98596 | 0.98538 | 0.98673 | 0.98612 | 0.9877 | 0.98836 | 0.98796 | 0.98857 | 0.98722 | 0.98763 | 1 | 1 | 1 | 1 | 0.98532 | 0.98452 | 0.98438 | 0.9845 | 0.98478 | 0.98406 | 0.98362 | 0.98435 | 0.9836 | 0.9844 | 0.9847 | 0.98371 | 0.98447 | 0.98447 | 0.98427 | 0.98479 | 0.98453 | 0.98432 | 0.98513 | 0.9844 | 0.9839 | 0.98476 | 0.98332 | 0.98379 | 0.98405 | 0.98415 | 0.98395 | 0.98548 | 0.9845 | 0.98535 | 0.98847 | 0.98794 | 0.98797 | 0.98367 | 0.98392 | 0.98383 | 0.98403 | 0.98392 | 0.98361 | 0.9841 | 0.98392 | 0.98396 | 0.9854 | 0.98473 | 0.9853 | 0.98804 | 0.98816 | 0.98677 | 0.98627 | 0.98617 | 0.98708 | 0.9861 | 0.98722 | 0.98701 | 1 | 1 | 1 | 1 | 1 | 1 | 0.98802 | 0.98709 | 0.98666 | 0.98743 | 0.98732 | 0.9872 | 0.98471 | 0.98482 | 0.98516 | 0.9845 | 0.98471 | 0.98494 | 0.98423 | 0.98456 | 0.98481 | 0.98538 | 0.98537 | 0.98586 | 0.98748 | 0.98732 | 0.98697 | 0.9841 | 0.98392 | 0.98415 | 0.98467 | 0.98444 | 0.98485
178 | KvA |  | 297.4002 | 295.9688 | 296.2024 | 278.8816 | 279.7215 | 277.4669 | 265.2827 | 264.7047 | 266.0056 | 257.1008 | 254.2769 | 254.6969 | 246.8727 | 246.0883 | 244.8459 | 19.6327 | 19.0735 | 19.5051 | 20.5655 | 20.4138 | 20.5025 | 19.815 | 19.0676 | 19.5561 | 19.969 | 20.2063 | 20.7082 | 52.7541 | 53.0711 | 52.599 | 55.3682 | 55.6972 | 55.334 | 59.5149 | 59.6074 | 59.7857 | 57.0882 | 56.9964 | 57.7809 | 60.0533 | 59.9164 | 60.1891 | 116.9815 | 116.8214 | 117.6491 | 118.1612 | 127.9838 | 127.5924 | 127.308 | 231.8969 | 233.9584 | 232.8021 | 257.68 | 257.8798 | 258.9923 | 258.2899 | 258.1311 | 257.9915 | 255.3382 | 255.6266 | 257.7859 | 121.0052 | 120.3011 | 121.0052 | 129.2498 | 129.6764 | 129.3082 | 59.896 | 60.5904 | 59.9891 | 54.8808 | 54.6528 | 55.1598 | 55.2447 | 54.8844 | 54.9074 | 19.3043 | 19.9726 | 19.6288 | 20.6619 | 20.0945 | 21.2378 | 53.3917 | 53.5965 | 53.4939 | 58.0551 | 57.343 | 58.0521 | 60.2698 | 59.5153 | 60.0978 | 123.8604 | 122.6675 | 123.1013 | 130.2757 | 130.0259 | 130.4278 | 128.0659 | 233.3126 | 233.1979 | 233.3763 | 233.2087 | 233.7648 | 233.7109 | 232.3788 | 233.665 | 259.8334 | 260.2949 | 258.7534 | 256.1062 | 258.9574 | 261.2513 | 255.8256 | 256.6155 | 253.7489 | 252.1496 | 257.1688 | 254.8527 | 117.4686 | 117.7043 | 117.9701 | 119.1463 | 119.4082 | 119.2404 | 52.8883 | 52.5699 | 52.6022 | 19.3076 | 18.9079 | 19.4552 | 20.8503 | 19.9527 | 127.9084 | 128.1674 | 128.222 | 56.6457 | 57.1396 | 57.8228 | 57.7325 | 60.1257 | 60.1361 | 59.7488 | 60.5038 | 61.2534 | 61.1388 | 20.7578 | 20.9116 | 20.5648 | 20.537 | 230.0805 | 230.7365 | 229.9608 | 229.4551 | 254.0111 | 254.6045 | 256.0167 | 251.9009 | 252.7801 | 252.3068 | 256.9721 | 255.2648 | 254.8903 | 255.6355 | 253.5096 | 254.5253 | 252.7785 | 252.8513 | 253.6246 | 254.2038 | 254.2623 | 253.9183 | 256.7501 | 257.7773 | 254.4604 | 253.5835 | 253.7932 | 230.9585 | 230.0722 | 230.391 | 59.794 | 59.6766 | 59.3078 | 255.791 | 256.2965 | 254.5574 | 254.4336 | 254.1602 | 253.5396 | 256.361 | 256.8544 | 254.819 | 230.0892 | 229.2124 | 229.5441 | 59.4338 | 59.6337 | 58.9141 | 56.8184 | 56.3691 | 57.0827 | 52.5802 | 52.7512 | 52.6716 | 19.7068 | 19.8131 | 19.7217 | 20.5707 | 21.0419 | 20.5815 | 118.9043 | 119.7305 | 118.8477 | 129.1187 | 127.9567 | 128.3392 | 253.8509 | 250.6833 | 252.5093 | 255.214 | 253.5668 | 252.1986 | 252.9578 | 251.668 | 253.2047 | 228.8341 | 228.8026 | 227.0325 | 59.0824 | 59.7982 | 59.0778 | 254.5256 | 257.9491 | 253.7417 | 258.0413 | 258.8129 | 256.5197
179 | Avg Amps |  | 471.7112 | 470.323 | 471.6813 | 444.5837 | 445.7103 | 442.5699 | 422.2909 | 421.6897 | 422.9586 | 410.0879 | 406.1561 | 407.5648 | 395.6363 | 394.0682 | 392.2818 | 43.6932 | 42.3757 | 43.3114 | 45.3766 | 45.1183 | 44.8105 | 43.3801 | 42.5601 | 43.5842 | 44.561 | 44.6928 | 44.9335 | 98.9901 | 99.2961 | 98.6985 | 102.8403 | 103.6064 | 103.0753 | 109.1555 | 109.0139 | 109.3268 | 105.2454 | 105.4527 | 106.877 | 109.0328 | 109.687 | 109.7441 | 193.1486 | 193.3641 | 193.9137 | 195.0282 | 209.8411 | 208.991 | 208.5966 | 373.7954 | 376.3387 | 375.1054 | 412.2233 | 413.7326 | 414.6323 | 414.1845 | 413.9436 | 413.4433 | 401.7433 | 410.5544 | 413.0934 | 198.2169 | 197.0177 | 198.1755 | 210.8151 | 209.8403 | 209.4777 | 109.7621 | 110.3409 | 109.7795 | 102.2083 | 102.3627 | 102.6635 | 102.636 | 102.6302 | 102.4973 | 41.5579 | 42.4692 | 42.1896 | 44.5324 | 43.8586 | 44.9091 | 100.0919 | 100.4658 | 100.2085 | 107.0996 | 105.6806 | 106.7282 | 109.6902 | 109.6648 | 109.4475 | 201.7879 | 200.1951 | 200.5353 | 212.5506 | 211.6159 | 212.5504 | 210.0381 | 375.117 | 374.5921 | 375.3003 | 373.8012 | 374.384 | 375.7209 | 372.852 | 375.7386 | 415.9383 | 415.9529 | 413.5079 | 409.3216 | 413.4576 | 415.9506 | 407.512 | 409.4437 | 405.81 | 404.7845 | 408.3836 | 402.3259 | 193.9921 | 194.5816 | 193.239 | 194.2933 | 195.6097 | 194.8844 | 98.627 | 97.9913 | 98.3123 | 42.757 | 42.0387 | 42.7479 | 44.6883 | 44.064 | 209.0182 | 209.116 | 209.2705 | 105.4131 | 105.8838 | 107.1133 | 106.5708 | 110.347 | 110.2649 | 110.1396 | 111.1045 | 111.9844 | 112.1136 | 44.5951 | 44.6187 | 44.4138 | 44.0918 | 363.5962 | 364.7379 | 363.4716 | 363.105 | 403.234 | 404.8295 | 406.9483 | 402.7558 | 403.9368 | 404.5305 | 407.4279 | 404.8705 | 404.0624 | 405.9487 | 401.927 | 403.6808 | 401.7732 | 400.8173 | 407.1818 | 406.2521 | 408.0559 | 408.2743 | 412.4587 | 413.3566 | 408.509 | 406.614 | 407.4392 | 371.7415 | 372.0711 | 371.6853 | 109.5799 | 109.3711 | 108.5172 | 408.4797 | 408.6728 | 408.4344 | 403.047 | 403.5292 | 403.0218 | 409.3046 | 410.3861 | 407.1268 | 368.4741 | 367.0903 | 367.7692 | 108.4562 | 108.934 | 107.7902 | 106.6318 | 105.8933 | 106.5109 | 100.0822 | 99.8304 | 99.8575 | 43.1081 | 42.6139 | 42.6379 | 44.7164 | 44.8675 | 44.6982 | 195.729 | 199.1823 | 197.8044 | 212.0562 | 210.561 | 210.6585 | 407.0918 | 400.6004 | 405.0268 | 408.9162 | 405.0924 | 404.1652 | 408.2635 | 405.8608 | 408.0494 | 363.4311 | 363.1467 | 361.3949 | 110.2655 | 110.4119 | 109.5581 | 407.6017 | 411.7574 | 405.381 | 412.5592 | 413.809 | 410.5173
180 | Avg Volts |  | 384.498 | 384.3981 | 383.4183 | 383.5481 | 383.5111 | 383.497 | 384.8048 | 383.7493 | 385.1285 | 384.2423 | 383.7209 | 383.1139 | 382.5714 | 382.5378 | 382.5482 | 389.0418 | 389.0671 | 389.2552 | 390.0542 | 389.9797 | 389.4561 | 389.3839 | 390.3805 | 390.0627 | 390.5511 | 391.5862 | 391.4913 | 392.8735 | 393.5134 | 392.6404 | 392.8991 | 392.2694 | 392.6146 | 393.4325 | 393.0915 | 393.2605 | 392.0551 | 392.1018 | 391.4015 | 391.4599 | 391.013 | 392.0944 | 387.9594 | 387.0325 | 387.7764 | 387.0918 | 385.9842 | 386.9211 | 386.6397 | 381.4491 | 381.8353 | 381.7871 | 382.919 | 382.2117 | 382.9539 | 382.2255 | 382.1007 | 382.3078 | 390.0889 | 381.511 | 381.8981 | 390.3302 | 390.0542 | 389.052 | 388.5241 | 391.5729 | 391.4151 | 391.7522 | 391.6864 | 391.2579 | 390.6733 | 390.5175 | 390.6552 | 390.8813 | 389.3611 | 390.2671 | 392.9801 | 393.1762 | 392.2882 | 391.9089 | 393.3145 | 393.8253 | 389.9816 | 389.9683 | 390.1896 | 393.6644 | 394.2612 | 394.0765 | 394.0405 | 393.7334 | 394.2007 | 390.5176 | 390.6103 | 390.2445 | 388.7046 | 389.1651 | 388.361 | 385.7452 | 382.2248 | 382.6649 | 381.9747 | 383.8342 | 383.6634 | 382.5459 | 383.0782 | 382.2204 | 382.1977 | 383.1486 | 383.1883 | 383.4158 | 383.5957 | 384.5513 | 384.8846 | 383.6146 | 383.2086 | 381.615 | 385.7331 | 388.0852 | 388.8505 | 387.5533 | 390.7897 | 391.6604 | 390.2927 | 390.8109 | 390.9367 | 391.3921 | 391.8185 | 392.9775 | 392.5231 | 392.1712 | 393.2232 | 392.8057 | 390.4794 | 390.5108 | 390.2639 | 389.8812 | 390.2494 | 390.8061 | 390.2036 | 389.5857 | 390.1744 | 389.658 | 387.7679 | 386.7801 | 386.6201 | 392.4092 | 392.4713 | 392.278 | 392.2552 | 389.2233 | 388.7649 | 388.6586 | 388.3289 | 386.2476 | 385.2888 | 385.0102 | 383.7248 | 383.2251 | 382.6565 | 386.7215 | 386.32 | 386.9652 | 386.1772 | 386.3559 | 386.3994 | 385.5925 | 386.2609 | 382.514 | 383.4735 | 381.8543 | 381.5201 | 381.133 | 381.7026 | 381.6024 | 381.8381 | 381.3962 | 382.4348 | 379.7855 | 381.225 | 388.3099 | 389.1472 | 389.0128 | 383.6948 | 384.036 | 381.3869 | 386.6603 | 385.7337 | 385.4495 | 383.8324 | 383.3681 | 383.2836 | 383.9508 | 383.9672 | 383.9595 | 391.1425 | 390.4525 | 390.747 | 387.4286 | 386.7675 | 387.2049 | 385.4733 | 386.2972 | 387.1702 | 393.9261 | 392.5656 | 393.8763 | 393.8264 | 393.1631 | 393.6332 | 388.5089 | 386.2183 | 386.7392 | 385.9385 | 385.5696 | 385.8897 | 382.3186 | 383.8547 | 382.7949 | 382.7744 | 383.8008 | 382.7616 | 379.8945 | 379.9939 | 380.1941 | 388.2321 | 388.6138 | 387.4973 | 391.9589 | 392.4904 | 391.8748 | 382.7221 | 383.6515 | 383.6008 | 383.4829 | 383.3454 | 384.2093
181 | Hz |  | 50.0885 | 50.0689 | 49.9778 | 50.0532 | 50.0655 | 50.1449 | 50.0653 | 50.0799 | 50.1477 | 50.132 | 50.1583 | 50.0952 | 50.069 | 50.0577 | 50.048 | 50.0014 | 49.982 | 49.9151 | 49.9474 | 49.9128 | 49.9202 | 49.9227 | 49.9126 | 49.9881 | 49.9227 | 50.0179 | 50.0688 | 50.1475 | 50.0862 | 49.9509 | 49.9418 | 49.9821 | 50.0176 | 50.061 | 50.0892 | 50.068 | 49.958 | 50.0565 | 49.9117 | 49.9975 | 49.9761 | 50.0889 | 50.0163 | 49.9434 | 50.0869 | 50.0936 | 50.0265 | 50.0185 | 50.0407 | 49.865 | 49.9038 | 49.9625 | 50.0907 | 50.0122 | 49.8577 | 50.0182 | 50.0274 | 49.9475 | 50.0417 | 50.1261 | 50.1284 | 49.945 | 49.9392 | 49.9397 | 49.9102 | 50.0631 | 50.0327 | 50.0306 | 49.9723 | 49.9556 | 50.0876 | 49.9798 | 50.1305 | 50.0809 | 50.0327 | 49.9785 | 49.9705 | 49.9765 | 49.955 | 49.9433 | 49.9928 | 50.0868 | 49.926 | 49.9431 | 49.9604 | 49.8776 | 49.9252 | 49.9871 | 50.0405 | 50.0211 | 50.0631 | 50.0717 | 50.0511 | 50.0466 | 49.9605 | 49.9962 | 49.9993 | 50.0326 | 50.125 | 50.1317 | 50.0952 | 50.0735 | 50.0325 | 50.029 | 49.9764 | 50.0032 | 50.0087 | 50.0111 | 50.0476 | 49.9611 | 50.0178 | 50.0507 | 50.0536 | 49.9935 | 50.004 | 49.9297 | 50.0601 | 50.024 | 50.0575 | 50.0123 | 50.1775 | 50.108 | 50.0719 | 50.073 | 49.9657 | 49.961 | 50.0151 | 49.9395 | 49.9556 | 49.9676 | 49.948 | 49.8984 | 49.8999 | 49.8783 | 49.8943 | 50.0758 | 50.0657 | 50.0702 | 49.9924 | 50.0805 | 50.0579 | 50.0693 | 49.9713 | 49.9505 | 49.915 | 49.9437 | 49.9621 | 49.98 | 49.9866 | 50.112 | 50.1316 | 50.1773 | 50.1568 | 50.1493 | 50.1049 | 49.9818 | 49.9969 | 49.998 | 50.0716 | 49.9889 | 49.9143 | 49.9113 | 49.9202 | 49.942 | 49.9816 | 49.9231 | 50.0247 | 49.9589 | 50.0579 | 49.9014 | 50.1222 | 50.0678 | 50.1 | 50.087 | 50.0778 | 50.1147 | 49.9431 | 49.9257 | 49.9474 | 50.0748 | 50.0952 | 50.0442 | 49.9403 | 49.9936 | 49.981 | 50.0087 | 49.9202 | 49.926 | 50.0725 | 50.0518 | 50.0421 | 50.041 | 50.0088 | 50.0214 | 50.1845 | 50.1506 | 50.0839 | 50.0539 | 50.0693 | 50.0828 | 50.0186 | 50.1223 | 49.985 | 50.0648 | 50.0385 | 50.0368 | 49.9596 | 49.9304 | 49.9603 | 49.9857 | 49.9625 | 49.9219 | 49.9219 | 49.9521 | 49.8836 | 49.9773 | 50.0042 | 50.0267 | 49.9339 | 50.0298 | 49.9564 | 49.9121 | 49.9334 | 50.0116 | 49.9703 | 49.982 | 49.9802 | 49.948 | 50.0155 | 49.9794 | 50.0346 | 50.0662 | 50.0362 | 49.9878 | 50.0324 | 50.0491
182
183 | Motor Temperatures
184 | T1 (terminal post) |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
185 | T2 (ambient terminal box) |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
186 | T3 (ambient rig enclosure) |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
187 | T4 |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
188 | T5 |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
189 | T6 |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
190 | T7 |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
191 | T8 |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
192 | T9 |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
193 | T10 |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
194 | T11 |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
195 | T12 |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
196 | T13 |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
197 | T14 |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
198 | T15 |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
199 | T16 |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
200 | T17 |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
201 | T18 |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
202 | T19 |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
203 | T20 |  | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1
204 | T21 |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
205 | T22 |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
206 | T23 |  | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2
207 | T24 |  | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2
208 | T25 |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
209 | T26 |  | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1
210 | T27 |  | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2
211 | T28 |  | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2
212 | T29 |  | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2
213 | T30 |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
214 | T spare 1
215 | T spare 2
216
217 | Max Temp |  | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2
218 | Min Temp |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
219 | Avg Temp |  | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13 | -2508.13
220
221
222 | Calculated Data
223 | Suction Flow at FM conditions | m^3/hr | 1151.4805 | 1152.8279 | 1152.0968 | 1151.4604 | 1154.0277 | 1147.5392 | 1142.2198 | 1144.5347 | 1143.7614 | 1127.7631 | 1131.9011 | 1133.7521 | 1125.7011 | 1125.3593 | 1124.7775 | 170.4691 | 170.7793 | 173.1454 | 185.5478 | 185.3106 | 182.0024 | 173.6105 | 179.6716 | 175.2181 | 186.2916 | 190.8848 | 189.2306 | 405.5737 | 406.1605 | 406.501 | 405.8454 | 405.5364 | 404.5136 | 438.866 | 437.9952 | 440.3912 | 441.9586 | 439.6614 | 437.6309 | 460.2157 | 459.3186 | 458.4065 | 709.7458 | 708.8906 | 708.9545 | 721.6864 | 763.8997 | 761.9131 | 763.2113 | 1069.3069 | 1070.9042 | 1068.5406 | 1140.6536 | 1137.8028 | 1140.7737 | 1141.7769 | 1138.8727 | 1136.4648 | 1139.9488 | 1141.6015 | 1143.08 | 708.5533 | 708.239 | 708.9824 | 753.3499 | 754.6669 | 753.9793 | 459.6092 | 459.1117 | 458.4765 | 402.5823 | 402.5339 | 405.1102 | 404.9291 | 403.8661 | 404.6599 | 179.8175 | 180.006 | 180.6444 | 192.8903 | 193.2239 | 196.0088 | 402.7638 | 402.2725 | 402.9232 | 432.2026 | 432.5648 | 432.9053 | 431.5543 | 433.2524 | 432.0915 | 717.0727 | 716.8703 | 717.2743 | 752.582 | 752.1472 | 750.0536 | 744.4851 | 1058.93 | 1061.3358 | 1060.2397 | 1059.7164 | 1057.6105 | 1057.1208 | 1059.3345 | 1060.6859 | 1120.7046 | 1122.7851 | 1125.4913 | 1126.2432 | 1125.8052 | 1122.9724 | 1128.7409 | 1127.6508 | 1125.5224 | 1094.5429 | 1094.4888 | 1094.2393 | 682.6334 | 679.5682 | 680.3845 | 695.7665 | 697.6081 | 696.4332 | 389.4074 | 389.6914 | 388.8562 | 163.5925 | 166.9995 | 155.5166 | 179.5908 | 180.9583 | 735.1244 | 734.6323 | 734.4339 | 421.724 | 421.0643 | 422.7079 | 422.476 | 444.7665 | 446.4117 | 445.5893 | 444.5517 | 445.6618 | 445.5565 | 175.3381 | 180.2559 | 176.42 | 182.0249 | 1032.9634 | 1033.6461 | 1034.0407 | 1036.3232 | 1100.9827 | 1103.1869 | 1101.1818 | 1107.5314 | 1112.7848 | 1109.5549 | 1106.4373 | 1107.5957 | 1107.953 | 1106.9884 | 1107.5945 | 1107.8572 | 1108.7734 | 1107.5527 | 1138.231 | 1138.4527 | 1142.0461 | 1141.9203 | 1141.2077 | 1141.1278 | 1145.9468 | 1145.4018 | 1146.4713 | 1066.1123 | 1071.2948 | 1069.3823 | 457.3374 | 457.0021 | 458.2307 | 1135.4609 | 1134.0225 | 1134.7348 | 1144.781 | 1140.8975 | 1140.9929 | 1147.2442 | 1141.9289 | 1147.5331 | 1068.0927 | 1069.1057 | 1069.6966 | 458.1127 | 459.1281 | 460.5906 | 432.0657 | 432.1927 | 432.6537 | 402.8876 | 402.368 | 402.4024 | 165.5452 | 166.7393 | 175.6701 | 189.3809 | 185.1499 | 186.6649 | 721.4893 | 722.4118 | 722.2458 | 763.2945 | 764.0845 | 765.0877 | 1133.5116 | 1132.8965 | 1126.0625 | 1134.0115 | 1136.7857 | 1137.393 | 1134.7679 | 1137.4385 | 1134.6126 | 1063.7015 | 1072.4233 | 1068.1636 | 455.8056 | 454.8754 | 455.8404 | 1141.5298 | 1139.8152 | 1139.1977 | 1141.3384 | 1142.9751 | 1143.4111
224 | Suction Flow at suction conditions (from Flowmeters) | m^3/hr | 1269.2262 | 1270.1668 | 1271.0489 | 1266.9549 | 1267.7245 | 1266.2762 | 1253.3469 | 1258.3691 | 1259.0184 | 1243.0235 | 1243.6522 | 1241.5106 | 1229.413 | 1229.854 | 1229.3759 | 170.6896 | 171.2756 | 173.4237 | 185.812 | 185.4773 | 182.2669 | 174.3227 | 180.2283 | 175.4278 | 186.6613 | 191.2738 | 189.7521 | 410.1436 | 410.6347 | 410.4212 | 409.9442 | 409.7748 | 408.6861 | 443.8636 | 442.7745 | 445.4861 | 447.0821 | 444.9715 | 443.4629 | 466.5054 | 466.4149 | 465.2552 | 731.6012 | 730.4765 | 730.5778 | 744.0632 | 791.6681 | 789.5806 | 790.3409 | 1155.6677 | 1157.7121 | 1156.5209 | 1245.5569 | 1245.8538 | 1245.03 | 1253.5526 | 1252.2192 | 1250.7346 | 1252.4294 | 1255.9232 | 1255.5561 | 731.8961 | 731.6168 | 731.7942 | 780.5865 | 782.1289 | 781.4163 | 465.9316 | 465.4707 | 465.061 | 407.198 | 407.0781 | 409.7502 | 409.4813 | 408.6627 | 409.1473 | 180.8857 | 180.8563 | 181.5073 | 193.9535 | 194.328 | 197.2309 | 407.2085 | 406.9548 | 408.074 | 437.8414 | 438.4573 | 438.477 | 437.2093 | 438.9258 | 437.6932 | 740.1854 | 739.7968 | 740.1364 | 779.2445 | 777.5309 | 776.7166 | 770.6592 | 1139.634 | 1141.4914 | 1142.1496 | 1141.2389 | 1139.0023 | 1138.3073 | 1141.7443 | 1140.959 | 1220.5253 | 1222.6087 | 1224.0078 | 1229.1848 | 1229.9968 | 1227.4021 | 1232.9103 | 1232.0966 | 1230.3022 | 1200.3594 | 1201.217 | 1201.2489 | 704.3695 | 702.4048 | 703.1388 | 718.9594 | 721.8457 | 719.985 | 394.8397 | 395.1843 | 394.316 | 164.3678 | 167.7678 | 156.0763 | 180.3324 | 181.8162 | 764.8714 | 763.9256 | 765.452 | 427.8803 | 427.0823 | 428.5392 | 428.09 | 451.9369 | 453.7461 | 452.6066 | 451.5341 | 452.9695 | 452.8054 | 176.9893 | 181.6006 | 177.4138 | 182.9027 | 1117.3446 | 1117.5182 | 1118.7084 | 1118.6845 | 1211.8179 | 1211.2473 | 1209.0505 | 1212.2486 | 1215.2424 | 1215.0122 | 1249.0351 | 1250.7126 | 1253.1355 | 1253.2126 | 1252.0274 | 1251.963 | 1252.9447 | 1254.3633 | 1256.8805 | 1255.3162 | 1258.7729 | 1262.2168 | 1261.3269 | 1261.9601 | 1265.7133 | 1266.0111 | 1266.2992 | 1162.7893 | 1163.9088 | 1165.2976 | 462.7573 | 463.0279 | 464.2643 | 1252.3665 | 1250.9616 | 1251.5064 | 1263.03 | 1258.0375 | 1259.3944 | 1265.5632 | 1261.9628 | 1269.3495 | 1164.6671 | 1164.425 | 1165.44 | 464.4651 | 464.9623 | 466.8919 | 437.5039 | 437.814 | 437.8271 | 406.7138 | 405.7478 | 406.3865 | 166.0037 | 167.2912 | 176.1108 | 189.6091 | 185.4768 | 187.0722 | 746.2678 | 747.1896 | 747.602 | 792.4345 | 793.596 | 793.3262 | 1243.2446 | 1245.3293 | 1242.2904 | 1247.5352 | 1250.4209 | 1251.6936 | 1250.9299 | 1250.6975 | 1250.6288 | 1158.9234 | 1165.8114 | 1159.4545 | 461.1849 | 459.5543 | 461.1948 | 1256.2799 | 1257.0348 | 1256.4184 | 1257.9322 | 1258.709 | 1259.3412
225 | Suction Flow at suction Conditions (from orifice Plate) | m^3/hr | 1029.8197 | 1033.2883 | 1029.3824 | 1023.6252 | 1027.4644 | 1024.3079 | 1012.8533 | 1014.9399 | 1019.1906 | 1000.8623 | 1005.7225 | 997.6357 | 989.2025 | 989.6422 | 986.6675 | 73.1953 | 82.8126 | 79.4865 | 95.6486 | 89.9406 | 95.1317 | 82.8002 | 80.2849 | 81.6204 | 95.4287 | 95.9837 | 98.4044 | 313.8655 | 313.4505 | 314.8769 | 313.4128 | 314.9401 | 313.275 | 342.3787 | 343.8635 | 343.7921 | 341.9576 | 342.7631 | 343.4626 | 363.6445 | 364.643 | 365.6346 | 591.7713 | 589.818 | 592.6283 | 596.6732 | 633.8166 | 632.2516 | 632.4503 | 932.8304 | 931.96 | 932.521 | 1004.0154 | 1003.1053 | 1003.6742 | 1010.4047 | 1015.2573 | 1010.0972 | 1008.5407 | 1010.5903 | 1015.4512 | 588.6431 | 587.4978 | 589.1919 | 626.3167 | 625.8564 | 625.6469 | 360.7214 | 357.4955 | 359.6043 | 309.3802 | 307.6276 | 308.8888 | 309.5396 | 308.8799 | 306.5254 | 83.1324 | 83.0887 | 85.7477 | 105.4488 | 103.3781 | 106.0117 | 310.7532 | 310.4954 | 310.4337 | 337.9718 | 337.6932 | 340.8582 | 340.0975 | 338.3671 | 338.3853 | 597.9771 | 599.3268 | 598.9668 | 632.4455 | 625.8082 | 626.5509 | 616.3912 | 912.7136 | 913.4674 | 915.0752 | 917.9553 | 913.0858 | 914.0106 | 913.2268 | 917.1187 | 982.4414 | 983.649 | 982.0972 | 989.5958 | 989.9525 | 992.9106 | 993.8674 | 992.8752 | 994.7658 | 963.8959 | 967.397 | 965.5232 | 570.29 | 571.6501 | 571.1958 | 576.2208 | 577.0197 | 579.2492 | 298.8347 | 297.5686 | 296.6989 | 70.9901 | 76.6304 | 75.7204 | 84.3887 | 92.4647 | 613.7579 | 610.5059 | 610.2641 | 327.2339 | 329.7415 | 329.6843 | 329.1593 | 350.768 | 350.1487 | 349.6766 | 345.6774 | 345.1779 | 346.7998 | 88.7528 | 88.1888 | 87.4609 | 87.0573 | 894.1563 | 897.4812 | 895.0107 | 897.7461 | 972.4105 | 975.1973 | 972.9486 | 979.9477 | 982.7264 | 980.4297 | 985.4754 | 986.4837 | 984.7731 | 985.9678 | 982.5348 | 986.1016 | 984.3795 | 985.9521 | 989.0984 | 988.2249 | 989.9247 | 1000.3143 | 996.2335 | 998.3187 | 998.5415 | 1001.3467 | 998.5198 | 913.8565 | 914.8163 | 919.7901 | 355.0406 | 354.4568 | 357.5956 | 991.9321 | 992.947 | 992.1709 | 1001.9422 | 998.8599 | 1001.378 | 1004.7608 | 1001.2675 | 1003.1321 | 921.8535 | 919.4395 | 920.5623 | 359.1456 | 357.1086 | 360.9452 | 341.6169 | 338.4678 | 338.6444 | 312.6246 | 308.1911 | 310.3888 | 71.8737 | 72.4298 | 79.4564 | 87.4731 | 92.388 | 93.7882 | 600.4855 | 597.4921 | 595.7325 | 633.1538 | 634.499 | 632.9529 | 994.4701 | 994.8971 | 994.8722 | 1000.5321 | 1003.5772 | 1000.3827 | 1000.2454 | 1001.554 | 1000.2746 | 920.4018 | 921.8313 | 924.1481 | 360.7183 | 357.9093 | 360.1539 | 1002.0917 | 1002.4822 | 999.9429 | 1002.0052 | 1000.967 | 1000.501
226 | ratio suction orifice / FM (suction conds) | % | 81.1376 | 81.3506 | 80.9868 | 80.7941 | 81.0479 | 80.8913 | 80.8119 | 80.6552 | 80.9512 | 80.5184 | 80.8685 | 80.3566 | 80.4614 | 80.4683 | 80.2576 | 42.8821 | 48.3505 | 45.8337 | 51.476 | 48.4914 | 52.1936 | 47.4982 | 44.5462 | 46.5265 | 51.124 | 50.1813 | 51.8595 | 76.5258 | 76.3332 | 76.7204 | 76.4525 | 76.8569 | 76.6542 | 77.136 | 77.6611 | 77.1724 | 76.4865 | 77.0304 | 77.4501 | 77.9508 | 78.18 | 78.588 | 80.8871 | 80.7443 | 81.1178 | 80.1912 | 80.0609 | 80.0744 | 80.0225 | 80.7179 | 80.5002 | 80.6316 | 80.6078 | 80.5155 | 80.6145 | 80.6033 | 81.0766 | 80.7603 | 80.5268 | 80.4659 | 80.8766 | 80.4272 | 80.3013 | 80.5133 | 80.2367 | 80.0196 | 80.0658 | 77.4194 | 76.803 | 77.3241 | 75.9778 | 75.5697 | 75.3847 | 75.5931 | 75.5831 | 74.9181 | 45.9585 | 45.9418 | 47.242 | 54.3681 | 53.1977 | 53.75 | 76.3131 | 76.2973 | 76.0729 | 77.1905 | 77.0185 | 77.7368 | 77.7883 | 77.0898 | 77.3111 | 80.7875 | 81.0124 | 80.9265 | 81.1614 | 80.4866 | 80.6666 | 79.9823 | 80.0883 | 80.024 | 80.1187 | 80.435 | 80.1654 | 80.2956 | 79.9852 | 80.3814 | 80.4933 | 80.4549 | 80.2362 | 80.5083 | 80.4841 | 80.8953 | 80.6115 | 80.5842 | 80.8554 | 80.3006 | 80.5347 | 80.3766 | 80.9646 | 81.3847 | 81.2351 | 80.1465 | 79.9367 | 80.453 | 75.6851 | 75.2987 | 75.244 | 43.1898 | 45.6765 | 48.515 | 46.7962 | 50.8562 | 80.2433 | 79.9169 | 79.726 | 76.4779 | 77.208 | 76.9321 | 76.8902 | 77.6144 | 77.1684 | 77.2584 | 76.5562 | 76.2034 | 76.5892 | 50.1458 | 48.5619 | 49.2977 | 47.5976 | 80.0251 | 80.3102 | 80.0039 | 80.2502 | 80.2439 | 80.5118 | 80.4721 | 80.8372 | 80.8667 | 80.693 | 78.8989 | 78.8737 | 78.5847 | 78.6752 | 78.4755 | 78.7644 | 78.5653 | 78.6018 | 78.6947 | 78.7232 | 78.642 | 79.2506 | 78.983 | 79.1086 | 78.8916 | 79.0946 | 78.8534 | 78.5918 | 78.5986 | 78.9318 | 76.7229 | 76.5519 | 77.0242 | 79.2046 | 79.3747 | 79.2781 | 79.3285 | 79.3983 | 79.5127 | 79.3924 | 79.3421 | 79.0273 | 79.1517 | 78.9608 | 78.9884 | 77.3246 | 76.8038 | 77.3081 | 78.0832 | 77.3086 | 77.3466 | 76.866 | 75.9563 | 76.3777 | 43.2964 | 43.2956 | 45.1173 | 46.1334 | 49.8111 | 50.1348 | 80.4652 | 79.9653 | 79.6858 | 79.8998 | 79.9524 | 79.7847 | 79.9899 | 79.8903 | 80.0837 | 80.2007 | 80.2592 | 79.9223 | 79.9601 | 80.0796 | 79.9817 | 79.4187 | 79.0721 | 79.7054 | 78.2155 | 77.8818 | 78.0915 | 79.7666 | 79.7498 | 79.5868 | 79.6549 | 79.5233 | 79.4464
227 | Error message if orifice plate ≠ Suction FM | - | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
228
229
230 | isentropic compression DH | KJ/kg | 22.5858 | 22.5945 | 22.5898 | 26.4051 | 26.3632 | 26.1602 | 30.3739 | 30.064 | 29.9543 | 34.0164 | 34.08 | 33.9729 | 38.4724 | 38.453 | 38.4347 | 13.9084 | 13.9362 | 13.9908 | 13.98 | 13.9102 | 13.8446 | 13.9692 | 13.979 | 13.9459 | 14.0135 | 13.9108 | 13.8987 | 17.379 | 17.4198 | 17.4021 | 17.3755 | 17.3653 | 17.3857 | 17.5685 | 17.5657 | 17.4802 | 17.3063 | 17.3122 | 17.316 | 17.2598 | 17.4555 | 17.4241 | 23.8757 | 23.798 | 23.8616 | 23.7136 | 23.9429 | 23.8317 | 23.7647 | 30.0564 | 30.0934 | 30.0218 | 32.7111 | 32.4941 | 32.7043 | 30.0626 | 30.1014 | 30.0816 | 29.8698 | 30.0091 | 30.2085 | 23.9068 | 23.9539 | 23.9926 | 24.0765 | 24.1659 | 24.137 | 17.8387 | 17.8348 | 17.7901 | 17.6621 | 17.6186 | 17.614 | 17.5831 | 17.6185 | 17.5547 | 13.8622 | 13.8754 | 13.8078 | 13.9171 | 13.93 | 13.8908 | 17.4814 | 17.4468 | 17.4123 | 17.3978 | 17.375 | 17.3405 | 17.3764 | 17.395 | 17.3615 | 24.1403 | 24.1532 | 24.1358 | 24.0721 | 24.0465 | 24.0353 | 24.0953 | 30.2522 | 30.2357 | 30.2757 | 30.2619 | 30.2427 | 30.2401 | 30.2288 | 30.2689 | 32.609 | 32.6896 | 32.5797 | 30.3316 | 30.2454 | 30.2446 | 30.1078 | 30.0184 | 29.9212 | 32.439 | 32.4924 | 32.4928 | 24.0778 | 24.0881 | 24.1833 | 24.1077 | 24.1173 | 24.1207 | 17.5006 | 17.5874 | 17.6112 | 13.935 | 13.9609 | 13.9461 | 13.9902 | 13.9002 | 23.879 | 23.8399 | 23.7801 | 17.4269 | 17.4004 | 17.416 | 17.3904 | 17.4404 | 17.3976 | 17.4039 | 18.6916 | 18.7543 | 18.6953 | 14.1866 | 14.1012 | 14.0413 | 13.9593 | 30.208 | 30.2837 | 30.3079 | 30.3579 | 30.231 | 30.2697 | 30.2537 | 30.6917 | 30.7726 | 30.5735 | 31.3299 | 31.3071 | 31.341 | 31.3432 | 31.0641 | 31.0878 | 31.0817 | 30.9129 | 32.6359 | 32.6445 | 32.7194 | 30.114 | 30.1259 | 30.2468 | 30.1461 | 30.1542 | 30.1818 | 30.0959 | 30.1725 | 30.0839 | 17.5783 | 17.5597 | 17.5226 | 32.5761 | 32.5417 | 32.4514 | 29.8141 | 29.7844 | 29.7366 | 30.3579 | 30.244 | 30.2517 | 30.0586 | 30.0869 | 30.1001 | 17.5526 | 17.5265 | 17.4218 | 17.6481 | 17.5801 | 17.7451 | 17.6013 | 17.5287 | 17.5399 | 13.8767 | 13.8889 | 13.7977 | 13.9763 | 13.9278 | 13.9065 | 23.992 | 23.8494 | 23.8626 | 23.9467 | 23.9479 | 23.8322 | 32.7875 | 32.5887 | 32.4273 | 30.1161 | 30.1182 | 30.1198 | 29.8366 | 29.6955 | 29.7901 | 30.378 | 30.5663 | 30.3549 | 17.6012 | 17.728 | 17.5448 | 30.1199 | 30.1564 | 30.2136 | 30.5246 | 30.5469 | 30.4696
231 | Actual Compression DH | KJ/kg | 36.5138 | 36.4867 | 36.5221 | 40.8026 | 40.7047 | 40.7185 | 45.9724 | 45.9952 | 45.9873 | 53.441 | 53.0489 | 53.3056 | 62.4174 | 62.4158 | 62.4148 | 21.193 | 21.1318 | 20.9583 | 20.4474 | 20.1848 | 20.1551 | 20.6111 | 20.4055 | 19.6356 | 19.998 | 20.0023 | 19.7979 | 25.5888 | 25.5523 | 25.6944 | 26.5555 | 26.6108 | 26.7471 | 26.4926 | 26.2516 | 26.4925 | 25.245 | 25.5053 | 25.5029 | 25.7237 | 25.8447 | 25.4901 | 33.7154 | 33.6782 | 33.7084 | 33.7492 | 34.1399 | 34.0701 | 33.948 | 45.3781 | 45.3494 | 45.3177 | 50.8855 | 51.1111 | 50.9655 | 46.5579 | 46.5435 | 46.5709 | 46.5808 | 46.6043 | 46.0595 | 34.8457 | 35.2214 | 35.5067 | 35.6881 | 35.6516 | 35.7802 | 25.7591 | 25.739 | 25.7935 | 26.5352 | 26.5074 | 26.49 | 26.4371 | 26.3523 | 26.155 | 20.1506 | 20.0153 | 20.249 | 19.2704 | 19.2154 | 18.93 | 25.5325 | 25.634 | 25.9476 | 25.7745 | 25.7912 | 25.6935 | 26.6899 | 26.6261 | 26.476 | 35.2186 | 35.2117 | 35.3152 | 35.4365 | 35.4057 | 35.4075 | 35.8362 | 46.5036 | 46.5029 | 46.4929 | 46.5153 | 46.5205 | 46.499 | 46.512 | 46.3901 | 51.9923 | 51.7108 | 51.8367 | 47.6455 | 47.6482 | 47.8512 | 47.0593 | 46.924 | 46.9275 | 51.8128 | 51.7996 | 51.8008 | 35.3236 | 35.3989 | 35.3147 | 35.4694 | 35.4888 | 35.4953 | 27.235 | 27.2185 | 27.0461 | 20.0976 | 19.9399 | 19.7598 | 19.3859 | 19.1078 | 35.4754 | 35.6113 | 36.4908 | 25.9448 | 25.971 | 25.9806 | 25.9244 | 26.1643 | 26.1934 | 26.1391 | 28.3622 | 28.3691 | 28.3919 | 21.5238 | 21.0804 | 21.031 | 21.2711 | 46.7685 | 46.7192 | 46.6633 | 46.6986 | 48.0429 | 47.9085 | 47.9479 | 48.3366 | 48.1923 | 47.8732 | 42.0104 | 41.9357 | 41.6765 | 41.498 | 41.4626 | 41.4657 | 41.2956 | 40.7216 | 49.7546 | 49.6874 | 49.6218 | 45.9911 | 46.13 | 45.9907 | 45.7378 | 45.787 | 45.7643 | 45.0659 | 44.4795 | 44.5951 | 25.7857 | 25.8347 | 25.8029 | 49.7447 | 49.6415 | 49.831 | 45.2423 | 45.2625 | 45.2714 | 45.7678 | 45.7297 | 46.0641 | 44.3365 | 44.3682 | 44.2137 | 25.2789 | 25.0134 | 25.2903 | 25.7531 | 26.0404 | 25.3571 | 25.1747 | 24.9169 | 24.9393 | 20.3246 | 20.1418 | 19.9338 | 20.0115 | 19.4081 | 19.1015 | 34.0851 | 34.0102 | 34.1849 | 34.2411 | 34.0642 | 34.0852 | 50.0334 | 49.9675 | 50.2045 | 45.9426 | 45.954 | 45.9178 | 45.2366 | 45.5898 | 45.7377 | 44.8807 | 44.5586 | 44.6761 | 25.1947 | 25.0091 | 24.9567 | 46.1283 | 46.2454 | 46.2602 | 46.4363 | 46.2845 | 46.2961
232 | isentropic efficiency (enthalpy only) | % | 61.8556 | 61.9254 | 61.8525 | 64.7143 | 64.7671 | 64.2465 | 66.0699 | 65.3634 | 65.136 | 63.6522 | 64.2426 | 63.7324 | 61.6373 | 61.6079 | 61.5795 | 65.6272 | 65.9488 | 66.7553 | 68.3707 | 68.9143 | 68.6905 | 67.7752 | 68.5063 | 71.0233 | 70.0747 | 69.5459 | 70.2029 | 67.9166 | 68.1732 | 67.7272 | 65.4311 | 65.2565 | 65.0003 | 66.3148 | 66.9129 | 65.9817 | 68.5533 | 67.8768 | 67.8984 | 67.0969 | 67.54 | 68.3565 | 70.8155 | 70.6628 | 70.7884 | 70.264 | 70.1318 | 69.9491 | 70.0033 | 66.2355 | 66.359 | 66.2474 | 64.2837 | 63.5755 | 64.1695 | 64.5704 | 64.6736 | 64.5932 | 64.1247 | 64.3913 | 65.5859 | 68.6076 | 68.0095 | 67.5722 | 67.4635 | 67.7837 | 67.459 | 69.252 | 69.2909 | 68.9715 | 66.5607 | 66.4665 | 66.4929 | 66.5092 | 66.8576 | 67.1177 | 68.7932 | 69.3242 | 68.1898 | 72.2199 | 72.4937 | 73.3798 | 68.4673 | 68.0611 | 67.1056 | 67.4999 | 67.368 | 67.4897 | 65.1046 | 65.3304 | 65.5744 | 68.5442 | 68.5944 | 68.344 | 67.9302 | 67.9171 | 67.8819 | 67.2374 | 65.0535 | 65.019 | 65.119 | 65.0581 | 65.0094 | 65.0338 | 64.9914 | 65.2486 | 62.7189 | 63.2162 | 62.8506 | 63.6609 | 63.4765 | 63.2056 | 63.9785 | 63.9724 | 63.7605 | 62.608 | 62.7271 | 62.7264 | 68.1637 | 68.0475 | 68.4793 | 67.9677 | 67.9573 | 67.9546 | 64.2576 | 64.6157 | 65.1156 | 69.3366 | 70.0149 | 70.5783 | 72.1668 | 72.7465 | 67.3116 | 66.9447 | 65.1675 | 67.1691 | 66.9992 | 67.0344 | 67.081 | 66.6571 | 66.4198 | 66.582 | 65.903 | 66.1081 | 65.8473 | 65.911 | 66.8923 | 66.765 | 65.6256 | 64.5905 | 64.8207 | 64.9502 | 65.0082 | 62.9249 | 63.1822 | 63.097 | 63.4959 | 63.8539 | 63.8636 | 74.5765 | 74.655 | 75.2007 | 75.5294 | 74.9208 | 74.9724 | 75.2665 | 75.9128 | 65.5937 | 65.6998 | 65.9375 | 65.4779 | 65.3064 | 65.7671 | 65.9108 | 65.8575 | 65.9504 | 66.7821 | 67.8346 | 67.4602 | 68.1708 | 67.9695 | 67.9094 | 65.4866 | 65.5533 | 65.1228 | 65.8989 | 65.8038 | 65.6853 | 66.3303 | 66.1365 | 65.6731 | 67.7966 | 67.8119 | 68.0786 | 69.4358 | 70.0685 | 68.8872 | 68.5282 | 67.511 | 69.9808 | 69.9168 | 70.3487 | 70.3306 | 68.2757 | 68.9556 | 69.2177 | 69.8412 | 71.7627 | 72.8032 | 70.3884 | 70.1243 | 69.8043 | 69.9356 | 70.3024 | 69.9195 | 65.5312 | 65.2198 | 64.5904 | 65.5516 | 65.54 | 65.5949 | 65.9567 | 65.1363 | 65.1325 | 67.6861 | 68.598 | 67.9442 | 69.8608 | 70.8862 | 70.3009 | 65.2959 | 65.2096 | 65.3125 | 65.7345 | 65.9981 | 65.8147
233
234 | Isentropic Efficiency (Power) | % | 61.4111 | 61.7623 | 61.582 | 64.6641 | 64.6006 | 64.9211 | 65.2694 | 65.6133 | 65.194 | 63.6361 | 64.4231 | 64.1463 | 61.5491 | 61.7197 | 61.9471 | 59.86 | 61.8618 | 61.3416 | 62.5057 | 62.6215 | 60.9157 | 60.6952 | 65.1917 | 61.8302 | 64.6903 | 65.1155 | 62.9483 | 67.2677 | 66.9458 | 67.607 | 64.2199 | 63.7877 | 64.1825 | 64.7732 | 64.7201 | 64.6612 | 67.7373 | 67.8369 | 66.6242 | 67.205 | 67.7909 | 67.2166 | 70.5581 | 70.2622 | 69.926 | 70.699 | 69.9475 | 69.9229 | 69.9266 | 66.6929 | 66.2455 | 66.6255 | 64.7907 | 64.5847 | 64.3871 | 65.0566 | 65.0271 | 64.9547 | 65.0573 | 65.1592 | 64.8352 | 68.2455 | 68.4819 | 68.28 | 68.0052 | 68.0163 | 68.0179 | 67.6978 | 67.1296 | 67.4337 | 64.2769 | 64.79 | 64.6389 | 64.5148 | 64.7819 | 64.5816 | 64.8289 | 62.6912 | 63.5481 | 64.4854 | 66.766 | 63.8323 | 66.2262 | 66.2018 | 66.2495 | 65.353 | 66.2768 | 65.4549 | 62.8789 | 63.5807 | 63.2646 | 67.5393 | 68.0816 | 67.7689 | 67.3796 | 67.4805 | 67.0905 | 67.8877 | 65.5454 | 65.6868 | 65.7324 | 65.6752 | 65.4273 | 65.3605 | 65.9763 | 65.5698 | 63.0184 | 62.9114 | 63.2627 | 64.5972 | 63.8014 | 63.0934 | 64.18 | 63.8159 | 64.3265 | 63.6938 | 62.5972 | 63.0685 | 67.5684 | 67.2343 | 67.2793 | 67.9423 | 68.0478 | 67.9385 | 64.6327 | 65.3214 | 65.0851 | 58.5565 | 61.1541 | 55.4787 | 60.2144 | 62.8106 | 67.3398 | 67.0743 | 67.2591 | 65.5189 | 64.8862 | 64.3094 | 64.5707 | 65.2187 | 65.3206 | 65.5777 | 65.3362 | 64.8598 | 64.9609 | 59.6856 | 60.6842 | 59.9669 | 61.6422 | 64.8064 | 64.9479 | 65.3483 | 65.3651 | 63.9927 | 63.9187 | 63.4652 | 64.0541 | 64.0755 | 64.2258 | 65.4268 | 66.1323 | 66.109 | 65.9225 | 66.0245 | 65.8749 | 66.249 | 66.069 | 66.3036 | 66.136 | 66.3422 | 66.7645 | 65.8163 | 65.6752 | 66.1068 | 66.1963 | 66.2645 | 67.6535 | 67.7196 | 67.7889 | 67.4433 | 67.658 | 67.7433 | 65.7037 | 65.4983 | 65.9415 | 66.124 | 65.7743 | 65.958 | 66.2172 | 65.9749 | 66.9186 | 67.7711 | 67.9601 | 67.8282 | 68.0769 | 68.0322 | 68.6973 | 67.2685 | 67.5002 | 66.8904 | 67.1856 | 66.4949 | 66.8674 | 58.0335 | 58.1753 | 61.328 | 63.8076 | 60.8821 | 62.6554 | 70.7206 | 70.1362 | 70.6948 | 69.0803 | 69.8664 | 69.4416 | 65.7471 | 66.4728 | 65.8451 | 65.7453 | 66.2876 | 66.5094 | 65.821 | 65.8619 | 65.5362 | 68.2642 | 68.4597 | 68.4399 | 67.5886 | 67.1082 | 67.6746 | 65.6951 | 64.8661 | 65.8374 | 65.5404 | 65.5978 | 66.1869
235 | Table Isentropic | % | 70.9715 | 70.9874 | 70.9915 | 73.1496 | 73.1598 | 73.1574 | 73.9382 | 73.9337 | 73.933 | 73.3924 | 73.394 | 73.3863 | 71.636 | 71.6357 | 71.6335 | 58.1451 | 58.1868 | 58.2633 | 58.2739 | 58.1238 | 57.9798 | 58.2925 | 58.2718 | 58.1765 | 58.336 | 58.1145 | 58.0839 | 64.8895 | 64.92 | 64.8919 | 64.8754 | 64.8757 | 64.9386 | 65.0453 | 65.0777 | 64.973 | 64.9007 | 64.9558 | 64.9592 | 64.8516 | 65.1113 | 65.0005 | 71.9632 | 71.9099 | 71.9718 | 71.8966 | 72.0116 | 71.951 | 71.9147 | 73.9384 | 73.9391 | 73.9388 | 73.7086 | 73.7233 | 73.7249 | 73.9382 | 73.9388 | 73.9382 | 73.9318 | 73.9289 | 73.9319 | 71.9638 | 71.9693 | 71.9987 | 71.8898 | 71.9467 | 71.9322 | 65.0915 | 65.1068 | 65.0525 | 64.9833 | 64.9496 | 64.9667 | 64.9547 | 65.0095 | 64.9093 | 58.2609 | 58.3039 | 58.1843 | 58.086 | 58.1937 | 58.115 | 64.9483 | 64.9666 | 64.9287 | 64.9762 | 64.9446 | 64.8979 | 64.937 | 64.9777 | 64.9399 | 71.9632 | 71.978 | 71.979 | 71.9594 | 71.9608 | 71.9698 | 71.9498 | 73.939 | 73.9388 | 73.9393 | 73.939 | 73.9387 | 73.9386 | 73.938 | 73.9377 | 73.7365 | 73.7354 | 73.7299 | 73.9396 | 73.9386 | 73.9386 | 73.9317 | 73.9293 | 73.9265 | 73.7366 | 73.7299 | 73.7342 | 71.9358 | 71.9533 | 72.01 | 71.9339 | 71.937 | 71.9374 | 64.8541 | 64.9342 | 64.9126 | 58.2078 | 58.2588 | 58.2378 | 58.4207 | 58.2262 | 71.9407 | 71.9267 | 71.9308 | 64.9229 | 64.897 | 64.9369 | 64.9589 | 64.9605 | 64.8925 | 64.8883 | 66.6005 | 66.6751 | 66.5992 | 58.8587 | 58.5627 | 58.4215 | 58.2832 | 73.9393 | 73.9397 | 73.9395 | 73.9397 | 73.9398 | 73.9384 | 73.9373 | 73.9316 | 73.9319 | 73.9276 | 73.9379 | 73.9377 | 73.9381 | 73.9382 | 73.9312 | 73.9326 | 73.9323 | 73.9258 | 73.7344 | 73.7409 | 73.7282 | 73.9387 | 73.9382 | 73.9382 | 73.9311 | 73.9298 | 73.9296 | 73.9393 | 73.9387 | 73.9389 | 65.0692 | 65.0633 | 64.9702 | 73.7226 | 73.723 | 73.7316 | 73.9304 | 73.9306 | 73.9311 | 73.9393 | 73.9386 | 73.9384 | 73.9384 | 73.9383 | 73.9384 | 65.1428 | 65.1104 | 64.9787 | 65.0812 | 64.9436 | 65.0846 | 64.8963 | 64.8415 | 64.9104 | 58.169 | 58.1689 | 57.9603 | 58.3446 | 58.2853 | 58.2501 | 71.992 | 71.9054 | 71.9163 | 71.9031 | 71.9196 | 71.8795 | 73.7202 | 73.7219 | 73.7087 | 73.9394 | 73.9397 | 73.9396 | 73.9333 | 73.9294 | 73.9326 | 73.9395 | 73.9393 | 73.9382 | 64.9362 | 65.1571 | 64.9056 | 73.9316 | 73.933 | 73.9337 | 73.9397 | 73.9399 | 73.94
236 | % of table isentropic | % | 86.5294 | 87.0046 | 86.7457 | 88.3997 | 88.3007 | 88.7417 | 88.2757 | 88.7461 | 88.1799 | 86.7067 | 87.7771 | 87.4091 | 85.9192 | 86.1578 | 86.4779 | 102.9494 | 106.3159 | 105.2834 | 107.2618 | 107.7381 | 105.0637 | 104.1219 | 111.8752 | 106.2804 | 110.8926 | 112.0469 | 108.3749 | 103.665 | 103.1204 | 104.1841 | 98.9896 | 98.323 | 98.8358 | 99.5818 | 99.4505 | 99.5201 | 104.3707 | 104.4355 | 102.5631 | 103.6289 | 104.1154 | 103.4094 | 98.0475 | 97.7086 | 97.1576 | 98.3342 | 97.1336 | 97.1812 | 97.2355 | 90.2006 | 89.5947 | 90.109 | 87.9012 | 87.6042 | 87.3343 | 87.9878 | 87.9473 | 87.8499 | 87.9964 | 88.1377 | 87.6958 | 94.8331 | 95.1543 | 94.8349 | 94.5965 | 94.5371 | 94.5584 | 104.004 | 103.1069 | 103.6605 | 98.9129 | 99.7542 | 99.4953 | 99.3227 | 99.6498 | 99.4951 | 111.2733 | 107.5249 | 109.2186 | 111.0172 | 114.7307 | 109.8381 | 101.9676 | 101.9013 | 102.0343 | 100.5799 | 102.0513 | 100.8583 | 96.8306 | 97.8501 | 97.4203 | 93.8525 | 94.5866 | 94.151 | 93.6356 | 93.7739 | 93.2204 | 94.3542 | 88.6479 | 88.8393 | 88.9005 | 88.8234 | 88.4885 | 88.3984 | 89.2319 | 88.6824 | 85.4644 | 85.3205 | 85.8034 | 87.3648 | 86.2898 | 85.3321 | 86.8099 | 86.3201 | 87.0141 | 86.3802 | 84.9006 | 85.5349 | 93.9288 | 93.4417 | 93.4304 | 94.4511 | 94.5935 | 94.4411 | 99.6586 | 100.5963 | 100.2659 | 100.5991 | 104.9696 | 95.2623 | 103.0702 | 107.8735 | 93.6047 | 93.2537 | 93.5053 | 100.9181 | 99.9834 | 99.0336 | 99.4024 | 100.3975 | 100.6596 | 101.0625 | 98.1016 | 97.2773 | 97.5402 | 101.4048 | 103.6226 | 102.6454 | 105.7633 | 87.6481 | 87.8391 | 88.3808 | 88.4032 | 86.547 | 86.4485 | 85.8366 | 86.6397 | 86.6682 | 86.8766 | 88.4889 | 89.4433 | 89.4113 | 89.1589 | 89.3053 | 89.1013 | 89.6077 | 89.3721 | 89.9222 | 89.687 | 89.9821 | 90.2971 | 89.0153 | 88.8244 | 89.4168 | 89.5394 | 89.632 | 91.4987 | 91.5889 | 91.6822 | 103.6487 | 103.988 | 104.2683 | 89.1229 | 88.8438 | 89.4345 | 89.4409 | 88.9676 | 89.2154 | 89.5562 | 89.2293 | 90.5059 | 91.6588 | 91.9146 | 91.736 | 104.5041 | 104.4873 | 105.7227 | 103.3609 | 103.9366 | 102.7745 | 103.5276 | 102.5499 | 103.0151 | 99.7671 | 100.011 | 105.8104 | 109.3634 | 104.4553 | 107.5626 | 98.2339 | 97.5396 | 98.3015 | 96.0741 | 97.1452 | 96.6083 | 89.1847 | 90.1669 | 89.3316 | 88.9178 | 89.6509 | 89.951 | 89.0275 | 89.0875 | 88.6431 | 92.3243 | 92.589 | 92.5636 | 104.0846 | 102.9945 | 104.2663 | 88.8593 | 87.7363 | 89.0492 | 88.6404 | 88.7178 | 89.5144
237 | Corrected IE% from N4 Powermeter Kw | % | 0.063134 | 0.063269 | 0.063266 | 0.066163 | 0.066206 | 0.066096 | 0.066862 | 0.067057 | 0.067024 | 0.065898 | 0.066007 | 0.065733 | 0.063568 | 0.063537 | 0.063475 | 0.068291 | 0.068421 | 0.069312 | 0.070394 | 0.070266 | 0.069139 | 0.069599 | 0.072002 | 0.070076 | 0.070749 | 0.072413 | 0.071912 | 0.07313 | 0.073259 | 0.073205 | 0.0699 | 0.069804 | 0.069693 | 0.070115 | 0.070005 | 0.070369 | 0.07367 | 0.073375 | 0.073271 | 0.073355 | 0.073189 | 0.073141 | 0.074407 | 0.074252 | 0.074292 | 0.074437 | 0.073789 | 0.07351 | 0.073576 | 0.068576 | 0.06876 | 0.068663 | 0.066229 | 0.06625 | 0.066356 | 0.066683 | 0.066709 | 0.066544 | 0.066512 | 0.066821 | 0.066908 | 0.072299 | 0.07224 | 0.072319 | 0.071308 | 0.071505 | 0.07145 | 0.073186 | 0.07317 | 0.073087 | 0.069843 | 0.069802 | 0.070258 | 0.070246 | 0.070216 | 0.07015 | 0.072495 | 0.07259 | 0.072793 | 0.073548 | 0.073534 | 0.074597 | 0.071999 | 0.071954 | 0.07216 | 0.071701 | 0.071756 | 0.071767 | 0.068397 | 0.068734 | 0.068471 | 0.071559 | 0.071575 | 0.071547 | 0.071003 | 0.07085 | 0.070786 | 0.071224 | 0.067768 | 0.067918 | 0.067934 | 0.067891 | 0.067702 | 0.06774 | 0.067898 | 0.067872 | 0.065103 | 0.065217 | 0.065294 | 0.065743 | 0.065802 | 0.065657 | 0.065918 | 0.065894 | 0.065827 | 0.064756 | 0.064801 | 0.064802 | 0.071231 | 0.071018 | 0.071122 | 0.071533 | 0.071768 | 0.071653 | 0.070629 | 0.070673 | 0.070655 | 0.066337 | 0.067699 | 0.062936 | 0.069006 | 0.069563 | 0.070541 | 0.070488 | 0.070627 | 0.070638 | 0.070449 | 0.070848 | 0.070708 | 0.070921 | 0.071182 | 0.070999 | 0.070354 | 0.070617 | 0.070611 | 0.067869 | 0.069695 | 0.068099 | 0.070198 | 0.067187 | 0.067225 | 0.067335 | 0.067298 | 0.065411 | 0.06547 | 0.06532 | 0.065707 | 0.065873 | 0.065897 | 0.067779 | 0.067866 | 0.067946 | 0.06798 | 0.067877 | 0.067924 | 0.067966 | 0.067955 | 0.067958 | 0.06781 | 0.068092 | 0.067894 | 0.067806 | 0.067905 | 0.068253 | 0.068223 | 0.068277 | 0.069653 | 0.069859 | 0.069951 | 0.072989 | 0.07303 | 0.073175 | 0.067655 | 0.067585 | 0.067624 | 0.068015 | 0.067714 | 0.067766 | 0.068376 | 0.0681 | 0.068515 | 0.070173 | 0.070162 | 0.070119 | 0.074234 | 0.074388 | 0.07468 | 0.072901 | 0.073041 | 0.073081 | 0.073231 | 0.073059 | 0.07314 | 0.066853 | 0.067362 | 0.070706 | 0.072064 | 0.070742 | 0.071391 | 0.074095 | 0.074168 | 0.074309 | 0.073164 | 0.07331 | 0.073268 | 0.067658 | 0.067701 | 0.067412 | 0.067673 | 0.06783 | 0.067884 | 0.067747 | 0.06771 | 0.067778 | 0.070331 | 0.07085 | 0.070342 | 0.073287 | 0.072941 | 0.073404 | 0.067522 | 0.067571 | 0.067527 | 0.067736 | 0.067784 | 0.067757
238
239 | Table volumetric efficiency | % | 97.7041 | 97.6996 | 97.6985 | 96.789 | 96.7818 | 96.7835 | 95.5633 | 95.6237 | 95.6313 | 94.0525 | 94.0549 | 94.0434 | 92.0451 | 92.0448 | 92.0426 | 99.2858 | 99.2831 | 99.2783 | 99.2776 | 99.2871 | 99.2962 | 99.2764 | 99.2777 | 99.2838 | 99.2736 | 99.2877 | 99.2897 | 98.7283 | 98.7249 | 98.728 | 98.7298 | 98.7298 | 98.7229 | 98.7111 | 98.7075 | 98.7191 | 98.727 | 98.721 | 98.7206 | 98.7324 | 98.7037 | 98.7161 | 97.3845 | 97.4044 | 97.3813 | 97.4093 | 97.3661 | 97.3891 | 97.4026 | 95.5579 | 95.5429 | 95.5495 | 94.6006 | 94.6319 | 94.6353 | 95.5624 | 95.5504 | 95.5616 | 95.6426 | 95.6668 | 95.641 | 97.3843 | 97.3822 | 97.371 | 97.4118 | 97.3907 | 97.3961 | 98.7059 | 98.7042 | 98.7103 | 98.718 | 98.7217 | 98.7198 | 98.7211 | 98.7151 | 98.7261 | 99.2784 | 99.2756 | 99.2833 | 99.2895 | 99.2827 | 99.2877 | 98.7218 | 98.7198 | 98.724 | 98.7187 | 98.7222 | 98.7273 | 98.7231 | 98.7186 | 98.7227 | 97.3845 | 97.3789 | 97.3785 | 97.3859 | 97.3854 | 97.382 | 97.3895 | 95.5445 | 95.5485 | 95.5354 | 95.5442 | 95.551 | 95.5544 | 95.5665 | 95.5716 | 94.6607 | 94.6583 | 94.6462 | 95.5253 | 95.5545 | 95.5543 | 95.6436 | 95.6633 | 95.6841 | 94.661 | 94.6463 | 94.6557 | 97.3948 | 97.3882 | 97.3667 | 97.3955 | 97.3943 | 97.3942 | 98.7321 | 98.7234 | 98.7257 | 99.2818 | 99.2785 | 99.2799 | 99.2681 | 99.2806 | 97.393 | 97.3981 | 97.3966 | 98.7246 | 98.7274 | 98.7231 | 98.7206 | 98.7205 | 98.7279 | 98.7284 | 98.5229 | 98.513 | 98.5231 | 99.2394 | 99.2589 | 99.2681 | 99.277 | 95.5342 | 95.5222 | 95.53 | 95.5204 | 95.5144 | 95.5576 | 95.5784 | 95.6442 | 95.6412 | 95.6764 | 95.5686 | 95.5725 | 95.5641 | 95.5617 | 95.6474 | 95.6348 | 95.638 | 95.6893 | 94.6561 | 94.6705 | 94.6427 | 95.5513 | 95.5624 | 95.5618 | 95.6484 | 95.6593 | 95.6612 | 95.5341 | 95.5519 | 95.5466 | 98.7084 | 98.7091 | 98.7194 | 94.6304 | 94.6313 | 94.6501 | 95.6545 | 95.6526 | 95.6484 | 95.5366 | 95.554 | 95.5584 | 95.5578 | 95.5606 | 95.5575 | 98.7002 | 98.7038 | 98.7185 | 98.7071 | 98.7223 | 98.7067 | 98.7275 | 98.7335 | 98.726 | 99.2843 | 99.2843 | 99.2975 | 99.273 | 99.2768 | 99.2791 | 97.3736 | 97.4061 | 97.402 | 97.4069 | 97.4008 | 97.4155 | 94.6253 | 94.629 | 94.601 | 95.5309 | 95.5205 | 95.5246 | 95.628 | 95.6625 | 95.6349 | 95.5275 | 95.5346 | 95.5628 | 98.7231 | 98.6986 | 98.7265 | 95.6442 | 95.6308 | 95.6242 | 95.5217 | 95.5099 | 95.4912
240 | Actual Volume Flow rate | m^3/hr | 1269.2262 | 1270.1668 | 1271.0489 | 1266.9549 | 1267.7245 | 1266.2762 | 1253.3469 | 1258.3691 | 1259.0184 | 1243.0235 | 1243.6522 | 1241.5106 | 1229.413 | 1229.854 | 1229.3759 | 170.6896 | 171.2756 | 173.4237 | 185.812 | 185.4773 | 182.2669 | 174.3227 | 180.2283 | 175.4278 | 186.6613 | 191.2738 | 189.7521 | 410.1436 | 410.6347 | 410.4212 | 409.9442 | 409.7748 | 408.6861 | 443.8636 | 442.7745 | 445.4861 | 447.0821 | 444.9715 | 443.4629 | 466.5054 | 466.4149 | 465.2552 | 731.6012 | 730.4765 | 730.5778 | 744.0632 | 791.6681 | 789.5806 | 790.3409 | 1155.6677 | 1157.7121 | 1156.5209 | 1245.5569 | 1245.8538 | 1245.03 | 1253.5526 | 1252.2192 | 1250.7346 | 1252.4294 | 1255.9232 | 1255.5561 | 731.8961 | 731.6168 | 731.7942 | 780.5865 | 782.1289 | 781.4163 | 465.9316 | 465.4707 | 465.061 | 407.198 | 407.0781 | 409.7502 | 409.4813 | 408.6627 | 409.1473 | 180.8857 | 180.8563 | 181.5073 | 193.9535 | 194.328 | 197.2309 | 407.2085 | 406.9548 | 408.074 | 437.8414 | 438.4573 | 438.477 | 437.2093 | 438.9258 | 437.6932 | 740.1854 | 739.7968 | 740.1364 | 779.2445 | 777.5309 | 776.7166 | 770.6592 | 1139.634 | 1141.4914 | 1142.1496 | 1141.2389 | 1139.0023 | 1138.3073 | 1141.7443 | 1140.959 | 1220.5253 | 1222.6087 | 1224.0078 | 1229.1848 | 1229.9968 | 1227.4021 | 1232.9103 | 1232.0966 | 1230.3022 | 1200.3594 | 1201.217 | 1201.2489 | 704.3695 | 702.4048 | 703.1388 | 718.9594 | 721.8457 | 719.985 | 394.8397 | 395.1843 | 394.316 | 164.3678 | 167.7678 | 156.0763 | 180.3324 | 181.8162 | 764.8714 | 763.9256 | 765.452 | 427.8803 | 427.0823 | 428.5392 | 428.09 | 451.9369 | 453.7461 | 452.6066 | 451.5341 | 452.9695 | 452.8054 | 176.9893 | 181.6006 | 177.4138 | 182.9027 | 1117.3446 | 1117.5182 | 1118.7084 | 1118.6845 | 1211.8179 | 1211.2473 | 1209.0505 | 1212.2486 | 1215.2424 | 1215.0122 | 1249.0351 | 1250.7126 | 1253.1355 | 1253.2126 | 1252.0274 | 1251.963 | 1252.9447 | 1254.3633 | 1256.8805 | 1255.3162 | 1258.7729 | 1262.2168 | 1261.3269 | 1261.9601 | 1265.7133 | 1266.0111 | 1266.2992 | 1162.7893 | 1163.9088 | 1165.2976 | 462.7573 | 463.0279 | 464.2643 | 1252.3665 | 1250.9616 | 1251.5064 | 1263.03 | 1258.0375 | 1259.3944 | 1265.5632 | 1261.9628 | 1269.3495 | 1164.6671 | 1164.425 | 1165.44 | 464.4651 | 464.9623 | 466.8919 | 437.5039 | 437.814 | 437.8271 | 406.7138 | 405.7478 | 406.3865 | 166.0037 | 167.2912 | 176.1108 | 189.6091 | 185.4768 | 187.0722 | 746.2678 | 747.1896 | 747.602 | 792.4345 | 793.596 | 793.3262 | 1243.2446 | 1245.3293 | 1242.2904 | 1247.5352 | 1250.4209 | 1251.6936 | 1250.9299 | 1250.6975 | 1250.6288 | 1158.9234 | 1165.8114 | 1159.4545 | 461.1849 | 459.5543 | 461.1948 | 1256.2799 | 1257.0348 | 1256.4184 | 1257.9322 | 1258.709 | 1259.3412
241 | Volumetric efficiency | % | 96.7046 | 96.7843 | 96.8354 | 96.5316 | 96.5982 | 96.4799 | 95.5027 | 95.8854 | 95.9349 | 94.724 | 94.764 | 94.5929 | 93.679 | 93.6814 | 93.6762 | 82.1187 | 82.4309 | 83.4384 | 84.9342 | 84.8024 | 83.2887 | 83.8886 | 86.7534 | 84.4116 | 85.3181 | 87.4439 | 86.7525 | 93.7636 | 93.8641 | 93.8106 | 93.6922 | 93.6699 | 93.414 | 94.3748 | 94.1389 | 94.7286 | 95.068 | 94.6192 | 94.2962 | 94.7958 | 94.769 | 94.5375 | 96.9633 | 96.7876 | 96.8123 | 97.1977 | 96.5204 | 96.2607 | 96.347 | 96.0652 | 96.2351 | 96.1448 | 94.917 | 94.9238 | 94.8769 | 95.5184 | 95.4168 | 95.3036 | 95.4328 | 95.707 | 95.671 | 95.6138 | 95.5759 | 95.5841 | 95.1706 | 95.3599 | 95.2629 | 94.6687 | 94.5708 | 94.5086 | 93.0692 | 93.0628 | 93.6619 | 93.6028 | 93.404 | 93.5311 | 87.0653 | 87.0511 | 87.3277 | 88.7089 | 88.8757 | 90.1312 | 93.0763 | 93.0323 | 93.2858 | 93.1204 | 93.2297 | 93.2317 | 92.9557 | 93.3423 | 93.078 | 95.3279 | 95.2846 | 95.3216 | 95.0044 | 94.7955 | 94.6975 | 95.2262 | 94.7324 | 94.8868 | 94.9415 | 94.8658 | 94.6885 | 94.6221 | 94.9078 | 94.8339 | 93.0018 | 93.1605 | 93.2593 | 93.6538 | 93.7235 | 93.5102 | 93.9455 | 93.8835 | 93.7546 | 91.4575 | 91.5305 | 91.5329 | 93.3393 | 93.1032 | 93.1911 | 93.9157 | 94.3062 | 94.0483 | 90.2491 | 90.3324 | 90.1362 | 79.1147 | 80.7385 | 75.1317 | 82.4048 | 83.1243 | 93.2508 | 93.1331 | 93.3341 | 90.9786 | 90.8152 | 91.1208 | 91.0485 | 91.8273 | 92.201 | 91.9572 | 91.7495 | 92.0616 | 92.018 | 80.8852 | 83.0009 | 81.1238 | 83.6378 | 92.8795 | 92.894 | 92.976 | 92.974 | 92.3383 | 92.2948 | 92.1274 | 92.3788 | 92.5992 | 92.5817 | 95.1821 | 95.294 | 95.5025 | 95.5004 | 95.4101 | 95.3973 | 95.4721 | 95.5802 | 95.772 | 95.6607 | 95.9082 | 96.1706 | 96.1108 | 96.159 | 96.437 | 96.4757 | 96.4977 | 96.6747 | 96.7502 | 96.8656 | 94.0195 | 94.0829 | 94.3488 | 95.436 | 95.313 | 95.3545 | 96.2325 | 95.8601 | 95.9635 | 96.4336 | 96.1592 | 96.7221 | 96.8044 | 96.7931 | 96.8775 | 94.3812 | 94.4654 | 94.8659 | 93.0313 | 93.0994 | 93.1 | 92.9725 | 92.7447 | 92.9139 | 79.9064 | 80.5134 | 84.7357 | 86.7045 | 84.8064 | 85.4846 | 96.1085 | 96.2286 | 96.2804 | 95.3313 | 95.4848 | 95.4423 | 94.7408 | 94.8839 | 94.6602 | 95.0519 | 95.2797 | 95.3688 | 95.3185 | 95.3008 | 95.3035 | 96.327 | 96.8995 | 96.3799 | 93.7126 | 93.375 | 93.7167 | 95.7342 | 95.7837 | 95.7527 | 95.8601 | 95.9113 | 95.9675
242 | Volumetric as % of table | % | 98.9771 | 99.0632 | 99.1166 | 99.734 | 99.8103 | 99.6862 | 99.9365 | 100.2737 | 100.3174 | 100.714 | 100.7539 | 100.5844 | 101.775 | 101.7781 | 101.7747 | 82.7094 | 83.0261 | 84.045 | 85.5522 | 85.4113 | 83.879 | 84.5001 | 87.3846 | 85.0205 | 85.9424 | 88.0712 | 87.3732 | 94.9714 | 95.0764 | 95.0193 | 94.8976 | 94.875 | 94.6225 | 95.6071 | 95.3716 | 95.9577 | 96.2938 | 95.8451 | 95.5183 | 96.0129 | 96.0136 | 95.7671 | 99.5675 | 99.3668 | 99.4157 | 99.7828 | 99.1314 | 98.8414 | 98.9163 | 100.5308 | 100.7244 | 100.623 | 100.3345 | 100.3085 | 100.2553 | 99.9539 | 99.8601 | 99.73 | 99.7806 | 100.042 | 100.0314 | 98.1819 | 98.1452 | 98.1648 | 97.6993 | 97.9148 | 97.8097 | 95.9098 | 95.8123 | 95.7434 | 94.2779 | 94.2678 | 94.8765 | 94.8154 | 94.6198 | 94.738 | 87.6981 | 87.6863 | 87.9581 | 89.3436 | 89.5178 | 90.7778 | 94.2814 | 94.2387 | 94.4915 | 94.329 | 94.4364 | 94.4335 | 94.158 | 94.5539 | 94.2823 | 97.8882 | 97.8493 | 97.8877 | 97.5546 | 97.3406 | 97.2433 | 97.7786 | 99.1499 | 99.3074 | 99.3783 | 99.2899 | 99.0973 | 99.0243 | 99.3107 | 99.2281 | 98.2475 | 98.4177 | 98.5347 | 98.0408 | 98.0838 | 97.8608 | 98.2245 | 98.1394 | 97.9834 | 96.6159 | 96.708 | 96.7009 | 95.836 | 95.6001 | 95.7114 | 96.4271 | 96.8293 | 96.5646 | 91.4081 | 91.5005 | 91.2996 | 79.6871 | 81.3252 | 75.6767 | 83.0123 | 83.7266 | 95.747 | 95.621 | 95.8288 | 92.1539 | 91.9858 | 92.2994 | 92.2285 | 93.0174 | 93.389 | 93.1416 | 93.125 | 93.4512 | 93.3974 | 81.5051 | 83.6206 | 81.7219 | 84.2469 | 97.2212 | 97.2486 | 97.3265 | 97.3342 | 96.6747 | 96.5855 | 96.3893 | 96.5859 | 96.8193 | 96.7655 | 99.5955 | 99.7087 | 99.9355 | 99.9358 | 99.7519 | 99.7516 | 99.8264 | 99.8859 | 101.1789 | 101.046 | 101.3371 | 100.6481 | 100.5738 | 100.6249 | 100.8245 | 100.8534 | 100.8744 | 101.1939 | 101.2541 | 101.3805 | 95.2497 | 95.3133 | 95.5727 | 100.8513 | 100.7204 | 100.7442 | 100.6042 | 100.2169 | 100.3295 | 100.9389 | 100.6333 | 101.2178 | 101.3045 | 101.2897 | 101.3813 | 95.6241 | 95.706 | 96.0974 | 94.2498 | 94.3043 | 94.3198 | 94.1708 | 93.9344 | 94.113 | 80.4824 | 81.0938 | 85.3352 | 87.3394 | 85.4241 | 86.1053 | 98.7008 | 98.7912 | 98.8484 | 97.8691 | 98.0329 | 97.9744 | 100.1221 | 100.2693 | 100.0626 | 99.4986 | 99.7479 | 99.8368 | 99.6764 | 99.6219 | 99.6535 | 100.837 | 101.4287 | 100.8551 | 94.9246 | 94.6062 | 94.9255 | 100.094 | 100.1599 | 100.1344 | 100.3543 | 100.4203 | 100.4988
243 | Corrected Volumetric Effciency for Hz | % | 96.7046 | 96.7843 | 96.8354 | 96.5316 | 96.5982 | 96.4799 | 95.5027 | 95.8854 | 95.9349 | 94.724 | 94.764 | 94.5929 | 93.679 | 93.6814 | 93.6762 | 82.1187 | 82.4309 | 83.4384 | 84.9342 | 84.8024 | 83.2887 | 83.8886 | 86.7534 | 84.4116 | 85.3181 | 87.4439 | 86.7525 | 93.7636 | 93.8641 | 93.8106 | 93.6922 | 93.6699 | 93.414 | 94.3748 | 94.1389 | 94.7286 | 95.068 | 94.6192 | 94.2962 | 94.7958 | 94.769 | 94.5375 | 96.9633 | 96.7876 | 96.8123 | 97.1977 | 96.5204 | 96.2607 | 96.347 | 96.0652 | 96.2351 | 96.1448 | 94.917 | 94.9238 | 94.8769 | 95.5184 | 95.4168 | 95.3036 | 95.4328 | 95.707 | 95.671 | 95.6138 | 95.5759 | 95.5841 | 95.1706 | 95.3599 | 95.2629 | 94.6687 | 94.5708 | 94.5086 | 93.0692 | 93.0628 | 93.6619 | 93.6028 | 93.404 | 93.5311 | 87.0653 | 87.0511 | 87.3277 | 88.7089 | 88.8757 | 90.1312 | 93.0763 | 93.0323 | 93.2858 | 93.1204 | 93.2297 | 93.2317 | 92.9557 | 93.3423 | 93.078 | 95.3279 | 95.2846 | 95.3216 | 95.0044 | 94.7955 | 94.6975 | 95.2262 | 94.7324 | 94.8868 | 94.9415 | 94.8658 | 94.6885 | 94.6221 | 94.9078 | 94.8339 | 93.0018 | 93.1605 | 93.2593 | 93.6538 | 93.7235 | 93.5102 | 93.9455 | 93.8835 | 93.7546 | 91.4575 | 91.5305 | 91.5329 | 93.3393 | 93.1032 | 93.1911 | 93.9157 | 94.3062 | 94.0483 | 90.2491 | 90.3324 | 90.1362 | 79.1147 | 80.7385 | 75.1317 | 82.4048 | 83.1243 | 93.2508 | 93.1331 | 93.3341 | 90.9786 | 90.8152 | 91.1208 | 91.0485 | 91.8273 | 92.201 | 91.9572 | 91.7495 | 92.0616 | 92.018 | 80.8852 | 83.0009 | 81.1238 | 83.6378 | 92.8795 | 92.894 | 92.976 | 92.974 | 92.3383 | 92.2948 | 92.1274 | 92.3788 | 92.5992 | 92.5817 | 95.1821 | 95.294 | 95.5025 | 95.5004 | 95.4101 | 95.3973 | 95.4721 | 95.5802 | 95.772 | 95.6607 | 95.9082 | 96.1706 | 96.1108 | 96.159 | 96.437 | 96.4757 | 96.4977 | 96.6747 | 96.7502 | 96.8656 | 94.0195 | 94.0829 | 94.3488 | 95.436 | 95.313 | 95.3545 | 96.2325 | 95.8601 | 95.9635 | 96.4336 | 96.1592 | 96.7221 | 96.8044 | 96.7931 | 96.8775 | 94.3812 | 94.4654 | 94.8659 | 93.0313 | 93.0994 | 93.1 | 92.9725 | 92.7447 | 92.9139 | 79.9064 | 80.5134 | 84.7357 | 86.7045 | 84.8064 | 85.4846 | 96.1085 | 96.2286 | 96.2804 | 95.3313 | 95.4848 | 95.4423 | 94.7408 | 94.8839 | 94.6602 | 95.0519 | 95.2797 | 95.3688 | 95.3185 | 95.3008 | 95.3035 | 96.327 | 96.8995 | 96.3799 | 93.7126 | 93.375 | 93.7167 | 95.7342 | 95.7837 | 95.7527 | 95.8601 | 95.9113 | 95.9675
244
245 | Assumed Subcooling | ºC | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
246 | Enthalpy liquid at DG with assumed subcooling | KJ/kg | 266.4581 | 266.5036 | 266.3098 | 266.4622 | 266.5354 | 266.485 | 266.6023 | 266.4473 | 266.3251 | 266.557 | 266.5984 | 266.6047 | 266.4876 | 266.3951 | 266.3298 | 231.7058 | 231.7073 | 231.7305 | 231.8618 | 231.7682 | 231.5691 | 231.7171 | 231.7126 | 231.7376 | 231.841 | 231.6776 | 231.6306 | 239.0571 | 239.0861 | 239.1295 | 239.2163 | 239.2111 | 239.2688 | 239.1842 | 239.3981 | 239.274 | 239.065 | 239.2626 | 239.2912 | 239.1946 | 239.397 | 239.3634 | 252.0527 | 251.8473 | 251.9871 | 251.8215 | 252.2036 | 252.1383 | 251.9373 | 264.7467 | 264.7678 | 264.8873 | 266.685 | 266.4865 | 266.5093 | 264.7792 | 264.7914 | 264.7339 | 263.9139 | 263.8044 | 264.0887 | 252.0422 | 251.9148 | 252.0478 | 251.8329 | 251.9357 | 251.7998 | 239.2891 | 239.4555 | 239.2999 | 239.0914 | 239.3245 | 239.3472 | 239.3827 | 239.3105 | 239.1496 | 231.8877 | 231.8953 | 231.6046 | 231.6265 | 231.8114 | 231.641 | 239.2111 | 239.3586 | 239.2346 | 239.1268 | 239.1056 | 239.1611 | 239.2058 | 239.2183 | 239.298 | 252.1155 | 252.0477 | 251.9471 | 251.9143 | 251.9926 | 251.9118 | 251.9441 | 264.8845 | 264.9003 | 264.9233 | 264.8918 | 264.8869 | 264.8904 | 264.8538 | 264.8504 | 266.5088 | 266.3956 | 266.3729 | 265.0332 | 264.859 | 264.8177 | 264.1219 | 263.9299 | 263.8169 | 266.3907 | 266.5134 | 266.3965 | 251.9414 | 251.9302 | 252.0902 | 251.9328 | 251.8857 | 251.8434 | 239.1209 | 239.2602 | 239.219 | 231.6193 | 231.6872 | 231.8677 | 232.0939 | 231.7178 | 251.8739 | 251.8212 | 251.9229 | 239.1392 | 239.1651 | 239.1976 | 239.3468 | 239.2337 | 239.18 | 239.1584 | 239.0729 | 239.0687 | 239.1208 | 232.1009 | 232.1856 | 232.0082 | 231.8833 | 264.5737 | 264.847 | 264.9228 | 264.822 | 264.9099 | 264.8559 | 264.7938 | 263.996 | 264.0262 | 264.0702 | 264.7994 | 264.9021 | 264.7277 | 264.735 | 264.1963 | 264.3675 | 264.218 | 263.8884 | 266.4344 | 266.4134 | 266.4741 | 264.9237 | 264.6419 | 264.7358 | 263.9698 | 263.8007 | 263.8812 | 265.0476 | 264.6822 | 264.8445 | 239.4465 | 239.4556 | 239.0955 | 266.6086 | 266.6266 | 266.5589 | 264.1601 | 264.0107 | 263.9636 | 264.7867 | 264.825 | 264.8411 | 264.7594 | 264.6516 | 264.6065 | 239.3824 | 239.4894 | 239.1308 | 239.4455 | 239.2236 | 239.3825 | 239.2031 | 239.0452 | 239.1397 | 231.727 | 231.7301 | 231.6986 | 231.8548 | 231.7821 | 231.7064 | 251.9908 | 251.7718 | 251.748 | 251.8625 | 251.9094 | 251.7448 | 266.6727 | 266.4978 | 266.6342 | 265.0459 | 265.0479 | 264.8558 | 264.1833 | 263.8761 | 264.0154 | 265.1981 | 264.9413 | 264.7795 | 239.0995 | 239.4414 | 239.1526 | 264.0813 | 264.0991 | 264.0502 | 264.975 | 265.1912 | 265.2487
247 | Suction enthalpy | KJ/kg | 416.6953 | 416.6126 | 416.4678 | 414.8768 | 414.4376 | 413.1479 | 411.8455 | 411.167 | 410.6484 | 407.6077 | 407.9697 | 407.2851 | 406.4045 | 406.2886 | 406.1686 | 412.9525 | 413.0565 | 413.3009 | 413.134 | 413.1282 | 413.1008 | 412.8327 | 413.0883 | 413.2572 | 413.1772 | 413.1655 | 413.1833 | 411.3944 | 411.6075 | 411.6363 | 411.5069 | 411.3985 | 411.1866 | 412.2769 | 412.0848 | 411.9116 | 410.576 | 410.3161 | 410.3404 | 410.4824 | 410.7288 | 411.1744 | 410.3837 | 410.4053 | 410.1546 | 409.943 | 410.3191 | 410.2395 | 410.1324 | 409.3784 | 409.3189 | 409.0721 | 408.6197 | 407.8941 | 409.0457 | 409.5047 | 409.5076 | 409.5845 | 409.6371 | 410.8605 | 411.6019 | 410.5988 | 410.834 | 410.7913 | 412.6953 | 412.6765 | 412.6035 | 414.7517 | 414.6521 | 414.5375 | 413.6497 | 413.5144 | 413.3518 | 413.131 | 413.0822 | 413.0885 | 411.6885 | 411.5973 | 411.3634 | 413.411 | 412.9647 | 412.8886 | 412.0786 | 411.6417 | 411.5163 | 411.0019 | 410.9843 | 410.9743 | 411.0823 | 410.9918 | 410.9396 | 412.3366 | 412.2237 | 412.0534 | 411.8219 | 411.6407 | 411.4218 | 412.1205 | 410.2804 | 410.2645 | 410.257 | 410.3312 | 410.3468 | 410.395 | 410.5446 | 410.8656 | 408.9269 | 409.2793 | 408.5159 | 410.4202 | 410.4182 | 410.3971 | 411.0814 | 410.8859 | 410.6906 | 408.0078 | 408.1048 | 408.2118 | 412.1669 | 412.0205 | 412.0527 | 412.408 | 412.4243 | 412.4319 | 412.9127 | 413.283 | 413.6703 | 412.8833 | 412.9246 | 412.9183 | 412.4238 | 412.3448 | 410.6295 | 410.4979 | 410.0451 | 411.6766 | 411.5949 | 411.4846 | 411.1166 | 411.5799 | 411.6023 | 411.6899 | 412.023 | 412.0608 | 412.0838 | 412.2246 | 413.0035 | 413.0567 | 412.8122 | 409.7464 | 410.036 | 410.3399 | 410.4155 | 409.6171 | 410.6118 | 410.8904 | 414.4393 | 414.8638 | 414.4055 | 416.9257 | 416.8978 | 416.8806 | 416.8486 | 416.7523 | 416.6903 | 416.6752 | 416.6134 | 408.9761 | 409.2313 | 409.2239 | 409.6353 | 409.8208 | 410.5235 | 411.3467 | 411.5526 | 411.7725 | 409.2577 | 409.9033 | 409.3565 | 412.2889 | 412.1437 | 412.3106 | 408.3339 | 408.1734 | 407.9611 | 409.6189 | 409.3679 | 409.0017 | 410.702 | 410.3908 | 410.5206 | 409.3928 | 409.5704 | 409.5737 | 411.4868 | 411.4839 | 411.2306 | 412.9167 | 413.1295 | 413.8673 | 413.6792 | 413.2696 | 412.9258 | 412.3954 | 412.5565 | 412.644 | 412.6428 | 412.3572 | 412.2746 | 410.8522 | 410.8139 | 410.7693 | 411.5833 | 411.404 | 410.9949 | 409.3795 | 408.3465 | 407.1389 | 409.3125 | 409.1365 | 409.1607 | 409.2558 | 409.0055 | 409.0704 | 410.7734 | 411.8971 | 411.17 | 413.3614 | 413.1889 | 413.0139 | 411.1501 | 411.1108 | 411.2978 | 411.4298 | 411.4038 | 410.6409
248 | Mass flow rate | kg/s | 7.9489 | 7.9571 | 7.9399 | 6.7195 | 6.7394 | 6.7741 | 5.6098 | 5.6844 | 5.697 | 4.7338 | 4.7317 | 4.7354 | 3.8907 | 3.8882 | 3.8842 | 0.84497 | 0.84666 | 0.85519 | 0.9195 | 0.91899 | 0.9021 | 0.86095 | 0.88922 | 0.86704 | 0.92182 | 0.94585 | 0.93789 | 2.0144 | 2.0139 | 2.0161 | 2.0198 | 2.0199 | 2.0153 | 2.1651 | 2.1694 | 2.1862 | 2.2051 | 2.2031 | 2.1964 | 2.3118 | 2.2994 | 2.2945 | 3.4147 | 3.409 | 3.4077 | 3.4827 | 3.6936 | 3.6974 | 3.6988 | 5.0717 | 5.0738 | 5.0904 | 5.0286 | 5.0508 | 5.0205 | 5.5041 | 5.4903 | 5.4845 | 5.4731 | 5.4607 | 5.4454 | 3.4113 | 3.3961 | 3.3989 | 3.6032 | 3.6028 | 3.5954 | 2.245 | 2.2506 | 2.2466 | 1.9719 | 1.9843 | 1.9989 | 2.0022 | 1.9923 | 1.9941 | 0.90279 | 0.90239 | 0.90339 | 0.95738 | 0.96313 | 0.97594 | 1.9955 | 2.0039 | 2.0079 | 2.1523 | 2.1567 | 2.1625 | 2.1544 | 2.1618 | 2.1624 | 3.4232 | 3.4153 | 3.4132 | 3.6009 | 3.6014 | 3.5939 | 3.5601 | 4.9802 | 4.9928 | 4.989 | 4.9863 | 4.9803 | 4.9786 | 4.9947 | 4.986 | 4.9395 | 4.9277 | 4.9444 | 5.3674 | 5.3761 | 5.3614 | 5.3669 | 5.3656 | 5.3682 | 4.872 | 4.8748 | 4.8678 | 3.2563 | 3.2448 | 3.2439 | 3.3194 | 3.3287 | 3.3173 | 1.9283 | 1.927 | 1.9185 | 0.81133 | 0.82824 | 0.77394 | 0.89741 | 0.9016 | 3.5591 | 3.5572 | 3.5789 | 2.0998 | 2.0996 | 2.1068 | 2.1139 | 2.2208 | 2.2316 | 2.2242 | 2.0907 | 2.0913 | 2.0981 | 0.87332 | 0.89993 | 0.87827 | 0.90689 | 4.8635 | 4.8719 | 4.8808 | 4.8639 | 5.295 | 5.2907 | 5.2826 | 5.1749 | 5.1771 | 5.2175 | 5.2843 | 5.3043 | 5.293 | 5.2932 | 5.3034 | 5.3113 | 5.3045 | 5.3194 | 5.076 | 5.0697 | 5.0724 | 5.5437 | 5.5157 | 5.5064 | 5.491 | 5.4786 | 5.4826 | 5.1164 | 5.0837 | 5.1154 | 2.2677 | 2.2716 | 2.2653 | 5.0749 | 5.0757 | 5.089 | 5.5529 | 5.5225 | 5.5315 | 5.5029 | 5.513 | 5.5463 | 5.1119 | 5.0984 | 5.0966 | 2.2775 | 2.2874 | 2.2923 | 2.136 | 2.1344 | 2.1239 | 1.9791 | 1.9755 | 1.9819 | 0.82416 | 0.8299 | 0.87659 | 0.93914 | 0.9198 | 0.92729 | 3.4629 | 3.4756 | 3.474 | 3.6779 | 3.6857 | 3.6916 | 5.0125 | 5.0357 | 5.0512 | 5.4851 | 5.4954 | 5.4851 | 5.4924 | 5.4956 | 5.4857 | 5.0671 | 5.0496 | 5.0464 | 2.2403 | 2.2349 | 2.2491 | 5.4632 | 5.4592 | 5.4415 | 5.4556 | 5.4714 | 5.4878
249 | Duty (calculated) | kw | 1194.2228 | 1194.4254 | 1192.2325 | 997.2752 | 996.7665 | 993.5022 | 814.7887 | 822.6454 | 822.2164 | 667.7088 | 668.9239 | 666.1789 | 544.3725 | 543.9382 | 543.1597 | 153.1475 | 153.5417 | 155.2766 | 166.6799 | 166.6685 | 163.76 | 155.9311 | 161.2838 | 157.3843 | 167.1599 | 171.6596 | 170.2766 | 347.1597 | 347.4329 | 347.7835 | 347.9863 | 347.7961 | 346.4648 | 374.7591 | 374.6223 | 377.4141 | 378.2037 | 376.8448 | 375.6916 | 395.9809 | 393.9581 | 394.219 | 540.648 | 540.5281 | 538.9827 | 550.6914 | 584.015 | 584.5683 | 585.137 | 733.5358 | 733.4254 | 733.9586 | 713.7371 | 714.2152 | 715.6009 | 796.578 | 794.5363 | 794.4285 | 797.5588 | 803.0304 | 803.2746 | 540.8805 | 539.7043 | 539.5458 | 579.6241 | 579.1164 | 578.1612 | 393.9223 | 394.3059 | 393.685 | 344.212 | 345.6501 | 347.8254 | 347.8734 | 346.2072 | 346.8584 | 162.323 | 162.1614 | 162.3914 | 174.0367 | 174.4735 | 176.887 | 344.9519 | 345.2318 | 345.9265 | 369.9332 | 370.6959 | 371.5539 | 370.2976 | 371.3379 | 371.1617 | 548.4659 | 547.0461 | 546.4694 | 575.8071 | 574.9503 | 573.2587 | 570.2439 | 724.1033 | 725.7734 | 725.0676 | 725.2018 | 724.4339 | 724.4052 | 727.6878 | 728.0313 | 703.4734 | 704.0912 | 702.8111 | 780.3448 | 782.5409 | 780.5032 | 788.7115 | 788.5019 | 788.4488 | 689.9625 | 690.2268 | 690.3263 | 521.7365 | 519.4672 | 518.8974 | 532.6852 | 534.3885 | 532.7135 | 335.1249 | 335.35 | 334.6935 | 147.0646 | 150.1079 | 140.1225 | 161.8291 | 162.8532 | 565.0233 | 564.4505 | 565.8985 | 362.291 | 362.0312 | 362.9766 | 363.0978 | 382.7382 | 384.7734 | 383.7492 | 361.5918 | 361.782 | 362.8972 | 157.3059 | 162.7231 | 159.0094 | 164.0821 | 706.0506 | 707.3473 | 709.7574 | 708.1543 | 766.2299 | 771.1453 | 771.7763 | 778.5322 | 780.904 | 784.3735 | 803.8838 | 806.2305 | 805.3498 | 805.1625 | 809.0632 | 809.0355 | 808.7085 | 812.4026 | 723.5485 | 724.0419 | 724.0891 | 802.2418 | 800.7644 | 802.7703 | 809.2512 | 809.4669 | 810.8308 | 737.8364 | 738.266 | 739.2393 | 391.9547 | 392.2816 | 392.3825 | 719.2411 | 718.4432 | 719.5961 | 807.7164 | 802.7335 | 802.2793 | 802.952 | 802.504 | 807.984 | 739.3523 | 738.8509 | 738.8339 | 391.9746 | 393.4178 | 394.5115 | 370.5324 | 371.1862 | 370.5925 | 345.3086 | 344.1844 | 344.4285 | 148.8988 | 150.067 | 158.6144 | 169.785 | 166.0926 | 167.4398 | 550.1263 | 552.7647 | 552.4402 | 587.4418 | 587.8488 | 587.8927 | 715.3194 | 714.3057 | 709.7185 | 791.3204 | 791.8306 | 791.5235 | 796.7927 | 797.5691 | 795.7307 | 737.6399 | 742.064 | 738.7508 | 390.4075 | 388.3136 | 391.0304 | 803.4694 | 802.5705 | 801.2543 | 798.9917 | 799.9889 | 797.88
250
251 | Energy balance kW/(Mref*(Hd-Hs)) no NI, No econ | kw | -1.0072 | -1.0026 | -1.0044 | -1.0008 | -1.0026 | -0.98961 | -1.0123 | -0.99619 | -0.99911 | -1.0003 | -0.9972 | -0.99355 | -1.0014 | -0.99819 | -0.99407 | -1.0963 | -1.0661 | -1.0883 | -1.0938 | -1.1005 | -1.1276 | -1.1166 | -1.0508 | -1.1487 | -1.0832 | -1.068 | -1.1152 | -1.0096 | -1.0183 | -1.0018 | -1.0189 | -1.023 | -1.0127 | -1.0238 | -1.0339 | -1.0204 | -1.012 | -1.0006 | -1.0191 | -0.99839 | -0.9963 | -1.017 | -1.0036 | -1.0057 | -1.0123 | -0.99385 | -1.0026 | -1.0004 | -1.0011 | -0.99314 | -1.0017 | -0.99433 | -0.99218 | -0.98437 | -0.99662 | -0.99253 | -0.99456 | -0.99443 | -0.98566 | -0.98821 | -1.0116 | -1.0053 | -0.9931 | -0.98963 | -0.99203 | -0.99658 | -0.99178 | -1.023 | -1.0322 | -1.0228 | -1.0355 | -1.0259 | -1.0287 | -1.0309 | -1.032 | -1.0393 | -1.0612 | -1.1058 | -1.073 | -1.1199 | -1.0858 | -1.1496 | -1.0338 | -1.0281 | -1.0129 | -1.0329 | -1.0165 | -1.0311 | -1.0354 | -1.0275 | -1.0365 | -1.0149 | -1.0075 | -1.0085 | -1.0082 | -1.0065 | -1.0118 | -0.99042 | -0.9925 | -0.98983 | -0.99067 | -0.9906 | -0.99361 | -0.995 | -0.98507 | -0.9951 | -0.99525 | -1.0048 | -0.99349 | -0.98551 | -0.99491 | -1.0018 | -0.99686 | -1.0025 | -0.9912 | -0.98295 | -1.0021 | -0.99458 | -1.0088 | -1.0121 | -1.0178 | -1.0004 | -0.99867 | -1.0002 | -0.9942 | -0.9892 | -1.0005 | -1.1841 | -1.1449 | -1.2722 | -1.1985 | -1.1582 | -0.99958 | -0.99807 | -0.9689 | -1.0252 | -1.0326 | -1.0424 | -1.0389 | -1.0221 | -1.0168 | -1.0153 | -1.0087 | -1.0192 | -1.0136 | -1.1043 | -1.1023 | -1.1134 | -1.0646 | -0.99667 | -0.99804 | -0.99391 | -0.99454 | -0.98331 | -0.98848 | -0.9942 | -0.99128 | -0.99654 | -0.99436 | -1.1398 | -1.1289 | -1.1375 | -1.1457 | -1.1347 | -1.1381 | -1.1361 | -1.149 | -0.98929 | -0.9934 | -0.9939 | -0.98073 | -0.99225 | -1.0014 | -0.99703 | -0.99488 | -0.99526 | -0.98712 | -1.0017 | -0.99515 | -1.0108 | -1.0046 | -1.0025 | -0.9967 | -1.0008 | -0.98758 | -0.9966 | -1.0004 | -0.99587 | -1.0017 | -1.0024 | -0.98139 | -1.0004 | -0.99782 | -1.0037 | -1.02 | -1.0299 | -1.0028 | -1.0187 | -1.0002 | -1.0462 | -1.0407 | -1.058 | -1.0518 | -1.1765 | -1.1853 | -1.1286 | -1.0946 | -1.1787 | -1.162 | -0.9953 | -0.99983 | -0.9874 | -1.0124 | -1.0062 | -1.0069 | -0.99672 | -0.98115 | -0.98094 | -0.99705 | -0.98872 | -0.98625 | -1.0021 | -0.98898 | -0.99384 | -0.99153 | -1.002 | -0.99276 | -1.0336 | -1.0563 | -1.0388 | -0.99392 | -1.0053 | -0.99203 | -1.003 | -1.0061 | -0.99438
252 | Energy balance kW/(Mref*(Hd-Hs)) no NI, | kw
253 | Energy balance kW/(Mref*(Hd-Hs)) | kw
254
255 | COP | - | 4.085 | 4.1032 | 4.0934 | 3.6346 | 3.6242 | 3.6397 | 3.1211 | 3.1584 | 3.1411 | 2.6387 | 2.6724 | 2.6563 | 2.2384 | 2.2454 | 2.2538 | 7.8006 | 8.05 | 7.9608 | 8.1048 | 8.1645 | 7.9873 | 7.8693 | 8.4585 | 8.0478 | 8.371 | 8.4953 | 8.2227 | 6.6705 | 6.6301 | 6.7019 | 6.3679 | 6.3249 | 6.3467 | 6.3817 | 6.3626 | 6.3861 | 6.713 | 6.7026 | 6.5812 | 6.6695 | 6.6539 | 6.6279 | 4.679 | 4.6813 | 4.6351 | 4.7142 | 4.6192 | 4.6387 | 4.6548 | 3.2093 | 3.182 | 3.1998 | 2.8113 | 2.8106 | 2.8062 | 3.1319 | 3.1263 | 3.1277 | 3.1739 | 3.1931 | 3.166 | 4.5262 | 4.5433 | 4.5176 | 4.5436 | 4.5241 | 4.5314 | 6.6588 | 6.5944 | 6.6424 | 6.3526 | 6.4056 | 6.3855 | 6.3751 | 6.3894 | 6.399 | 8.4087 | 8.1192 | 8.2731 | 8.4231 | 8.6826 | 8.3289 | 6.5489 | 6.5373 | 6.5549 | 6.4563 | 6.5563 | 6.4854 | 6.2196 | 6.2785 | 6.2546 | 4.4826 | 4.5149 | 4.4955 | 4.4759 | 4.4801 | 4.4525 | 4.5129 | 3.1502 | 3.158 | 3.1554 | 3.1564 | 3.1469 | 3.1449 | 3.1798 | 3.163 | 2.7523 | 2.7498 | 2.7601 | 3.0963 | 3.0705 | 3.0369 | 3.1327 | 3.1241 | 3.1576 | 2.7806 | 2.7278 | 2.7526 | 4.4963 | 4.4684 | 4.4503 | 4.5226 | 4.5297 | 4.5231 | 6.4184 | 6.4634 | 6.4471 | 7.6169 | 7.9389 | 7.2023 | 7.7615 | 8.162 | 4.477 | 4.4644 | 4.4723 | 6.4868 | 6.4299 | 6.3618 | 6.3778 | 6.4449 | 6.4737 | 6.501 | 6.0455 | 5.9828 | 6.01 | 7.5781 | 7.7815 | 7.7321 | 7.9896 | 3.1144 | 3.1138 | 3.1354 | 3.1348 | 3.0632 | 3.0778 | 3.0648 | 3.1398 | 3.1408 | 3.1581 | 3.1769 | 3.2107 | 3.2094 | 3.1993 | 3.2425 | 3.2277 | 3.2495 | 3.2641 | 2.8959 | 2.8934 | 2.8944 | 3.2083 | 3.1717 | 3.1655 | 3.2318 | 3.2435 | 3.247 | 3.2417 | 3.2594 | 3.2563 | 6.6315 | 6.6537 | 6.6966 | 2.8585 | 2.849 | 2.8733 | 3.2261 | 3.21 | 3.217 | 3.1827 | 3.1754 | 3.2225 | 3.2609 | 3.2734 | 3.2667 | 6.675 | 6.6763 | 6.7862 | 6.6121 | 6.6773 | 6.5772 | 6.6599 | 6.6092 | 6.6252 | 7.5557 | 7.5741 | 8.0426 | 8.2537 | 7.8934 | 8.1355 | 4.6827 | 4.6771 | 4.7111 | 4.6075 | 4.6531 | 4.6402 | 2.8616 | 2.8934 | 2.853 | 3.1494 | 3.1713 | 3.1865 | 3.2004 | 3.2188 | 3.1911 | 3.2713 | 3.2914 | 3.3006 | 6.6916 | 6.5771 | 6.7063 | 3.2077 | 3.1622 | 3.2086 | 3.1446 | 3.1398 | 3.1582
256
257
258 | Conditions to compcalc
259 | Table Duty
260 | % of Duty
261 | Table Power
262 | % of Power
263 | Table COP
264 | % of COP
265
266 | Econ Port specific volume with assumed SH | m3/kg | 0.024471 | 0.024489 | 0.024502 | 0.024724 | 0.024731 | 0.024802 | 0.025045 | 0.025102 | 0.025156 | 0.025509 | 0.025559 | 0.025619 | 0.025951 | 0.025952 | 0.025977 | 0.02754 | 0.027589 | 0.027586 | 0.027706 | 0.02774 | 0.027756 | 0.027144 | 0.027168 | 0.027173 | 0.027255 | 0.027278 | 0.027289 | 0.025003 | 0.024987 | 0.024977 | 0.024956 | 0.024957 | 0.024955 | 0.024937 | 0.024941 | 0.024928 | 0.024896 | 0.024887 | 0.024812 | 0.024781 | 0.024757 | 0.024752 | 0.024668 | 0.024641 | 0.024678 | 0.024689 | 0.024737 | 0.024739 | 0.024786 | 0.025012 | 0.025059 | 0.025174 | 0.025795 | 0.025909 | 0.026165 | 0.026701 | 0.02678 | 0.026865 | 0.027159 | 0.027228 | 0.027341 | 0.025133 | 0.025212 | 0.025245 | 0.025491 | 0.025545 | 0.025557 | 0.026114 | 0.026138 | 0.02618 | 0.026248 | 0.02628 | 0.026316 | 0.026379 | 0.026413 | 0.026442 | 0.026856 | 0.026918 | 0.026925 | 0.027279 | 0.02739 | 0.027401 | 0.02525 | 0.025236 | 0.025249 | 0.025205 | 0.025198 | 0.025185 | 0.025138 | 0.025123 | 0.02513 | 0.024968 | 0.024953 | 0.024978 | 0.025047 | 0.025027 | 0.025009 | 0.024981 | 0.025058 | 0.025062 | 0.025069 | 0.02514 | 0.025157 | 0.025193 | 0.025228 | 0.025314 | 0.02616 | 0.026207 | 0.026307 | 0.026822 | 0.026873 | 0.02695 | 0.027142 | 0.027248 | 0.027234 | 0.024952 | 0.025012 | 0.025037 | 0.025688 | 0.025721 | 0.025724 | 0.025893 | 0.025891 | 0.025924 | 0.026583 | 0.026619 | 0.026628 | 0.027255 | 0.027274 | 0.027309 | 0.027402 | 0.027433 | 0.025468 | 0.025495 | 0.025546 | 0.026158 | 0.026135 | 0.026165 | 0.026327 | 0.026372 | 0.026407 | 0.026414 | 0.026795 | 0.026806 | 0.026817 | 0.027259 | 0.027306 | 0.027311 | 0.027293 | 0.023463 | 0.023492 | 0.023508 | 0.023516 | 0.023772 | 0.023814 | 0.023845 | 0.024145 | 0.024183 | 0.024342 | 0.023777 | 0.023806 | 0.023834 | 0.023834 | 0.023899 | 0.023948 | 0.023992 | 0.024055 | 0.024993 | 0.025034 | 0.025075 | 0.025461 | 0.025502 | 0.025566 | 0.025643 | 0.025695 | 0.025744 | 0.026008 | 0.026126 | 0.026225 | 0.027339 | 0.027401 | 0.027405 | 0.025028 | 0.025099 | 0.025147 | 0.02548 | 0.02553 | 0.025557 | 0.025961 | 0.026012 | 0.026069 | 0.026203 | 0.026275 | 0.026364 | 0.028015 | 0.028049 | 0.028109 | 0.027021 | 0.027054 | 0.027105 | 0.027307 | 0.027347 | 0.027404 | 0.02623 | 0.026241 | 0.026243 | 0.026229 | 0.026246 | 0.026242 | 0.025855 | 0.025892 | 0.025913 | 0.02621 | 0.026226 | 0.02628 | 0.025046 | 0.025208 | 0.025314 | 0.025574 | 0.02563 | 0.025731 | 0.025906 | 0.026009 | 0.026121 | 0.025507 | 0.02555 | 0.025606 | 0.026722 | 0.026784 | 0.026808 | 0.025024 | 0.025086 | 0.025156 | 0.025337 | 0.025427 | 0.025498
267 | Econ Port Enthalpy with assumed SH | KJ/kg | 422.1411 | 422.128 | 422.1192 | 421.9602 | 421.9554 | 421.9049 | 421.7334 | 421.6929 | 421.6548 | 421.4089 | 421.3741 | 421.3331 | 421.1046 | 421.104 | 421.0872 | 420.0481 | 420.0164 | 420.0182 | 419.9407 | 419.919 | 419.9085 | 420.3062 | 420.2904 | 420.2871 | 420.2332 | 420.2187 | 420.2114 | 421.7625 | 421.7737 | 421.7807 | 421.7962 | 421.7949 | 421.7965 | 421.809 | 421.8067 | 421.8155 | 421.8382 | 421.8449 | 421.8975 | 421.9201 | 421.937 | 421.9402 | 422.0004 | 422.0198 | 421.9934 | 421.985 | 421.9511 | 421.9497 | 421.9165 | 421.7565 | 421.7232 | 421.6422 | 421.2119 | 421.1334 | 420.959 | 420.5992 | 420.5466 | 420.4902 | 420.2961 | 420.2511 | 420.1772 | 421.6713 | 421.6157 | 421.5928 | 421.4216 | 421.384 | 421.3757 | 420.994 | 420.9778 | 420.9492 | 420.9031 | 420.8812 | 420.8571 | 420.8149 | 420.7918 | 420.7726 | 420.4959 | 420.4548 | 420.4502 | 420.2175 | 420.1454 | 420.138 | 421.5889 | 421.5988 | 421.5899 | 421.6208 | 421.6256 | 421.6345 | 421.6677 | 421.678 | 421.6731 | 421.7871 | 421.7978 | 421.7801 | 421.7313 | 421.7458 | 421.7582 | 421.7778 | 421.7242 | 421.7212 | 421.7165 | 421.666 | 421.6541 | 421.6291 | 421.6048 | 421.5447 | 420.963 | 420.9308 | 420.8635 | 420.5186 | 420.4848 | 420.4342 | 420.3076 | 420.2383 | 420.2476 | 421.7989 | 421.7566 | 421.7384 | 421.2855 | 421.2627 | 421.2608 | 421.1445 | 421.1457 | 421.1233 | 420.6775 | 420.6534 | 420.6476 | 420.2337 | 420.2211 | 420.1981 | 420.1373 | 420.1177 | 421.4374 | 421.4186 | 421.3834 | 420.9643 | 420.9798 | 420.9589 | 420.8497 | 420.8196 | 420.7961 | 420.7912 | 420.5368 | 420.5296 | 420.522 | 420.2311 | 420.2001 | 420.1969 | 420.2087 | 422.8782 | 422.8565 | 422.8441 | 422.8388 | 422.6491 | 422.6181 | 422.5959 | 422.3767 | 422.3494 | 422.2338 | 422.6455 | 422.6242 | 422.604 | 422.604 | 422.5562 | 422.52 | 422.4878 | 422.4419 | 421.7699 | 421.7405 | 421.7119 | 421.4421 | 421.4134 | 421.3692 | 421.3162 | 421.2801 | 421.2467 | 421.0662 | 420.986 | 420.9188 | 420.1784 | 420.1384 | 420.136 | 421.745 | 421.6951 | 421.6617 | 421.4293 | 421.3946 | 421.3759 | 421.0979 | 421.0632 | 421.0247 | 420.9336 | 420.885 | 420.8249 | 419.7425 | 419.721 | 419.6829 | 420.3872 | 420.3653 | 420.332 | 420.1996 | 420.1737 | 420.1365 | 420.9149 | 420.9076 | 420.9065 | 420.9157 | 420.9043 | 420.9068 | 421.1702 | 421.1449 | 421.1305 | 420.9286 | 420.9178 | 420.8815 | 421.7324 | 421.6184 | 421.5443 | 421.3637 | 421.3253 | 421.2558 | 421.1358 | 421.0655 | 420.9889 | 421.4105 | 421.3803 | 421.3421 | 420.5849 | 420.544 | 420.528 | 421.7481 | 421.7045 | 421.655 | 421.5284 | 421.4658 | 421.4167
268 | Econ liquid out enthalpy | KJ/kg | 254.9711 | 254.9326 | 254.9064 | 254.4364 | 254.4224 | 254.2735 | 253.769 | 253.6502 | 253.5385 | 252.8203 | 252.7192 | 252.5999 | 251.9371 | 251.9355 | 251.8868 | 248.9162 | 248.8267 | 248.8317 | 248.6131 | 248.5519 | 248.5222 | 249.648 | 249.603 | 249.5935 | 249.4406 | 249.3994 | 249.3787 | 253.8545 | 253.8875 | 253.9079 | 253.9534 | 253.9495 | 253.9543 | 253.991 | 253.9842 | 254.0102 | 254.0771 | 254.0968 | 254.2515 | 254.318 | 254.3679 | 254.3774 | 254.555 | 254.6124 | 254.5343 | 254.5095 | 254.4095 | 254.4054 | 254.3075 | 253.8368 | 253.7391 | 253.5016 | 252.248 | 252.0205 | 251.5168 | 250.4836 | 250.3331 | 250.172 | 249.6193 | 249.4915 | 249.2818 | 253.5869 | 253.4243 | 253.357 | 252.8573 | 252.7479 | 252.7238 | 251.6175 | 251.5709 | 251.4884 | 251.3557 | 251.2926 | 251.2231 | 251.1018 | 251.0355 | 250.9804 | 250.1883 | 250.071 | 250.058 | 249.3961 | 249.1916 | 249.1707 | 253.3458 | 253.3747 | 253.3488 | 253.439 | 253.4531 | 253.4791 | 253.5763 | 253.6067 | 253.5923 | 253.9267 | 253.9582 | 253.9062 | 253.7629 | 253.8054 | 253.8419 | 253.8996 | 253.7421 | 253.7332 | 253.7195 | 253.5715 | 253.5367 | 253.4634 | 253.3922 | 253.2165 | 251.5281 | 251.4354 | 251.2417 | 250.253 | 250.1567 | 250.0122 | 249.6521 | 249.455 | 249.4814 | 253.9613 | 253.8372 | 253.7836 | 252.4615 | 252.3954 | 252.3897 | 252.0526 | 252.056 | 251.9911 | 250.7077 | 250.6387 | 250.622 | 249.442 | 249.4063 | 249.3409 | 249.1687 | 249.1132 | 252.9034 | 252.8486 | 252.7462 | 251.5321 | 251.5766 | 251.5165 | 251.2019 | 251.1155 | 251.0478 | 251.0337 | 250.3052 | 250.2846 | 250.2628 | 249.4345 | 249.3466 | 249.3376 | 249.3712 | 257.1753 | 257.1098 | 257.0725 | 257.0565 | 256.4858 | 256.393 | 256.3265 | 255.6714 | 255.5901 | 255.2463 | 256.4752 | 256.4111 | 256.3506 | 256.3506 | 256.2076 | 256.0992 | 256.0029 | 255.8658 | 253.8763 | 253.7899 | 253.7059 | 252.9171 | 252.8336 | 252.7048 | 252.5508 | 252.4458 | 252.3487 | 251.8261 | 251.5944 | 251.4008 | 249.2851 | 249.1718 | 249.1649 | 253.8031 | 253.6568 | 253.5587 | 252.8799 | 252.7789 | 252.7243 | 251.9179 | 251.8174 | 251.7061 | 251.4436 | 251.3036 | 251.1306 | 248.055 | 247.9948 | 247.8878 | 249.8784 | 249.8161 | 249.7214 | 249.3454 | 249.2717 | 249.1663 | 251.3896 | 251.3685 | 251.3654 | 251.3919 | 251.3591 | 251.3662 | 252.1272 | 252.0539 | 252.0122 | 251.4291 | 251.398 | 251.2935 | 253.7661 | 253.4319 | 253.2153 | 252.6889 | 252.5772 | 252.3751 | 252.0274 | 251.8242 | 251.6028 | 252.8249 | 252.7373 | 252.6259 | 250.4426 | 250.3258 | 250.2798 | 253.8123 | 253.6844 | 253.5391 | 253.1691 | 252.9862 | 252.8432
269 | Econ Vol Flow Econ / Suc Thermodynamic | - | 0.040709 | 0.041065 | 0.040326 | 0.036509 | 0.036888 | 0.037529 | 0.033384 | 0.03365 | 0.033734 | 0.031024 | 0.031393 | 0.03184 | 0.027824 | 0.027607 | 0.027575 | -0.044848 | -0.044634 | -0.044479 | -0.043961 | -0.044138 | -0.044516 | -0.045887 | -0.045781 | -0.045787 | -0.045268 | -0.045643 | -0.045699 | -0.035805 | -0.035743 | -0.035738 | -0.035728 | -0.035749 | -0.035643 | -0.035504 | -0.035177 | -0.035552 | -0.036308 | -0.036039 | -0.036245 | -0.03659 | -0.036035 | -0.036138 | -0.0061029 | -0.0067266 | -0.0062087 | -0.0065718 | -0.0053992 | -0.0055678 | -0.005823 | 0.027458 | 0.027781 | 0.028973 | 0.035026 | 0.035372 | 0.036871 | 0.038721 | 0.039238 | 0.039649 | 0.039056 | 0.038991 | 0.040496 | -0.0038402 | -0.0037477 | -0.0032594 | -0.0025586 | -0.0020305 | -0.0023066 | -0.030734 | -0.030366 | -0.030549 | -0.030867 | -0.030401 | -0.030239 | -0.029992 | -0.02995 | -0.030221 | -0.046821 | -0.046608 | -0.047142 | -0.045675 | -0.045099 | -0.045394 | -0.034523 | -0.034406 | -0.034617 | -0.034982 | -0.035075 | -0.035087 | -0.035122 | -0.035127 | -0.035032 | -0.0044376 | -0.0046674 | -0.0047836 | -0.0045359 | -0.0044566 | -0.0047339 | -0.0047834 | 0.028006 | 0.028101 | 0.028168 | 0.028553 | 0.028671 | 0.028919 | 0.029051 | 0.029567 | 0.036966 | 0.036812 | 0.037469 | 0.04008 | 0.039947 | 0.040319 | 0.039405 | 0.039558 | 0.039203 | 0.029159 | 0.029837 | 0.029656 | -0.0013129 | -0.0011752 | -0.00075631 | -0.00030471 | -0.00043239 | -0.00037529 | -0.029828 | -0.029313 | -0.029315 | -0.045764 | -0.045556 | -0.045231 | -0.044577 | -0.045217 | -0.0025904 | -0.002589 | -0.0020889 | -0.031497 | -0.031575 | -0.031386 | -0.030568 | -0.030526 | -0.030551 | -0.030552 | -0.027646 | -0.027538 | -0.027476 | -0.044614 | -0.044464 | -0.04482 | -0.045239 | 0.017183 | 0.018054 | 0.018355 | 0.018088 | 0.019971 | 0.020088 | 0.020125 | 0.019503 | 0.019762 | 0.020994 | 0.019098 | 0.019567 | 0.01923 | 0.019247 | 0.018384 | 0.019122 | 0.01898 | 0.018582 | 0.029377 | 0.02958 | 0.029919 | 0.030882 | 0.03024 | 0.030847 | 0.029064 | 0.028863 | 0.029406 | 0.034912 | 0.034398 | 0.035698 | -0.026256 | -0.026024 | -0.026774 | 0.030138 | 0.030663 | 0.030854 | 0.028925 | 0.028792 | 0.028853 | 0.033456 | 0.034059 | 0.034486 | 0.035301 | 0.035384 | 0.035803 | -0.02378 | -0.023442 | -0.024097 | -0.027383 | -0.027765 | -0.027046 | -0.026805 | -0.027063 | -0.026653 | -0.048725 | -0.048649 | -0.048879 | -0.04833 | -0.048504 | -0.04866 | -0.00034802 | -0.00072217 | -0.00067631 | 0.0011224 | 0.0013269 | 0.0011747 | 0.030259 | 0.030909 | 0.032098 | 0.031999 | 0.032359 | 0.032392 | 0.031713 | 0.031544 | 0.032617 | 0.0318 | 0.03108 | 0.031145 | -0.029208 | -0.028183 | -0.028873 | 0.025516 | 0.025917 | 0.026158 | 0.029832 | 0.031076 | 0.031774
270 | Econ Vol Flow Econ / Suc Measured | - | 5.0658e-05 | 0.00060319 | -5.8983e-06 | -2.8506e-05 | -2.1546e-05 | -3.5511e-05 | -1.8026e-05 | -1.9713e-05 | -3.2943e-05 | -2.4149e-05 | -1.7613e-05 | -2.1842e-05 | -2.4137e-05 | -9.3344e-06 | -1.7458e-05 | -3.0957e-05 | 8.7695e-06 | 4.5524e-05 | -6.0723e-05 | 1.4719e-06 | 2.2538e-05 | -7.0651e-05 | -9.8076e-05 | -3.6288e-05 | -1.8826e-05 | -8.6499e-05 | -3.8729e-05 | -9.4772e-05 | -6.8311e-05 | -9.6026e-05 | -0.00010681 | -9.2336e-05 | -0.00010064 | -5.8766e-05 | -7.7014e-05 | -8.2728e-05 | -7.8361e-05 | -6.5694e-05 | -5.1501e-05 | -9.2175e-05 | -6.6891e-05 | -7.2236e-05 | -5.4877e-05 | -4.2642e-05 | -5.2868e-05 | -6.7373e-05 | -5.6428e-05 | -5.1782e-05 | -4.4266e-05 | 0.10722 | 0.10704 | 0.10715 | -1.8849e-05 | -1.8411e-05 | -1.7633e-05 | 0.00015772 | 6.6583e-05 | 4.4763e-05 | -1.7411e-05 | -6.3611e-06 | -4.0906e-06 | -3.5438e-05 | -5.8976e-05 | -4.2364e-05 | -2.9069e-05 | -4.6554e-05 | -3.6527e-05 | -6.3265e-05 | -6.449e-05 | -1.7494e-05 | -6.2851e-05 | -6.2145e-05 | -4.0617e-05 | -7.0545e-05 | -3.1341e-05 | -2.9381e-05 | -6.7269e-05 | -0.00022498 | -2.8842e-05 | -6.5021e-05 | -0.00011803 | -2.0058e-05 | -0.00011152 | -5.2134e-05 | -7.4526e-05 | -0.00010843 | -6.2519e-05 | -8.0123e-05 | -5.9548e-05 | -7.612e-05 | -7.7234e-05 | -4.4674e-05 | -2.7614e-05 | -5.8097e-05 | -4.0983e-05 | -7.8008e-05 | -4.3143e-05 | -3.525e-05 | 0.02702 | 0.028127 | 0.026048 | 0.036369 | 0.048472 | 0.038607 | 0.036416 | 0.034983 | -2.0807e-05 | -2.2461e-05 | -1.6008e-05 | -1.722e-05 | -2.2007e-05 | -9.7939e-06 | -1.338e-05 | 7.2454e-06 | -7.4526e-06 | -2.0256e-05 | -3.3505e-05 | -3.1662e-05 | -6.0908e-05 | -2.6495e-05 | -3.7446e-05 | -4.9687e-05 | -3.5114e-05 | -2.3594e-05 | -3.7045e-05 | -1.6357e-05 | -1.4897e-05 | -1.8087e-05 | 1.3936e-05 | -3.7949e-05 | -2.4937e-05 | 1.9349e-05 | -2.6774e-05 | -3.2986e-05 | -4.8403e-05 | -1.0395e-05 | -3.874e-05 | -5.1459e-05 | -3.727e-05 | -6.196e-05 | -2.9744e-05 | -4.1226e-05 | -5.0689e-05 | -4.7816e-05 | -1.015e-05 | -2.3188e-05 | -6.3485e-05 | -5.2234e-05 | -4.6363e-05 | 0.031326 | 0.026001 | 0.030548 | 0.027373 | -3.7147e-05 | -3.274e-05 | -3.4264e-05 | -2.5736e-05 | -2.369e-05 | -3.1546e-05 | -3.2143e-05 | -3.7998e-05 | -4.2908e-05 | -2.8505e-05 | -2.2248e-05 | -4.7622e-05 | -3.3927e-05 | -1.8678e-05 | -1.8053e-05 | -2.7047e-05 | -3.5762e-05 | -8.5104e-06 | -4.0329e-05 | -1.9112e-05 | -1.987e-05 | -2.876e-05 | -2.4987e-05 | 0.025453 | 0.022331 | 0.025561 | 4.4148e-06 | -2.6279e-05 | -8.8398e-06 | -3.4531e-05 | -2.1755e-05 | -2.7719e-05 | -1.2282e-05 | -1.4246e-05 | 0.00020314 | -1.8785e-05 | -8.902e-06 | -2.1557e-05 | 0.035489 | 0.035503 | 0.035447 | 1.382e-05 | -1.3162e-06 | -1.869e-05 | -1.4324e-05 | -2.2178e-05 | -4.6998e-05 | 2.0619e-05 | 3.4603e-06 | 9.988e-06 | -8.3667e-05 | -4.7163e-05 | -9.7297e-05 | -0.00014276 | -0.00010802 | -2.4039e-05 | -2.8693e-05 | -2.8855e-05 | -1.8447e-05 | -1.2501e-05 | -1.9423e-05 | -3.4678e-05 | -3.1304e-05 | -1.0718e-05 | -2.2976e-05 | 0.0009407 | 0.0016767 | 0.0013966 | -1.7196e-05 | -4.7358e-06 | -2.338e-06 | 0.033538 | 0.023741 | 0.023869 | -3.9073e-05 | 1.0223e-05 | -3.4701e-05 | -2.3269e-05 | -9.9934e-06 | -1.7395e-05 | -2.015e-05 | -2.2364e-05 | -1.6027e-05
271 | Econ Balance (Measured/Thermo) |  | 0.0012444 | 0.014689 | -0.00014626 | -0.00078081 | -0.00058409 | -0.00094622 | -0.00053997 | -0.00058582 | -0.00097655 | -0.00077841 | -0.00056107 | -0.00068599 | -0.00086749 | -0.00033812 | -0.0006331 | 0.00069026 | -0.00019647 | -0.0010235 | 0.0013813 | -3.3348e-05 | -0.0005063 | 0.0015397 | 0.0021423 | 0.00079255 | 0.00041587 | 0.0018951 | 0.00084749 | 0.0026469 | 0.0019112 | 0.002687 | 0.0029896 | 0.0025829 | 0.0028237 | 0.0016552 | 0.0021893 | 0.0023269 | 0.0021582 | 0.0018229 | 0.0014209 | 0.0025192 | 0.0018563 | 0.0019989 | 0.0089919 | 0.0063394 | 0.0085151 | 0.010252 | 0.010451 | 0.0093002 | 0.0076019 | 3.9049 | 3.8529 | 3.6982 | -0.00053816 | -0.00052049 | -0.00047825 | 0.0040731 | 0.0016969 | 0.001129 | -0.00044579 | -0.00016314 | -0.00010101 | 0.0092282 | 0.015737 | 0.012998 | 0.011361 | 0.022927 | 0.015836 | 0.0020585 | 0.0021237 | 0.00057267 | 0.0020362 | 0.0020442 | 0.0013432 | 0.0023522 | 0.0010465 | 0.00097219 | 0.0014367 | 0.0048271 | 0.0006118 | 0.0014235 | 0.0026172 | 0.00044186 | 0.0032301 | 0.0015153 | 0.0021529 | 0.0030996 | 0.0017824 | 0.0022835 | 0.0016955 | 0.002167 | 0.0022047 | 0.010067 | 0.0059164 | 0.012145 | 0.0090352 | 0.017504 | 0.0091136 | 0.0073693 | 0.96481 | 1.0009 | 0.92474 | 1.2737 | 1.6906 | 1.335 | 1.2535 | 1.1832 | -0.00056288 | -0.00061016 | -0.00042724 | -0.00042965 | -0.00055089 | -0.00024291 | -0.00033954 | 0.00018316 | -0.00019011 | -0.00069465 | -0.0011229 | -0.0010676 | 0.046391 | 0.022546 | 0.049512 | 0.16306 | 0.081209 | 0.062867 | 0.001242 | 0.00055801 | 0.00050816 | 0.00039523 | -0.0003059 | 0.00083901 | 0.00055943 | -0.00042792 | 0.010336 | 0.012741 | 0.023172 | 0.00033005 | 0.0012269 | 0.0016395 | 0.0012193 | 0.0020298 | 0.00097356 | 0.0013494 | 0.0018335 | 0.0017364 | 0.00036941 | 0.00051975 | 0.0014278 | 0.0011654 | 0.0010249 | 1.8231 | 1.4402 | 1.6643 | 1.5133 | -0.0018601 | -0.0016298 | -0.0017026 | -0.0013196 | -0.0011988 | -0.0015026 | -0.0016831 | -0.0019419 | -0.0022313 | -0.001481 | -0.0012102 | -0.0024904 | -0.0017875 | -0.0010052 | -0.00061455 | -0.00091434 | -0.0011953 | -0.00027558 | -0.0013336 | -0.00061956 | -0.00068366 | -0.00099643 | -0.00084971 | 0.72907 | 0.64921 | 0.71602 | -0.00016815 | 0.0010098 | 0.00033016 | -0.0011458 | -0.00070949 | -0.00089838 | -0.0004246 | -0.00049478 | 0.0070404 | -0.00056146 | -0.00026137 | -0.00062509 | 1.0053 | 1.0034 | 0.99004 | -0.00058116 | 5.6147e-05 | 0.0007756 | 0.00052311 | 0.00079878 | 0.0017377 | -0.00076921 | -0.00012786 | -0.00037475 | 0.0017171 | 0.00096946 | 0.0019906 | 0.0029538 | 0.0022271 | 0.00049402 | 0.082448 | 0.039956 | 0.027276 | -0.011137 | -0.014638 | -0.029521 | -0.0010346 | -0.00034677 | -0.00071581 | 0.029398 | 0.051817 | 0.043114 | -0.00054223 | -0.00015013 | -7.1682e-05 | 1.0547 | 0.76386 | 0.76639 | 0.0013377 | -0.00036274 | 0.0012018 | -0.00091194 | -0.00038559 | -0.000665 | -0.00067544 | -0.00071967 | -0.00050441
272 | Economised Duty |  | 1285.5318 | 1286.4971 | 1282.7741 | 1078.0834 | 1078.4003 | 1076.2238 | 886.7811 | 895.3896 | 895.0622 | 732.7356 | 734.5958 | 732.4974 | 600.9839 | 600.1606 | 599.2589 | 138.6053 | 139.0473 | 140.6519 | 151.2771 | 151.2444 | 148.4666 | 140.4935 | 145.3752 | 141.9025 | 150.9362 | 154.8974 | 153.6309 | 317.3516 | 317.6251 | 317.9896 | 318.2209 | 318.0264 | 316.869 | 342.7013 | 342.9795 | 345.1982 | 345.1002 | 344.1639 | 342.8328 | 361.0187 | 359.5342 | 359.7694 | 532.1033 | 531.102 | 530.3025 | 541.3298 | 575.8675 | 576.186 | 576.3699 | 788.8678 | 789.3832 | 791.9162 | 786.3352 | 787.2796 | 790.8702 | 875.2622 | 873.917 | 874.2928 | 875.7947 | 881.189 | 883.905 | 535.6112 | 534.5778 | 535.096 | 575.9332 | 576.1901 | 574.839 | 366.2443 | 367.0384 | 366.3025 | 320.0279 | 321.9014 | 324.0861 | 324.4098 | 322.8472 | 323.2661 | 145.8013 | 145.7599 | 145.7209 | 157.0245 | 157.7342 | 159.779 | 316.7466 | 317.1455 | 317.5865 | 339.1284 | 339.7522 | 340.5906 | 339.3372 | 340.2333 | 340.2514 | 542.2657 | 540.5213 | 539.7824 | 569.1504 | 568.4215 | 566.3223 | 563.2824 | 779.595 | 781.5283 | 780.9635 | 781.6478 | 780.9613 | 781.2955 | 784.9356 | 786.0378 | 777.4702 | 777.8107 | 777.6258 | 859.6757 | 861.5819 | 859.8804 | 866.3691 | 866.1682 | 865.4049 | 750.519 | 752.0208 | 751.7233 | 520.0429 | 517.9577 | 517.9259 | 532.2875 | 533.8217 | 532.2234 | 312.7819 | 313.4231 | 312.8162 | 132.6045 | 135.4322 | 126.5993 | 146.506 | 147.1696 | 561.359 | 560.7958 | 562.9523 | 336.2688 | 335.9721 | 337.0229 | 338.0377 | 356.3516 | 358.2896 | 357.336 | 338.108 | 338.3261 | 339.5198 | 142.168 | 147.2795 | 143.7895 | 148.2225 | 742.0331 | 745.0422 | 748.0737 | 745.925 | 810.8357 | 815.9196 | 816.5062 | 821.6113 | 824.5786 | 830.4121 | 847.8718 | 851.2695 | 849.69 | 849.5426 | 851.4302 | 852.9516 | 852.2854 | 855.078 | 787.2941 | 788.0393 | 788.8548 | 868.8031 | 865.8954 | 869.0182 | 871.9533 | 871.6753 | 874.0589 | 805.4831 | 804.8007 | 808.0095 | 369.6438 | 370.2102 | 369.5724 | 784.2278 | 784.2737 | 785.754 | 870.3541 | 864.7612 | 864.4495 | 873.7675 | 874.2148 | 880.8346 | 807.4213 | 806.9046 | 807.5146 | 372.2224 | 373.9627 | 374.4374 | 348.2479 | 348.5775 | 348.6336 | 325.236 | 323.9818 | 324.5566 | 132.6938 | 133.7693 | 141.3747 | 151.4369 | 148.0857 | 149.2094 | 549.6542 | 551.7842 | 551.5222 | 589.0355 | 589.7337 | 589.5587 | 780.0139 | 780.1013 | 777.5005 | 859.0997 | 860.3626 | 859.9811 | 863.5574 | 863.8011 | 863.823 | 800.3355 | 803.6893 | 800.0833 | 364.995 | 363.9877 | 366.0042 | 859.5716 | 859.4268 | 858.4508 | 863.3998 | 866.7674 | 865.9582
273 | Econ Power
274
275 | LI comp Power | kw | 0.2376 | 0.23703 | 0.23751 | 0.24042 | 0.2386 | 0.23854 | 0.24177 | 0.2394 | 0.23993 | 0.24535 | 0.24617 | 0.24407 | 0.25184 | 0.25249 | 0.253 | 0.2177 | 0.2179 | 0.21842 | 0.21749 | 0.21672 | 0.21648 | 0.21697 | 0.21735 | 0.2186 | 0.21738 | 0.21823 | 0.21842 | 0.22233 | 0.2217 | 0.22242 | 0.22347 | 0.22344 | 0.22428 | 0.22391 | 0.22378 | 0.22382 | 0.22013 | 0.22058 | 0.22191 | 0.22014 | 0.22123 | 0.22171 | 0.2274 | 0.22918 | 0.22802 | 0.22838 | 0.22967 | 0.22845 | 0.22963 | 0.23883 | 0.23957 | 0.23809 | 0.24337 | 0.24396 | 0.24312 | 0.23888 | 0.2399 | 0.24002 | 0.23946 | 0.24204 | 0.24061 | 0.2303 | 0.23196 | 0.22974 | 0.23439 | 0.2322 | 0.23341 | 0.22629 | 0.22458 | 0.2272 | 0.2269 | 0.22606 | 0.22421 | 0.22624 | 0.22553 | 0.2254 | 0.21636 | 0.2177 | 0.21765 | 0.21903 | 0.21936 | 0.88912 | 0.22583 | 0.22417 | 0.2245 | 0.22259 | 0.22452 | 0.22415 | 0.22484 | 0.22469 | 0.22504 | 0.23423 | 0.23403 | 0.23425 | 0.23541 | 0.2329 | 0.23403 | 0.2347 | 0.24378 | 0.2434 | 0.24239 | 0.24314 | 0.24367 | 0.24447 | 0.24445 | 0.24313 | 0.24661 | 0.24695 | 0.24623 | 0.24379 | 0.24312 | 0.24429 | 0.24472 | 0.24465 | 0.24264 | 0.25417 | 0.25252 | 0.25366 | 0.24091 | 0.24104 | 0.23978 | 0.24204 | 0.24157 | 0.2424 | 0.23342 | 0.23418 | 0.23409 | 0.22652 | 0.22587 | 0.22593 | 0.22588 | 0.22339 | 0.24001 | 0.24109 | 0.2422 | 0.23094 | 0.23175 | 0.23271 | 0.23123 | 0.23246 | 0.23132 | 0.23277 | 0.23548 | 0.23482 | 0.23576 | 0.22795 | 0.22887 | 0.22972 | 0.2276 | 0.252 | 0.25231 | 0.25089 | 0.2523 | 0.25205 | 0.25458 | 0.25364 | 0.25836 | 0.25935 | 0.25889 | 0.25774 | 0.25719 | 0.25676 | 0.25511 | 0.25682 | 0.25626 | 0.25493 | 0.25427 | 0.2549 | 0.25555 | 0.25462 | 0.25218 | 0.25298 | 0.25269 | 0.25313 | 0.25295 | 0.25397 | 0.25107 | 0.25016 | 0.25079 | 0.23491 | 0.23351 | 0.2334 | 0.25784 | 0.25601 | 0.25756 | 0.2535 | 0.25329 | 0.25396 | 0.25374 | 0.25451 | 0.25548 | 0.25139 | 0.25235 | 0.25072 | 0.23365 | 0.2339 | 0.23434 | 0.23771 | 0.23939 | 0.23931 | 0.23903 | 0.23771 | 0.23684 | 0.23267 | 0.23217 | 0.23385 | 0.23345 | 0.23235 | 0.23174 | 0.24528 | 0.24492 | 0.2464 | 0.24594 | 0.24528 | 0.24502 | 0.26074 | 0.25995 | 0.2597 | 0.25562 | 0.2555 | 0.25549 | 0.25405 | 0.25552 | 0.25541 | 0.25621 | 0.25744 | 0.25726 | 0.23851 | 0.23787 | 0.23919 | 0.26515 | 0.26363 | 0.26485 | 0.26521 | 0.26422 | 0.26443
276
277
278 | Pressure Loss data
279 | Suction line PD
280 | Rig Data
281 | FCV01 Position |  | 36.9987 | 36.9987 | 36.9987 | 29.9996 | 29.9996 | 29.9996 | 15.9993 | 16.9997 | 16.9997 | 14.9989 | 14.9989 | 14.9989 | 14.9989 | 14.9989 | 14.9989 | 0.99861 | 0.99861 | 0.99861 | 0.99861 | 0.99861 | 0.99861 | 0.99861 | 0.99861 | 0.99861 | 0.99861 | 0.99861 | 0.99861 | 13 | 13 | 13 | 13 | 13 | 13 | 17.9982 | 17.9982 | 17.9982 | 17.9982 | 17.9982 | 17.9982 | 18.9986 | 17.9982 | 17.9982 | 4.9984 | 4.9984 | 4.9984 | 4.9984 | 7.9997 | 7.9997 | 7.9997 | 16.9997 | 16.9997 | 16.9997 | 7.9997 | 7.9997 | 7.9997 | 13.9984 | 13.9984 | 13.9984 | 13.9984 | 13 | 13 | 19.9991 | 19.9991 | 19.9991 | 19.9991 | 19.9991 | 19.9991 | 19.9991 | 19.9991 | 19.9991 | 10.9991 | 10.9991 | 10.9991 | 10.9991 | 10.9991 | 10.9991 | 7.9997 | 7.9997 | 7.9997 | 11.9995 | 11.9995 | 11.9995 | 3.9999 | 3.9999 | 3.9999 | 4.9984 | 4.9984 | 4.9984 | 4.9984 | 4.9984 | 4.9984 | 20.9995 | 20.9995 | 20.9995 | 24.9993 | 24.9993 | 24.9993 | 23.9989 | 19.9991 | 19.9991 | 19.9991 | 19.9991 | 19.9991 | 19.9991 | 19.9991 | 19.9991 | 10.9991 | 10.9991 | 10.9991 | 14.9989 | 14.9989 | 14.9989 | 14.9989 | 14.9989 | 14.9989 | 20.9995 | 20.9995 | 20.9995 | 2.9995 | 2.9995 | 2.9995 | 2.9995 | 2.9995 | 2.9995 | 2.9995 | 2.9995 | 2.9995 | 0.99861 | 0.99861 | 0.99861 | 0.99861 | 0.99861 | 16.9997 | 16.9997 | 16.9997 | 14.9989 | 14.9989 | 14.9989 | 14.9989 | 17.9982 | 17.9982 | 17.9982 | 17.9982 | 17.9982 | 17.9982 | 2.9995 | 2.9995 | 2.9995 | 2.9995 | 25.9998 | 25.9998 | 25.9998 | 25.9998 | 25.9998 | 23.9989 | 23.9989 | 26.9982 | 26.9982 | 27.9987 | 11.9995 | 11.9995 | 11.9995 | 11.9995 | 11.9995 | 11.9995 | 11.9995 | 11.9995 | 2.9995 | 2.9995 | 2.9995 | 14.9989 | 14.9989 | 14.9989 | 14.9989 | 14.9989 | 14.9989 | 11.9995 | 13 | 13 | 15.9993 | 15.9993 | 15.9993 | 11.9995 | 11.9995 | 11.9995 | 13.9984 | 13.9984 | 13.9984 | 17.9982 | 17.9982 | 17.9982 | 16.9997 | 16.9997 | 16.9997 | 16.9997 | 16.9997 | 16.9997 | 10.9991 | 10.9991 | 4.9984 | 9.9986 | 9.9986 | 9.9986 | 0.99861 | 0.99861 | 0.99861 | 0.99861 | 0.99861 | 0.99861 | 5.9988 | 5.9988 | 5.9988 | 8.9982 | 8.9982 | 8.9982 | 13 | 13 | 13 | 13.9984 | 13.9984 | 13.9984 | 13.9984 | 13.9984 | 13.9984 | 14.9989 | 14.9989 | 14.9989 | 19.9991 | 19.9991 | 19.9991 | 10.9991 | 10.9991 | 10.9991 | 11.9995 | 11.9995 | 11.9995
282 | FCV02 Position |  | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998
283 | TCV031 Position |  | 0.99835 | 0.99835 | 0.99835 | 3.9995 | 4.9999 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 2.9991 | 1.9987 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 4.9999 | 4.9999 | 4.9999 | 4.9999 | 4.9999 | 4.9999 | 6.9987 | 6.9987 | 5.9983 | 5.9983 | 5.9983 | 5.9983 | 6.9987 | 6.9987 | 6.9987 | 2.9991 | 1.9987 | 2.9991 | 1.9987 | 1.9987 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 2.9991 | 3.9995 | 0.99835 | 0.99835 | 1.9987 | 1.9987 | 1.9987 | 3.9995 | 0.99835 | 2.9991 | 10.9983 | 10.9983 | 9.9999 | 13.9995 | 11.9987 | 11.9987 | 12.9991 | 13.9995 | 12.9991 | 11.9987 | 11.9987 | 10.9983 | 10.9983 | 10.9983 | 10.9983 | 2.9991 | 1.9987 | 0.99835 | 0.99835 | 2.9991 | 0.99835 | 1.9987 | 1.9987 | 1.9987 | 3.9995 | 4.9999 | 4.9999 | 5.9983 | 5.9983 | 5.9983 | 2.9991 | 2.9991 | 2.9991 | 2.9991 | 2.9991 | 2.9991 | 3.9995 | 2.9991 | 2.9991 | 2.9991 | 2.9991 | 2.9991 | 2.9991 | 2.9991 | 2.9991 | 5.9983 | 5.9983 | 5.9983 | 5.9983 | 5.9983 | 5.9983 | 6.9987 | 6.9987 | 6.9987 | 7.9991 | 7.9991 | 7.9991 | 4.9999 | 5.9983 | 5.9983 | 5.9983 | 5.9983 | 5.9983 | 7.9991 | 7.9991 | 7.9991 | 2.9991 | 2.9991 | 2.9991 | 0.99835 | 0.99835 | 12.9991 | 12.9991 | 12.9991 | 8.9995 | 8.9995 | 8.9995 | 8.9995 | 8.9995 | 8.9995 | 8.9995 | 8.9995 | 8.9995 | 8.9995 | 11.9987 | 9.9999 | 4.9999 | 2.9991 | 4.9999 | 4.9999 | 2.9991 | 5.9983 | 6.9987 | 6.9987 | 8.9995 | 7.9991 | 6.9987 | 6.9987 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 1.9987 | 1.9987 | 1.9987 | 1.9987 | 2.9991 | 2.9991 | 1.9987 | 2.9991 | 0.99835 | 2.9991 | 2.9991 | 1.9987 | 2.9991 | 0.99835 | 0.99835 | 1.9987 | 0.99835 | 0.99835 | 0.99835 | 2.9991 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 1.9987 | 1.9987 | 1.9987 | 11.9987 | 11.9987 | 11.9987 | 10.9983 | 10.9983 | 10.9983 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 1.9987 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 1.9987 | 1.9987 | 0.99835 | 1.9987 | 1.9987 | 1.9987 | 0.99835 | 0.99835 | 0.99835
284
285 | Setpoint Suction Gauge | ºC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
286 | Setpoint Pressure Conversion Discharge | BarA | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928 | 2.928
287 | Setpoint Discharge Gauge | ºC | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
288 | Setpoint Pressure Conversion Discharge | BarA | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702 | 7.702
289
290 | Comp comcalc ID | - | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168
291
292
293 | Raw Data
294 | Copy of data from labview input - can be pasted into labview input cells to re-run log.
295 | Variable |  | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs | Labview Inputs
296 | a_Suction Pressure Comp (AI0) |  | 4.8908 | 4.8901 | 4.8736 | 4.1496 | 4.1497 | 4.1475 | 3.4835 | 3.5021 | 3.4986 | 2.9254 | 2.9281 | 2.9249 | 2.4361 | 2.4323 | 2.4294 | 3.8522 | 3.849 | 3.8449 | 3.8544 | 3.8588 | 3.8543 | 3.8415 | 3.8428 | 3.8523 | 3.8478 | 3.8524 | 3.8511 | 3.794 | 3.7928 | 3.7991 | 3.8074 | 3.807 | 3.8043 | 3.7863 | 3.7985 | 3.8009 | 3.7934 | 3.802 | 3.8037 | 3.8084 | 3.7946 | 3.8045 | 3.5977 | 3.5977 | 3.5913 | 3.5993 | 3.5952 | 3.6062 | 3.6023 | 3.3771 | 3.3717 | 3.3812 | 3.1083 | 3.1091 | 3.1114 | 3.3808 | 3.3763 | 3.378 | 3.3679 | 3.3725 | 3.377 | 3.5968 | 3.5873 | 3.5884 | 3.6017 | 3.5943 | 3.5891 | 3.7889 | 3.7995 | 3.794 | 3.7862 | 3.8072 | 3.807 | 3.811 | 3.7996 | 3.7987 | 3.8575 | 3.8547 | 3.8411 | 3.8506 | 3.8567 | 3.8494 | 3.799 | 3.8079 | 3.8029 | 3.7896 | 3.7916 | 3.8008 | 3.7998 | 3.7963 | 3.8064 | 3.6017 | 3.5936 | 3.5869 | 3.5897 | 3.5944 | 3.587 | 3.594 | 3.3789 | 3.3815 | 3.3771 | 3.3791 | 3.3818 | 3.3835 | 3.3868 | 3.3888 | 3.1203 | 3.1137 | 3.1083 | 3.3788 | 3.3818 | 3.3794 | 3.38 | 3.378 | 3.3809 | 3.1144 | 3.1155 | 3.1128 | 3.5974 | 3.5923 | 3.5883 | 3.5973 | 3.5935 | 3.5906 | 3.8027 | 3.8042 | 3.8035 | 3.8404 | 3.8418 | 3.8577 | 3.8611 | 3.8468 | 3.5918 | 3.5918 | 3.5974 | 3.7965 | 3.8012 | 3.7992 | 3.8079 | 3.7993 | 3.8028 | 3.8017 | 3.6002 | 3.591 | 3.6037 | 3.8266 | 3.857 | 3.8543 | 3.8554 | 3.3572 | 3.3671 | 3.3747 | 3.365 | 3.3672 | 3.383 | 3.3887 | 3.3732 | 3.3736 | 3.3916 | 3.3847 | 3.3921 | 3.3787 | 3.3781 | 3.3858 | 3.3898 | 3.3829 | 3.3872 | 3.1149 | 3.1188 | 3.1122 | 3.384 | 3.3732 | 3.3782 | 3.3736 | 3.369 | 3.3743 | 3.3834 | 3.3709 | 3.3776 | 3.803 | 3.8043 | 3.788 | 3.1147 | 3.116 | 3.1191 | 3.3869 | 3.3778 | 3.3733 | 3.37 | 3.3797 | 3.3825 | 3.3777 | 3.373 | 3.3691 | 3.79 | 3.8016 | 3.7897 | 3.8016 | 3.8004 | 3.7965 | 3.8041 | 3.7984 | 3.7979 | 3.852 | 3.8523 | 3.8661 | 3.8482 | 3.8472 | 3.844 | 3.5865 | 3.5939 | 3.5897 | 3.6003 | 3.5993 | 3.5985 | 3.1162 | 3.1087 | 3.1058 | 3.3819 | 3.3775 | 3.3687 | 3.3765 | 3.3746 | 3.3702 | 3.3889 | 3.3777 | 3.381 | 3.792 | 3.7928 | 3.7994 | 3.378 | 3.3731 | 3.3674 | 3.374 | 3.3809 | 3.3759
297 | b_subcooler temperature (AI1) |  | 34.7437 | 34.7346 | 34.4435 | 35.7236 | 35.7902 | 34.8252 | 35.2053 | 35.2009 | 35.0102 | 34.9789 | 35.2117 | 35.2204 | 34.9352 | 34.9488 | 34.945 | 17.8038 | 17.8312 | 17.7747 | 17.862 | 17.7672 | 17.5962 | 17.8976 | 17.8873 | 17.8279 | 17.8598 | 17.7811 | 17.677 | 20.6725 | 20.7017 | 20.7203 | 20.7251 | 20.761 | 20.7262 | 20.3731 | 20.4903 | 20.4128 | 20.2779 | 20.3769 | 19.9903 | 20.0466 | 20.0041 | 19.9343 | 28.1693 | 27.8892 | 28.0226 | 27.6953 | 27.5823 | 27.4823 | 27.444 | 34.6871 | 34.541 | 34.8198 | 35.6167 | 34.5773 | 35.0371 | 33.7364 | 33.6318 | 33.5283 | 33.3071 | 33.1562 | 33.5123 | 29.0021 | 28.9869 | 29.0149 | 29.0102 | 28.8169 | 28.7461 | 21.38 | 21.375 | 21.1908 | 21.3214 | 21.3547 | 21.3058 | 21.2804 | 21.1561 | 21.0461 | 17.2186 | 17.1122 | 17.0143 | 17.2088 | 17.2278 | 17.079 | 19.313 | 19.3444 | 19.2727 | 19.5562 | 19.5731 | 19.5359 | 19.641 | 19.6704 | 19.6941 | 27.3652 | 27.2356 | 27.238 | 26.8615 | 26.9966 | 26.8959 | 26.6132 | 34.1279 | 34.0904 | 34.1235 | 34.0809 | 34.1036 | 33.9928 | 33.9812 | 34.0222 | 34.4804 | 34.3391 | 34.4312 | 33.0054 | 32.8919 | 32.7878 | 32.5998 | 32.3773 | 32.1706 | 34.3243 | 34.448 | 34.3434 | 25.8604 | 26.0478 | 25.8512 | 25.5922 | 25.5837 | 25.4993 | 19.3921 | 19.3127 | 19.2213 | 16.2609 | 16.3237 | 16.4641 | 16.7296 | 16.4696 | 27.0216 | 26.8224 | 26.9503 | 18.9743 | 19.0189 | 18.9786 | 18.7989 | 18.5951 | 18.595 | 18.5008 | 17.9245 | 17.9224 | 17.8117 | 14.3898 | 14.334 | 14.3407 | 14.4527 | 32.2101 | 32.4764 | 32.144 | 32.5293 | 31.4977 | 31.3917 | 31.6605 | 30.8659 | 31.3142 | 30.666 | 35.0574 | 35.1961 | 34.9777 | 34.8514 | 34.4416 | 34.624 | 34.4875 | 34.1503 | 35.3256 | 35.5907 | 35.7076 | 34.4023 | 34.1469 | 34.2401 | 33.8044 | 33.8787 | 34.0404 | 35.5448 | 35.5852 | 35.1979 | 19.8947 | 19.7594 | 19.6051 | 36.6178 | 36.3798 | 36.359 | 34.0754 | 33.9537 | 33.7652 | 34.7419 | 34.6066 | 34.736 | 35.5194 | 35.5097 | 35.4311 | 20.0211 | 19.9949 | 19.9039 | 22.063 | 21.8672 | 21.9719 | 21.9546 | 21.8406 | 21.8592 | 18.8304 | 18.8767 | 18.8597 | 19.0283 | 19.0492 | 18.9425 | 30.0631 | 29.7971 | 29.9067 | 29.4712 | 29.3586 | 29.3106 | 37.4451 | 37.1653 | 37.0418 | 35.7082 | 35.69 | 35.5846 | 34.673 | 34.7085 | 34.6919 | 37.3191 | 37.2599 | 37.2178 | 21.3508 | 21.2377 | 21.0307 | 35.9837 | 35.9584 | 35.9104 | 36.6502 | 37.0727 | 37.0964
298 | c_Suction Flowmeter Pressure Low Duty (AI2) |  | 4.9708 | 4.973 | 4.9592 | 4.0623 | 4.0557 | 4.0578 | 3.2255 | 3.265 | 3.2544 | 2.542 | 2.5418 | 2.5323 | 1.9205 | 1.9166 | 1.9156 | 3.2144 | 3.2126 | 3.2078 | 3.2197 | 3.2256 | 3.2189 | 3.2077 | 3.208 | 3.216 | 3.2138 | 3.2198 | 3.218 | 3.193 | 3.1891 | 3.193 | 3.2044 | 3.2044 | 3.2038 | 3.1873 | 3.2019 | 3.204 | 3.1965 | 3.2057 | 3.2087 | 3.2204 | 3.2006 | 3.2155 | 3.0641 | 3.0632 | 3.0573 | 3.0683 | 3.0882 | 3.0987 | 3.0947 | 3.0248 | 3.0186 | 3.0313 | 2.7494 | 2.7501 | 2.7577 | 3.0989 | 3.1041 | 3.0992 | 3.0848 | 3.0899 | 3.0942 | 3.0727 | 3.06 | 3.0603 | 3.0945 | 3.0878 | 3.0809 | 3.2053 | 3.2166 | 3.21 | 3.1886 | 3.2126 | 3.212 | 3.2155 | 3.2064 | 3.2007 | 3.2369 | 3.2348 | 3.2174 | 3.2337 | 3.2385 | 3.2305 | 3.2028 | 3.212 | 3.2094 | 3.1978 | 3.2001 | 3.2076 | 3.2092 | 3.2036 | 3.2157 | 3.0763 | 3.068 | 3.0585 | 3.0754 | 3.0792 | 3.0739 | 3.0786 | 3.0073 | 3.0076 | 3.0086 | 3.0084 | 3.0111 | 3.0141 | 3.0183 | 3.0171 | 2.745 | 2.7292 | 2.729 | 3.07 | 3.0767 | 3.0753 | 3.0782 | 3.0729 | 3.0808 | 2.7598 | 2.7619 | 2.7587 | 3.0688 | 3.0675 | 3.062 | 3.0756 | 3.0748 | 3.0696 | 3.2071 | 3.2113 | 3.2084 | 3.2148 | 3.2181 | 3.234 | 3.2416 | 3.2224 | 3.0962 | 3.095 | 3.1043 | 3.2137 | 3.2166 | 3.2115 | 3.2218 | 3.218 | 3.2217 | 3.2207 | 2.9934 | 2.9848 | 2.9987 | 3.2065 | 3.2435 | 3.2371 | 3.2397 | 2.9956 | 3.0077 | 3.0161 | 3.0026 | 3.0773 | 3.0921 | 3.0974 | 3.0677 | 3.0686 | 3.097 | 3.0909 | 3.0972 | 3.0816 | 3.0806 | 3.0901 | 3.0977 | 3.0893 | 3.0904 | 2.7885 | 2.7941 | 2.7919 | 3.1262 | 3.1142 | 3.1206 | 3.1139 | 3.1093 | 3.1122 | 3.0545 | 3.0412 | 3.0547 | 3.2157 | 3.2148 | 3.1985 | 2.7886 | 2.7911 | 2.7915 | 3.1299 | 3.1183 | 3.1119 | 3.1123 | 3.1244 | 3.1301 | 3.0591 | 3.0508 | 3.0517 | 3.2046 | 3.2148 | 3.2056 | 3.2086 | 3.2045 | 3.1996 | 3.2031 | 3.1967 | 3.1979 | 3.2167 | 3.2171 | 3.2349 | 3.2104 | 3.2193 | 3.2139 | 3.0679 | 3.0746 | 3.0698 | 3.1023 | 3.1049 | 3.1068 | 2.7722 | 2.7688 | 2.7681 | 3.1068 | 3.1079 | 3.0905 | 3.0999 | 3.1032 | 3.0962 | 3.0614 | 3.0466 | 3.0483 | 3.2016 | 3.1953 | 3.207 | 3.108 | 3.1059 | 3.1008 | 3.1078 | 3.1133 | 3.1087
299 | d_subcooler pressure (AI3) |  | 11.462 | 11.4578 | 11.4155 | 11.6605 | 11.6778 | 11.6504 | 11.8228 | 11.7943 | 11.74 | 11.8652 | 11.8716 | 11.9032 | 11.933 | 11.926 | 11.9142 | 5.6897 | 5.6955 | 5.7006 | 5.7287 | 5.6967 | 5.6709 | 5.7066 | 5.7098 | 5.7124 | 5.731 | 5.6973 | 5.6893 | 6.7715 | 6.7947 | 6.8021 | 6.8007 | 6.8142 | 6.8087 | 6.7846 | 6.8162 | 6.793 | 6.8012 | 6.8174 | 6.8441 | 6.7922 | 6.8492 | 6.8444 | 8.9997 | 8.9768 | 9.0033 | 8.9655 | 9.0244 | 9.0466 | 8.9618 | 11.4729 | 11.4601 | 11.5025 | 11.9066 | 11.8549 | 11.8675 | 11.4273 | 11.427 | 11.408 | 11.2301 | 11.2201 | 11.262 | 9.0002 | 8.9912 | 8.9998 | 8.9588 | 8.9705 | 8.945 | 6.8293 | 6.8588 | 6.8315 | 6.8095 | 6.8421 | 6.8413 | 6.8431 | 6.8356 | 6.8237 | 5.7206 | 5.7275 | 5.6903 | 5.6971 | 5.711 | 5.6866 | 6.8125 | 6.8522 | 6.8078 | 6.7626 | 6.77 | 6.7819 | 6.7988 | 6.8022 | 6.8017 | 9.0113 | 8.9963 | 8.9771 | 8.9626 | 8.9822 | 8.9664 | 8.9854 | 11.4843 | 11.494 | 11.498 | 11.4855 | 11.4912 | 11.4775 | 11.4744 | 11.4901 | 11.8758 | 11.8536 | 11.8333 | 11.4984 | 11.4629 | 11.431 | 11.3023 | 11.2416 | 11.2163 | 11.8745 | 11.9031 | 11.8864 | 9.0023 | 9.0112 | 9.0542 | 9.0087 | 9.0116 | 8.9993 | 6.8374 | 6.8495 | 6.844 | 5.712 | 5.7267 | 5.7522 | 5.7803 | 5.7265 | 8.9801 | 8.9797 | 8.9886 | 6.8241 | 6.8348 | 6.8364 | 6.8536 | 6.8437 | 6.8274 | 6.827 | 6.7996 | 6.8156 | 6.8082 | 5.7817 | 5.7942 | 5.7731 | 5.7527 | 11.4817 | 11.5341 | 11.5583 | 11.5418 | 11.5023 | 11.4757 | 11.4747 | 11.3068 | 11.3099 | 11.3014 | 11.4212 | 11.4423 | 11.4114 | 11.4291 | 11.3004 | 11.3327 | 11.293 | 11.2133 | 11.7399 | 11.7918 | 11.7959 | 11.3982 | 11.3621 | 11.3688 | 11.1791 | 11.1387 | 11.165 | 11.5077 | 11.4343 | 11.4395 | 6.8513 | 6.8671 | 6.8044 | 11.846 | 11.8669 | 11.8384 | 11.2524 | 11.2022 | 11.2043 | 11.4026 | 11.381 | 11.3853 | 11.4312 | 11.4322 | 11.4122 | 6.8499 | 6.8611 | 6.8051 | 6.853 | 6.8037 | 6.8398 | 6.8245 | 6.805 | 6.7943 | 5.7221 | 5.7085 | 5.7126 | 5.7464 | 5.7349 | 5.7088 | 9.0045 | 8.9505 | 8.9488 | 8.95 | 8.967 | 8.9314 | 11.8867 | 11.844 | 11.8593 | 11.4539 | 11.4566 | 11.4067 | 11.2584 | 11.1924 | 11.2158 | 11.5392 | 11.4829 | 11.4669 | 6.7814 | 6.8403 | 6.7769 | 11.2346 | 11.2337 | 11.2237 | 11.4266 | 11.4815 | 11.5007
300 | e_Suction Flow Low Duty (AI4) |  | 337.5 | 337.5 | 62.8112 | 337.5 | 63.7369 | 337.5 | 62.4118 | 61.5254 | 337.5 | 337.5 | 337.5 | 61.8859 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 61.5412 | 337.5 | 337.5 | 337.5 | 62.2787 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 253.6056 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 62.662 | 61.1592 | 337.5 | 61.3157 | 337.5 | 337.5 | 62.1509 | 337.5 | 62.0331 | 59.8879 | 52.3908 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 284.6359 | 337.5 | 337.5 | 61.4666 | 337.5 | 337.5 | 337.5 | 63.271 | 337.5 | 337.5 | 337.5 | 79.3762 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 62.6372 | 337.5 | 337.5 | 337.5 | 337.5 | 34.8992 | 63.7147 | 337.5 | 337.5 | 337.5 | 283.0505 | 337.5 | 63.5516 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 327.8145 | 61.6379 | 62.2928 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 279.7698 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 61.9268 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 62.8289 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 280.1211 | 337.5 | 53.2033 | 337.5 | 286.7679 | 337.5 | 337.5 | 337.5 | 337.5 | 62.6991 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 61.0153 | 337.5 | 337.5 | 337.5 | 62.0509 | 307.1505 | 337.5 | 337.5 | 62.5315 | 337.5 | 23.8928 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 63.0696 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 311.0876 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 57.5395 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 337.5 | 62.3779 | 62.5444 | 337.5 | 62.3906 | 337.5 | 337.5 | 337.5 | 61.4216 | 337.5 | 337.5 | 337.5 | 337.5 | 69.6895 | 337.5 | 63.3226 | 63.5784 | 337.5 | 337.5 | 337.5
301 | f_Suction Flowmeter Pressure High Duty (AI5) |  | 5.3465 | 5.3435 | 5.3306 | 4.5366 | 4.5336 | 4.5386 | 3.8009 | 3.8276 | 3.8271 | 3.1977 | 3.1955 | 3.1905 | 2.6482 | 2.6454 | 2.6426 | 3.8526 | 3.8548 | 3.8485 | 3.8596 | 3.8628 | 3.8606 | 3.8483 | 3.8481 | 3.8569 | 3.8537 | 3.858 | 3.8589 | 3.8278 | 3.8266 | 3.8305 | 3.841 | 3.8421 | 3.8385 | 3.8251 | 3.8366 | 3.8408 | 3.8319 | 3.8415 | 3.841 | 3.8509 | 3.838 | 3.8494 | 3.6973 | 3.6963 | 3.6891 | 3.701 | 3.7151 | 3.7253 | 3.7211 | 3.6289 | 3.6234 | 3.6389 | 3.3801 | 3.3824 | 3.3861 | 3.6875 | 3.6855 | 3.6878 | 3.6741 | 3.6806 | 3.6871 | 3.7034 | 3.6923 | 3.6945 | 3.7203 | 3.714 | 3.7085 | 3.838 | 3.8489 | 3.8445 | 3.8266 | 3.8474 | 3.8475 | 3.8504 | 3.8402 | 3.8378 | 3.8766 | 3.8707 | 3.8579 | 3.8729 | 3.8773 | 3.8707 | 3.8401 | 3.8472 | 3.8453 | 3.8317 | 3.8354 | 3.8423 | 3.8442 | 3.84 | 3.8494 | 3.7088 | 3.6999 | 3.6933 | 3.7075 | 3.7073 | 3.705 | 3.7095 | 3.6166 | 3.6173 | 3.6182 | 3.6183 | 3.6219 | 3.6229 | 3.6276 | 3.626 | 3.3766 | 3.3696 | 3.3647 | 3.6655 | 3.6717 | 3.6681 | 3.6711 | 3.6699 | 3.6726 | 3.3914 | 3.3951 | 3.3922 | 3.7038 | 3.7028 | 3.6968 | 3.706 | 3.7068 | 3.7008 | 3.8443 | 3.8449 | 3.846 | 3.8561 | 3.8584 | 3.8732 | 3.8782 | 3.8653 | 3.7247 | 3.7226 | 3.7296 | 3.8468 | 3.8505 | 3.847 | 3.8552 | 3.8521 | 3.8563 | 3.8524 | 3.6494 | 3.6417 | 3.6543 | 3.8501 | 3.8812 | 3.8781 | 3.8795 | 3.6076 | 3.6189 | 3.6282 | 3.6153 | 3.6727 | 3.6845 | 3.6905 | 3.6679 | 3.6665 | 3.6912 | 3.6817 | 3.6906 | 3.6771 | 3.6759 | 3.6839 | 3.6895 | 3.6808 | 3.686 | 3.4138 | 3.416 | 3.4132 | 3.7119 | 3.6981 | 3.705 | 3.7002 | 3.6967 | 3.6994 | 3.6569 | 3.6451 | 3.6564 | 3.8468 | 3.8471 | 3.833 | 3.4136 | 3.4147 | 3.4154 | 3.7124 | 3.7009 | 3.6995 | 3.6977 | 3.7083 | 3.7157 | 3.6591 | 3.6511 | 3.6491 | 3.8374 | 3.8464 | 3.8401 | 3.8424 | 3.8403 | 3.8358 | 3.8416 | 3.8331 | 3.8347 | 3.8566 | 3.8593 | 3.8737 | 3.8539 | 3.8544 | 3.8526 | 3.6984 | 3.7057 | 3.704 | 3.7281 | 3.7293 | 3.728 | 3.3997 | 3.3977 | 3.395 | 3.6944 | 3.6901 | 3.6801 | 3.6926 | 3.6883 | 3.6831 | 3.6604 | 3.6516 | 3.6532 | 3.8359 | 3.8301 | 3.8405 | 3.6934 | 3.6947 | 3.687 | 3.693 | 3.7021 | 3.6962
302 | g_Spare6 (AI6) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
303 | h_Suction Flow High Duty (AI7) |  | 1151.4805 | 1152.8279 | 1152.0968 | 1151.4604 | 1154.0277 | 1147.5392 | 1142.2198 | 1144.5347 | 1143.7614 | 1127.7631 | 1131.9011 | 1133.7521 | 1125.7011 | 1125.3593 | 1124.7775 | 170.4691 | 170.7793 | 173.1454 | 185.5478 | 185.3106 | 182.0024 | 173.6105 | 179.6716 | 175.2181 | 186.2916 | 190.8848 | 189.2306 | 405.5737 | 406.1605 | 406.501 | 405.8454 | 405.5364 | 404.5136 | 438.866 | 437.9952 | 440.3912 | 441.9586 | 439.6614 | 437.6309 | 460.2157 | 459.3186 | 458.4065 | 709.7458 | 708.8906 | 708.9545 | 721.6864 | 763.8997 | 761.9131 | 763.2113 | 1069.3069 | 1070.9042 | 1068.5406 | 1140.6536 | 1137.8028 | 1140.7737 | 1141.7769 | 1138.8727 | 1136.4648 | 1139.9488 | 1141.6015 | 1143.08 | 708.5533 | 708.239 | 708.9824 | 753.3499 | 754.6669 | 753.9793 | 459.6092 | 459.1117 | 458.4765 | 402.5823 | 402.5339 | 405.1102 | 404.9291 | 403.8661 | 404.6599 | 179.8175 | 180.006 | 180.6444 | 192.8903 | 193.2239 | 196.0088 | 402.7638 | 402.2725 | 402.9232 | 432.2026 | 432.5648 | 432.9053 | 431.5543 | 433.2524 | 432.0915 | 717.0727 | 716.8703 | 717.2743 | 752.582 | 752.1472 | 750.0536 | 744.4851 | 1058.93 | 1061.3358 | 1060.2397 | 1059.7164 | 1057.6105 | 1057.1208 | 1059.3345 | 1060.6859 | 1120.7046 | 1122.7851 | 1125.4913 | 1126.2432 | 1125.8052 | 1122.9724 | 1128.7409 | 1127.6508 | 1125.5224 | 1094.5429 | 1094.4888 | 1094.2393 | 682.6334 | 679.5682 | 680.3845 | 695.7665 | 697.6081 | 696.4332 | 389.4074 | 389.6914 | 388.8562 | 163.5925 | 166.9995 | 155.5166 | 179.5908 | 180.9583 | 735.1244 | 734.6323 | 734.4339 | 421.724 | 421.0643 | 422.7079 | 422.476 | 444.7665 | 446.4117 | 445.5893 | 444.5517 | 445.6618 | 445.5565 | 175.3381 | 180.2559 | 176.42 | 182.0249 | 1032.9634 | 1033.6461 | 1034.0407 | 1036.3232 | 1100.9827 | 1103.1869 | 1101.1818 | 1107.5314 | 1112.7848 | 1109.5549 | 1106.4373 | 1107.5957 | 1107.953 | 1106.9884 | 1107.5945 | 1107.8572 | 1108.7734 | 1107.5527 | 1138.231 | 1138.4527 | 1142.0461 | 1141.9203 | 1141.2077 | 1141.1278 | 1145.9468 | 1145.4018 | 1146.4713 | 1066.1123 | 1071.2948 | 1069.3823 | 457.3374 | 457.0021 | 458.2307 | 1135.4609 | 1134.0225 | 1134.7348 | 1144.781 | 1140.8975 | 1140.9929 | 1147.2442 | 1141.9289 | 1147.5331 | 1068.0927 | 1069.1057 | 1069.6966 | 458.1127 | 459.1281 | 460.5906 | 432.0657 | 432.1927 | 432.6537 | 402.8876 | 402.368 | 402.4024 | 165.5452 | 166.7393 | 175.6701 | 189.3809 | 185.1499 | 186.6649 | 721.4893 | 722.4118 | 722.2458 | 763.2945 | 764.0845 | 765.0877 | 1133.5116 | 1132.8965 | 1126.0625 | 1134.0115 | 1136.7857 | 1137.393 | 1134.7679 | 1137.4385 | 1134.6126 | 1063.7015 | 1072.4233 | 1068.1636 | 455.8056 | 454.8754 | 455.8404 | 1141.5298 | 1139.8152 | 1139.1977 | 1141.3384 | 1142.9751 | 1143.4111
304 | i_Suction Orifice Meter Pressure (AI8) |  | 5.216 | 5.2182 | 5.1985 | 4.4265 | 4.426 | 4.4279 | 3.7075 | 3.7354 | 3.7322 | 3.1181 | 3.1164 | 3.1118 | 2.5861 | 2.5828 | 2.5799 | 3.8566 | 3.8564 | 3.8503 | 3.8623 | 3.8631 | 3.8596 | 3.8487 | 3.8484 | 3.8559 | 3.8528 | 3.8599 | 3.86 | 3.8239 | 3.8214 | 3.8248 | 3.8339 | 3.8354 | 3.8331 | 3.8163 | 3.8294 | 3.833 | 3.8248 | 3.8342 | 3.8347 | 3.8437 | 3.8285 | 3.8413 | 3.6717 | 3.6699 | 3.6662 | 3.6728 | 3.681 | 3.69 | 3.6895 | 3.5548 | 3.5498 | 3.5606 | 3.301 | 3.3016 | 3.3031 | 3.5973 | 3.5954 | 3.5964 | 3.58 | 3.5867 | 3.5951 | 3.6758 | 3.6644 | 3.6705 | 3.6877 | 3.6863 | 3.6779 | 3.8293 | 3.8382 | 3.8343 | 3.8213 | 3.8409 | 3.8422 | 3.8433 | 3.8336 | 3.8282 | 3.8756 | 3.8735 | 3.856 | 3.8731 | 3.8784 | 3.8715 | 3.8344 | 3.8415 | 3.8397 | 3.8255 | 3.8266 | 3.8332 | 3.8361 | 3.8331 | 3.8404 | 3.6831 | 3.6728 | 3.6675 | 3.6826 | 3.6794 | 3.6735 | 3.6803 | 3.5481 | 3.5496 | 3.5505 | 3.5514 | 3.5526 | 3.5538 | 3.5599 | 3.5616 | 3.3022 | 3.2934 | 3.2919 | 3.5812 | 3.5881 | 3.5827 | 3.5863 | 3.5838 | 3.5866 | 3.3081 | 3.3152 | 3.3094 | 3.6831 | 3.6812 | 3.6711 | 3.6819 | 3.682 | 3.678 | 3.8382 | 3.8405 | 3.8411 | 3.8554 | 3.8625 | 3.8756 | 3.8783 | 3.8683 | 3.6928 | 3.688 | 3.6981 | 3.8405 | 3.8409 | 3.8385 | 3.8478 | 3.8444 | 3.849 | 3.8462 | 3.6404 | 3.6361 | 3.6467 | 3.8491 | 3.8824 | 3.8803 | 3.881 | 3.5336 | 3.5451 | 3.5526 | 3.5419 | 3.5812 | 3.5953 | 3.5991 | 3.5806 | 3.5825 | 3.6027 | 3.5932 | 3.5989 | 3.5887 | 3.5867 | 3.5919 | 3.598 | 3.5949 | 3.5978 | 3.3181 | 3.3226 | 3.3133 | 3.6081 | 3.5952 | 3.6013 | 3.5956 | 3.5958 | 3.599 | 3.5679 | 3.5541 | 3.567 | 3.8387 | 3.8398 | 3.8213 | 3.319 | 3.3222 | 3.3213 | 3.6086 | 3.599 | 3.598 | 3.5944 | 3.6047 | 3.6118 | 3.5723 | 3.5622 | 3.5611 | 3.832 | 3.8366 | 3.8303 | 3.837 | 3.8328 | 3.8283 | 3.8341 | 3.8272 | 3.8319 | 3.859 | 3.8605 | 3.8767 | 3.8528 | 3.8544 | 3.8517 | 3.6691 | 3.6747 | 3.6724 | 3.6921 | 3.6929 | 3.694 | 3.3126 | 3.306 | 3.3061 | 3.5963 | 3.5948 | 3.5821 | 3.5941 | 3.5918 | 3.5857 | 3.576 | 3.5635 | 3.5706 | 3.8283 | 3.8228 | 3.8324 | 3.5924 | 3.5943 | 3.5849 | 3.5937 | 3.6008 | 3.5953
305 | j_Differential pressure_keller (AI9) |  | 124.9364 | 131.35 | 126.2434 | 108.0124 | 107.7301 | 112.2508 | 78.3955 | 83.7058 | 81.3998 | 52.2686 | 56.2395 | 60.5593 | 39.9584 | 39.3529 | 46.2643 | -27.8349 | -27.7782 | -27.8952 | -24.655 | -24.8899 | -25.46 | -39.4644 | -40.6683 | -38.1206 | -37.5194 | -37.9955 | -37.7703 | -42.8811 | -43.3355 | -44.0979 | -43.4322 | -43.296 | -44.3839 | -41.8767 | -42.5915 | -39.8537 | -40.9002 | -41.1469 | -42.255 | -40.2659 | -38.3968 | -39.207 | -20.5057 | -20.7455 | -19.0854 | -18.116 | -12.8726 | -13.6361 | -12.8364 | 42.8707 | 43.7581 | 41.4358 | 43.9897 | 41.7788 | 49.8202 | 74.3575 | 75.1961 | 77.5187 | 78.238 | 86.044 | 91.3751 | 11.4237 | 11.2712 | 11.116 | 26.7362 | 26.8795 | 30.243 | 23.5601 | 23.8764 | 23.4327 | 19.4411 | 19.3321 | 19.5496 | 19.6763 | 19.4346 | 19.1448 | -41.1048 | -39.229 | -40.2851 | -33.653 | -32.236 | -31.7316 | -44.2682 | -44.1651 | -44.208 | -41.3113 | -42.2265 | -40.9873 | -41.7795 | -41.8862 | -41.4374 | -11.7218 | -13.2601 | -12.5922 | -7.4391 | -8.5503 | -7.8958 | -10.7588 | 46.1296 | 49.1754 | 51.2038 | 53.992 | 54.408 | 52.5981 | 50.9724 | 50.5157 | 53.2873 | 54.3793 | 55.519 | 74.1703 | 75.7378 | 73.8866 | 75.876 | 74.0134 | 74.2967 | 63.1563 | 56.5162 | 60.2441 | -12.1231 | -9.1849 | -11.2451 | -9.4513 | -9.2282 | -9.319 | -42.1316 | -42.0512 | -41.508 | -51.2782 | -51.2166 | -50.8276 | -51.2353 | -51.4977 | -5.309 | -4.9317 | -6.027 | -37.4659 | -37.391 | -38.116 | -37.6995 | -35.2035 | -35.1451 | -35.172 | -37.871 | -37.9693 | -38.9195 | -49.2944 | -51.4884 | -52.0011 | -52.2686 | 49.6988 | 50.0217 | 51.5566 | 47.7059 | 68.0981 | 66.9529 | 68.1724 | 66.6396 | 68.4361 | 68.0013 | 79.0247 | 80.1724 | 78.0239 | 77.3604 | 77.5338 | 79.1872 | 79.7761 | 78.6354 | 75.5917 | 77.6488 | 76.9624 | 107.0174 | 104.939 | 109.412 | 108.2745 | 104.9177 | 110.4504 | 87.8408 | 89.4283 | 89.2542 | 14.4046 | 14.8704 | 14.4734 | 73.0744 | 73.3379 | 72.7526 | 102.1218 | 99.8221 | 101.3964 | 82.0104 | 88.6669 | 95.2842 | 84.5304 | 83.3904 | 82.702 | 21.4992 | 21.0842 | 19.5993 | 13.0339 | 12.8718 | 14.2854 | 17.9867 | 17.6517 | 16.6618 | -37.5477 | -36.8685 | -36.8109 | -37.7457 | -37.7216 | -36.9524 | 45.8257 | 44.1498 | 46.2135 | 53.1608 | 53.6882 | 52.3774 | 58.6279 | 63.9108 | 74.0172 | 55.0864 | 57.583 | 60.4757 | 66.7685 | 67.5161 | 63.0096 | 107.6746 | 107.8072 | 106.0458 | -7.2758 | -9.8827 | -7.3511 | 65.0066 | 68.452 | 66.9939 | 74.8069 | 67.6929 | 68.6795
306 | k_Suction Diff Pressure (AI10) |  | 323.2773 | 325.4291 | 322.0993 | 270.6982 | 273.5318 | 273.1486 | 224.3841 | 226.8361 | 229.2083 | 186.1282 | 188.184 | 185.5767 | 151.7925 | 151.7388 | 150.665 | 1.3097 | 1.674 | 1.5389 | 2.2373 | 1.982 | 2.2151 | 1.6721 | 1.5708 | 1.6275 | 2.2243 | 2.2516 | 2.3649 | 23.9647 | 23.8745 | 24.1535 | 23.9946 | 24.2287 | 23.9784 | 28.3516 | 28.7205 | 28.7446 | 28.5867 | 28.8264 | 28.9657 | 32.4752 | 32.4983 | 32.6608 | 80.9685 | 80.4602 | 81.1306 | 82.5922 | 92.7642 | 92.7023 | 92.6066 | 187.6478 | 186.9884 | 187.976 | 199.4122 | 199.897 | 199.1162 | 219.1486 | 220.8378 | 218.5636 | 217.5305 | 217.2101 | 218.5795 | 79.8628 | 79.2624 | 79.6515 | 89.5666 | 89.0704 | 88.9981 | 31.0156 | 30.5822 | 30.9036 | 22.9183 | 22.818 | 23.0146 | 23.1846 | 23.0049 | 22.6776 | 1.6981 | 1.6955 | 1.8036 | 2.7025 | 2.6085 | 2.7387 | 23.3978 | 23.4844 | 23.4356 | 27.7894 | 27.7675 | 28.393 | 28.2084 | 27.9007 | 28.0143 | 81.7623 | 82.0445 | 81.8173 | 91.2603 | 89.7492 | 89.8254 | 86.746 | 179.0383 | 179.583 | 179.664 | 180.9687 | 179.2053 | 179.6663 | 179.2186 | 180.6522 | 191.7625 | 191.5935 | 191.1097 | 209.5718 | 209.675 | 211.0695 | 210.5388 | 210.2152 | 211.497 | 183.9637 | 184.935 | 184.1161 | 74.1054 | 74.3359 | 74.2546 | 75.61 | 75.6386 | 76.1941 | 21.5537 | 21.3326 | 21.1526 | 1.2244 | 1.4253 | 1.3989 | 1.7453 | 2.0865 | 86.2212 | 85.4827 | 85.6452 | 25.9342 | 26.4164 | 26.4108 | 26.4385 | 29.8578 | 29.7686 | 29.6787 | 27.3374 | 27.1385 | 27.5139 | 1.9117 | 1.8941 | 1.8606 | 1.8466 | 170.3776 | 171.9033 | 171.0744 | 171.6025 | 201.3058 | 202.6124 | 201.8391 | 200.2897 | 200.9652 | 201.5061 | 200.7868 | 201.8515 | 200.0367 | 200.6286 | 199.9383 | 201.6509 | 200.2157 | 201.3455 | 192.5661 | 192.1864 | 192.6156 | 214.0819 | 211.4244 | 211.8216 | 210.7527 | 211.1096 | 210.1364 | 179.8359 | 178.9393 | 181.5336 | 30.5956 | 30.5311 | 30.928 | 194.3187 | 194.8563 | 195.2655 | 215.2247 | 213.4955 | 214.481 | 213.8325 | 213.2737 | 213.851 | 182.0441 | 180.9149 | 180.9762 | 31.2741 | 31.0827 | 31.643 | 28.2064 | 27.6692 | 27.5663 | 23.5541 | 22.9075 | 23.2396 | 1.2654 | 1.2836 | 1.55 | 1.8736 | 2.0917 | 2.1546 | 82.7042 | 82.1155 | 81.4888 | 91.9118 | 92.3175 | 91.9847 | 194.9318 | 195.6006 | 196.4679 | 215.1084 | 216.1721 | 214.3456 | 214.4257 | 215.2081 | 214.3566 | 181.221 | 180.1475 | 181.7608 | 31.3086 | 30.9101 | 31.3611 | 213.419 | 212.7942 | 211.3186 | 212.3947 | 212.4331 | 212.7782
307 | l_Spare (AI11) |  | -0.003638 | -0.003716 | -0.003696 | -0.003698 | -0.003641 | -0.003658 | -0.003481 | -0.003515 | -0.003601 | -0.00339 | -0.003386 | -0.003413 | -0.00334 | -0.003425 | -0.003459 | 0.0024 | 0.002446 | 0.002389 | 0.002238 | 0.002355 | 0.002334 | 0.002063 | 0.002025 | 0.001903 | 0.001748 | 0.00152 | 0.001772 | -0.003833 | -0.004015 | -0.003997 | -0.003928 | -0.004032 | -0.004057 | -0.004011 | -0.003915 | -0.004031 | -0.004075 | -0.00407 | -0.004018 | -0.004062 | -0.004085 | -0.003936 | -0.00405 | -0.003987 | -0.004059 | -0.004064 | -0.003926 | -0.004031 | -0.004085 | -0.003814 | -0.003901 | -0.003844 | -0.003846 | -0.00374 | -0.00385 | -0.003636 | -0.003503 | -0.003652 | -0.003377 | -0.003425 | -0.003476 | -0.003964 | -0.004101 | -0.00406 | -0.004015 | -0.003903 | -0.003871 | -0.003902 | -0.004061 | -0.004073 | -0.003981 | -0.00408 | -0.003983 | -0.003647 | -0.003697 | -0.003797 | -0.002994 | -0.003814 | -0.003802 | -0.003855 | -0.003614 | -0.003618 | -0.003997 | -0.004024 | -0.004103 | -0.004089 | -0.004088 | -0.004075 | -0.0041 | -0.004095 | -0.004094 | -0.004049 | -0.003982 | -0.003946 | -0.004015 | -0.004097 | -0.003977 | -0.004006 | -0.003866 | -0.003883 | -0.003928 | -0.004047 | -0.004055 | -0.004141 | -0.00386 | -0.003867 | -0.003881 | -0.003756 | -0.003929 | -0.003617 | -0.003612 | -0.003509 | -0.003567 | -0.003456 | -0.003492 | -0.003926 | -0.004055 | -0.003996 | -0.003848 | -0.003888 | -0.003694 | -0.003799 | -0.003816 | -0.003851 | -0.003693 | -0.003756 | -0.003719 | -0.00363 | -0.003548 | -0.003597 | -0.003629 | -0.003566 | -0.00408 | -0.003829 | -0.004061 | -0.003951 | -0.003765 | -0.003781 | -0.003735 | -0.003795 | -0.00378 | -0.003838 | -0.003707 | -0.003752 | -0.003824 | -0.003608 | -0.003602 | -0.003634 | -0.003554 | -0.003822 | -0.00383 | -0.003744 | -0.003837 | -0.003792 | -0.003814 | -0.003814 | -0.003721 | -0.003794 | -0.003723 | -0.004021 | -0.00405 | -0.003947 | -0.003973 | -0.003955 | -0.004024 | -0.004003 | -0.004008 | -0.003798 | -0.003946 | -0.003973 | -0.003882 | -0.00386 | -0.003891 | -0.003911 | -0.003874 | -0.003747 | -0.003879 | -0.003868 | -0.003896 | -0.003598 | -0.003583 | -0.00359 | -0.003945 | -0.003954 | -0.00393 | -0.003865 | -0.003909 | -0.003793 | -0.003898 | -0.003821 | -0.003856 | -0.003925 | -0.003861 | -0.003746 | -0.00361 | -0.003639 | -0.003635 | -0.007724 | -0.007803 | -0.007699 | -0.007629 | -0.007555 | -0.007752 | -0.008664 | -0.008714 | -0.009337 | -0.008703 | -0.009099 | -0.009209 | -0.006575 | -0.006665 | -0.006587 | -0.006335 | -0.006317 | -0.0062 | -0.005584 | -0.005637 | -0.005542 | -0.00569 | -0.005617 | -0.005581 | -0.005621 | -0.005635 | -0.005471 | -0.005903 | -0.005926 | -0.005913 | -0.008688 | -0.008748 | -0.008667 | -0.004154 | -0.00401 | -0.00405 | -0.00409 | -0.004014 | -0.004035
308 | m_Oil Injection Pressure (before filter)(PT-56) (AI12) |  | 0.40428 | 0.40368 | 0.40484 | 0.39618 | 0.40034 | 0.39663 | 0.39437 | 0.39523 | 0.38979 | 0.38473 | 0.38933 | 0.38824 | 0.37487 | 0.37427 | 0.38408 | 0.36521 | 0.36034 | 0.36194 | 0.35849 | 0.35599 | 0.36863 | 0.35811 | 0.36584 | 0.36368 | 0.37315 | 0.36289 | 0.36038 | 0.38349 | 0.37692 | 0.38387 | 0.38675 | 0.37336 | 0.38425 | 0.36899 | 0.38115 | 0.38943 | 0.38328 | 0.38776 | 0.37745 | 0.36808 | 0.38801 | 0.37849 | 0.36824 | 0.38011 | 0.3727 | 0.37034 | 0.37252 | 0.37535 | 0.36897 | 0.36786 | 0.3588 | 0.37545 | 0.35808 | 0.34832 | 0.34569 | 0.34158 | 0.33819 | 0.33865 | 0.33285 | 0.33603 | 0.3437 | 0.2023 | 0.20286 | 0.18882 | 0.19436 | 0.19092 | 0.18632 | 0.1877 | 0.18411 | 0.19442 | 0.19046 | 0.17336 | 0.15967 | 0.19479 | 0.19555 | 0.18971 | 0.16849 | 0.17727 | 0.18103 | 0.16808 | 0.1577 | 0.16335 | 0.15315 | 0.14213 | 0.15508 | 0.1449 | 0.14949 | 0.14118 | 0.14707 | 0.13967 | 0.14259 | 0.13415 | 0.15307 | 0.13302 | 0.12947 | 0.13001 | 0.1331 | 0.11083 | 0.11745 | 0.1261 | 0.11123 | 0.10768 | 0.10355 | 0.10459 | 0.10917 | 0.095876 | 0.068488 | 0.071218 | 0.075196 | 0.059831 | 0.059339 | 0.060618 | 0.051594 | 0.053438 | 0.056411 | -0.10298 | -0.082212 | -0.090678 | -0.098338 | -0.086707 | -0.085145 | -0.086707 | -0.075327 | -0.083518 | -0.115 | -0.094807 | -0.10209 | -0.11255 | -0.096415 | -0.10069 | -0.11356 | -0.111 | -0.087397 | -0.08334 | -0.083984 | -0.092286 | -0.096926 | -0.097734 | -0.08086 | -0.087764 | -0.10328 | -0.097819 | -0.10725 | -0.094216 | -0.10587 | -0.11058 | -0.11956 | -0.10861 | -0.11071 | -0.094603 | -0.090645 | -0.096132 | -0.097622 | -0.096697 | -0.1006 | -0.094977 | -0.10831 | -0.10069 | -0.097412 | -0.12791 | -0.12852 | -0.12961 | -0.13175 | -0.1216 | -0.13736 | -0.13951 | -0.13365 | -0.38521 | -0.38726 | -0.38799 | -0.40874 | -0.40163 | -0.39662 | -0.40115 | -0.40261 | -0.40996 | -0.403 | -0.41595 | -0.40728 | -0.41641 | -0.41418 | -0.4122 | 0.30176 | 0.2975 | 0.30189 | 0.29643 | 0.28657 | 0.30058 | 0.27816 | 0.28326 | 0.28054 | 0.28498 | 0.27183 | 0.28771 | 0.25677 | 0.25645 | 0.2534 | 0.47929 | 0.48214 | 0.47097 | 0.47123 | 0.47949 | 0.47372 | 0.47567 | 0.47772 | 0.48204 | 0.49206 | 0.48324 | 0.47623 | 0.47267 | 0.4739 | 0.4738 | 0.46632 | 0.4696 | 0.46895 | 0.43638 | 0.43777 | 0.429 | 0.43478 | 0.42679 | 0.42176 | 0.41833 | 0.41834 | 0.41589 | 0.33645 | 0.348 | 0.34464 | 0.31292 | 0.30898 | 0.30428 | 0.60126 | 0.60389 | 0.60186 | 0.5757 | 0.57547 | 0.56846
309 | n_Oil Pressure Orifice Plate (AI13) |  | 12.7402 | 12.7708 | 12.7 | 12.5597 | 12.5653 | 12.5396 | 12.4079 | 12.3841 | 12.3624 | 12.2753 | 12.2774 | 12.294 | 12.1688 | 12.1537 | 12.1489 | 6.1013 | 6.0976 | 6.0912 | 6.1302 | 6.119 | 6.0935 | 6.1185 | 6.106 | 6.1159 | 6.1139 | 6.1086 | 6.1062 | 7.2423 | 7.2599 | 7.2502 | 7.2614 | 7.2645 | 7.2764 | 7.2532 | 7.2822 | 7.2769 | 7.2281 | 7.2662 | 7.2711 | 7.2603 | 7.2937 | 7.2825 | 9.4272 | 9.3913 | 9.415 | 9.3784 | 9.4122 | 9.4155 | 9.3584 | 11.9778 | 11.9718 | 12.0059 | 12.3715 | 12.3252 | 12.3173 | 12.0075 | 12.0107 | 11.982 | 11.8153 | 11.7814 | 11.8294 | 9.3183 | 9.3199 | 9.3445 | 9.3019 | 9.301 | 9.2725 | 7.216 | 7.2369 | 7.2123 | 7.1232 | 7.16 | 7.1641 | 7.1869 | 7.1284 | 7.1155 | 6.0591 | 6.091 | 5.9969 | 6.0379 | 6.0713 | 6.0444 | 7.1988 | 7.2165 | 7.2055 | 7.19 | 7.1929 | 7.2011 | 7.1817 | 7.1734 | 7.2027 | 9.3912 | 9.375 | 9.3468 | 9.3258 | 9.3393 | 9.3237 | 9.3245 | 11.9587 | 11.9684 | 11.961 | 11.9669 | 11.9721 | 11.9583 | 11.9732 | 11.9466 | 12.2897 | 12.2486 | 12.2409 | 11.9885 | 11.9489 | 11.9303 | 11.7817 | 11.7267 | 11.7098 | 12.1866 | 12.2124 | 12.2007 | 9.3146 | 9.3206 | 9.3491 | 9.3206 | 9.3097 | 9.3111 | 7.1895 | 7.2235 | 7.2118 | 6.0582 | 6.0778 | 6.1045 | 6.1414 | 6.0871 | 9.2983 | 9.2854 | 9.3041 | 7.2123 | 7.2167 | 7.217 | 7.2509 | 7.2454 | 7.2304 | 7.2299 | 7.1726 | 7.1768 | 7.1773 | 6.1164 | 6.151 | 6.1303 | 6.1147 | 11.8324 | 11.8937 | 11.899 | 11.8873 | 11.9384 | 11.9145 | 11.9202 | 11.7155 | 11.7352 | 11.7295 | 11.8604 | 11.9015 | 11.8549 | 11.8499 | 11.7475 | 11.7714 | 11.743 | 11.6764 | 12.277 | 12.2994 | 12.2928 | 12.1001 | 12.0406 | 12.0488 | 11.8435 | 11.8319 | 11.8457 | 12.1085 | 11.9929 | 12.0488 | 7.3041 | 7.3014 | 7.2481 | 12.3134 | 12.3135 | 12.3073 | 11.8787 | 11.8316 | 11.8286 | 11.9783 | 12.0143 | 12.0002 | 11.9493 | 11.9136 | 11.9159 | 7.2721 | 7.2857 | 7.2336 | 7.3271 | 7.2878 | 7.3099 | 7.2825 | 7.2532 | 7.2723 | 6.0896 | 6.0728 | 6.0826 | 6.0747 | 6.0996 | 6.0931 | 9.4154 | 9.3801 | 9.3635 | 9.3821 | 9.3853 | 9.3677 | 12.3645 | 12.3444 | 12.3527 | 12.0865 | 12.0646 | 12.0312 | 11.8916 | 11.831 | 11.8508 | 12.0449 | 11.9631 | 11.9596 | 7.2617 | 7.3213 | 7.2671 | 11.7661 | 11.7669 | 11.7642 | 11.9501 | 11.9887 | 12.0024
310 | o_Oil Temperature Orifice Plate (AI14) |  | 40.7921 | 40.6546 | 40.3874 | 40.5348 | 40.4462 | 40.3549 | 40.6436 | 39.7913 | 39.4147 | 39.802 | 39.3913 | 39.3952 | 40.225 | 40.0836 | 39.9408 | 16.6922 | 16.625 | 16.5061 | 16.0862 | 16.0184 | 15.9368 | 17.7019 | 17.64 | 17.6008 | 17.5067 | 17.4708 | 17.413 | 26.8286 | 26.9557 | 27.1538 | 27.3963 | 27.4766 | 27.5626 | 27.0967 | 26.8434 | 26.6569 | 26.4149 | 26.7394 | 27.5656 | 28.8275 | 29.2425 | 29.6643 | 32.6334 | 32.544 | 32.458 | 32.4803 | 32.5396 | 32.5281 | 32.8562 | 38.6698 | 38.5563 | 38.0194 | 41.2519 | 40.8887 | 39.1629 | 32.126 | 31.4642 | 30.5471 | 31.0461 | 28.369 | 26.383 | 31.7175 | 31.8898 | 31.898 | 30.4307 | 30.1481 | 30.0147 | 24.8227 | 24.7174 | 24.3974 | 23.3593 | 23.0792 | 22.7127 | 22.251 | 22.0818 | 22.005 | 19.4261 | 19.5224 | 19.6483 | 18.59 | 18.1689 | 17.5883 | 26.1989 | 26.0528 | 25.8626 | 26.2855 | 26.4289 | 26.5404 | 26.657 | 26.7897 | 27.0011 | 33.3966 | 33.4712 | 33.4535 | 32.9174 | 32.8211 | 32.6756 | 37.2602 | 41.3436 | 41.3477 | 41.2798 | 40.9855 | 40.976 | 40.9601 | 40.6978 | 40.1321 | 36.1842 | 35.2439 | 34.6642 | 26.6952 | 25.6215 | 24.4677 | 21.4709 | 19.9685 | 18.9235 | 41.7329 | 41.6097 | 41.5205 | 32.3824 | 32.2807 | 32.2552 | 31.3883 | 31.2228 | 31.1445 | 24.9212 | 25.064 | 25.1768 | 16.5444 | 16.4665 | 16.4009 | 16.1617 | 16.1241 | 30.5172 | 30.4709 | 30.8901 | 24.9111 | 24.9004 | 24.893 | 24.5651 | 24.7244 | 24.6987 | 24.6131 | 23.3695 | 23.2757 | 23.0251 | 18.9694 | 18.8393 | 18.7843 | 18.8262 | 43.0611 | 43.0568 | 42.9161 | 42.9186 | 43.1771 | 43.3292 | 43.3649 | 43.3368 | 42.8804 | 41.2072 | 36.5552 | 36.3188 | 35.7905 | 35.438 | 34.4068 | 33.7584 | 33.1812 | 32.4522 | 41.4939 | 41.2797 | 40.9057 | 38.6219 | 38.6503 | 38.6909 | 38.6359 | 38.4659 | 38.206 | 34.4619 | 33.2104 | 32.5343 | 18.0675 | 17.9035 | 17.738 | 36.3144 | 35.6583 | 35.0687 | 30.0558 | 29.2215 | 28.3415 | 22.3259 | 21.3972 | 20.8953 | 19.6278 | 18.9572 | 18.5365 | 14.9461 | 14.8862 | 14.8184 | 22.6244 | 22.443 | 22.7439 | 20.505 | 20.2009 | 19.8564 | 19.7192 | 19.7019 | 19.6793 | 19.5719 | 19.5581 | 19.5728 | 30.8866 | 30.818 | 30.7885 | 30.2571 | 30.4709 | 30.2027 | 40.8035 | 40.2832 | 40.2979 | 38.1685 | 37.8408 | 37.385 | 36.5859 | 36.095 | 35.3836 | 29.3898 | 28.8142 | 27.8532 | 16.9053 | 16.8412 | 16.8044 | 39.3221 | 39.1511 | 38.9259 | 37.5414 | 36.5293 | 35.4607
311 | p_pressure differential meter (not here yet) (AI15) |  | -0.50001 | -0.50001 | -0.50001 | -0.49999 | -0.49999 | -0.50001 | -0.5 | -0.50001 | -0.50001 | -0.50001 | -0.5 | -0.5 | -0.5 | -0.50001 | -0.5 | -0.50001 | -0.50001 | -0.50001 | -0.5 | -0.5 | -0.5 | -0.5 | -0.5 | -0.5 | -0.50001 | -0.50001 | -0.5 | -0.5 | -0.50001 | -0.5 | -0.50001 | -0.50001 | -0.50001 | -0.50001 | -0.50001 | -0.5 | -0.50001 | -0.50001 | -0.5 | -0.50001 | -0.5 | -0.5 | -0.5 | -0.5 | -0.50001 | -0.5 | -0.5 | -0.5 | -0.5 | -0.50001 | -0.5 | -0.49999 | -0.5 | -0.49999 | -0.49999 | -0.5 | -0.50001 | -0.5 | -0.5 | -0.5 | -0.5 | -0.5 | -0.5 | -0.50001 | -0.50001 | -0.50001 | -0.5 | -0.49999 | -0.50001 | -0.5 | -0.50001 | -0.5 | -0.5 | -0.5 | -0.5 | -0.50001 | -0.5 | -0.50001 | -0.5 | -0.5 | -0.5 | -0.5 | -0.50001 | -0.50001 | -0.5 | -0.50001 | -0.49999 | -0.50001 | -0.5 | -0.50001 | -0.5 | -0.5 | -0.5 | -0.50001 | -0.49999 | -0.5 | -0.50001 | -0.50001 | -0.50001 | -0.5 | -0.5 | -0.50001 | -0.50001 | -0.5 | -0.5 | -0.50001 | -0.50001 | -0.5 | -0.50001 | -0.5 | -0.50001 | -0.5 | -0.50001 | -0.50001 | -0.50001 | -0.5 | -0.5 | -0.50001 | -0.5 | -0.5 | -0.5 | -0.5 | -0.5 | -0.5 | -0.50001 | -0.5 | -0.5 | -0.5 | -0.50001 | -0.50001 | -0.50001 | -0.50001 | -0.50001 | -0.50001 | -0.5 | -0.50001 | -0.50001 | -0.5 | -0.5 | -0.5 | -0.50001 | -0.49999 | -0.5 | -0.5 | -0.50001 | -0.50001 | -0.50001 | -0.5 | -0.50001 | -0.5 | -0.50001 | -0.5 | -0.49999 | -0.50001 | -0.5 | -0.50001 | -0.5 | -0.50001 | -0.5 | -0.5 | -0.50001 | -0.49999 | -0.5 | -0.50001 | -0.5 | -0.5 | -0.5 | -0.5 | -0.5 | -0.50001 | -0.49999 | -0.5 | -0.50001 | -0.50001 | -0.5 | -0.5 | -0.5 | -0.50001 | -0.5 | -0.49999 | -0.50001 | -0.50001 | -0.50001 | -0.5 | -0.5 | -0.50001 | -0.49999 | -0.50001 | -0.50001 | -0.5 | -0.5 | -0.50001 | -0.5 | -0.50002 | -0.50001 | -0.5 | -0.50001 | -0.5 | -0.5 | -0.5 | -0.5 | -0.50002 | -0.5 | -0.5 | -0.5 | -0.5 | -0.49999 | -0.50001 | -0.5 | -0.5 | -0.50001 | -0.50001 | -0.5 | -0.5 | -0.50001 | -0.49999 | -0.50001 | -0.5 | -0.5 | -0.5 | -0.5 | -0.49999 | -0.5 | -0.50001 | -0.5 | -0.50001 | -0.50001 | -0.50001 | -0.50001 | -0.50001 | -0.50001 | -0.5 | -0.5 | -0.5 | -0.5 | -0.50001
312 | a_Economiser Temp at Comp (AI0) |  | 22.7776 | 22.7296 | 22.7056 | 22.3947 | 22.3519 | 22.2101 | 21.7072 | 21.603 | 21.5399 | 20.8922 | 20.7709 | 20.6787 | 20.6079 | 20.6004 | 20.5981 | 17.9771 | 17.9956 | 17.8833 | 17.7385 | 17.6792 | 17.6379 | 18.6242 | 18.5443 | 18.4993 | 18.4114 | 18.3591 | 18.3201 | 22.8264 | 22.8483 | 22.8683 | 22.8926 | 22.9215 | 22.9062 | 22.9182 | 22.9483 | 22.9339 | 23.0018 | 22.9914 | 23.0139 | 23.0127 | 23.0337 | 23.0286 | 22.8327 | 22.8259 | 22.7699 | 22.7464 | 22.6381 | 22.6055 | 22.5855 | 22.2827 | 22.183 | 22.0311 | 21.2121 | 21.0633 | 20.6967 | 19.929 | 19.8278 | 19.6724 | 19.1605 | 18.8852 | 18.7036 | 23.1507 | 23.0822 | 23.0314 | 22.6296 | 22.5849 | 22.537 | 21.5798 | 21.5382 | 21.4427 | 21.2781 | 21.225 | 21.1688 | 21.0591 | 20.9891 | 20.9295 | 20.0619 | 20.0102 | 19.9554 | 19.0473 | 18.7823 | 18.5746 | 22.5989 | 22.592 | 22.5856 | 22.5851 | 22.5704 | 22.5848 | 22.6203 | 22.6256 | 22.6394 | 22.9762 | 22.9477 | 22.9516 | 22.8491 | 22.8037 | 22.8399 | 22.9652 | 22.8799 | 22.8507 | 22.8429 | 22.7172 | 22.6382 | 22.5915 | 22.5228 | 22.4003 | 21.0526 | 20.9714 | 20.8422 | 20.0663 | 19.939 | 19.8323 | 19.5084 | 19.2777 | 19.1276 | 21.8241 | 21.7414 | 21.6717 | 20.7673 | 20.7147 | 20.6736 | 20.5433 | 20.5384 | 20.5088 | 19.4722 | 19.3873 | 19.3536 | 17.6604 | 17.5894 | 17.5609 | 17.3494 | 17.2473 | 21.2418 | 21.231 | 21.199 | 19.9991 | 19.9789 | 19.937 | 19.643 | 19.5493 | 19.5242 | 19.5208 | 19.0131 | 18.9861 | 18.9567 | 17.6915 | 17.5855 | 17.5831 | 17.5389 | 24.9401 | 24.8996 | 24.9012 | 24.8546 | 24.6722 | 24.6053 | 24.5658 | 24.0188 | 23.912 | 23.5293 | 23.4345 | 23.3864 | 23.3561 | 23.3411 | 23.2462 | 23.1835 | 23.1491 | 23.0527 | 21.7648 | 21.674 | 21.6298 | 21.111 | 21.0415 | 20.9985 | 20.8925 | 20.8325 | 20.7531 | 20.3791 | 20.2051 | 20.0522 | 18.3873 | 18.2884 | 18.2317 | 21.7326 | 21.6181 | 21.5173 | 21.0421 | 20.9607 | 20.882 | 19.942 | 19.887 | 19.8199 | 19.6187 | 19.536 | 19.4589 | 16.7604 | 16.6981 | 16.6225 | 18.2066 | 18.0843 | 18.0152 | 17.3168 | 17.2251 | 17.104 | 19.3907 | 19.3829 | 19.4077 | 19.353 | 19.3431 | 19.3408 | 20.2704 | 20.2346 | 20.2482 | 19.8033 | 19.7573 | 19.7239 | 21.517 | 21.3045 | 21.12 | 20.798 | 20.6835 | 20.5372 | 20.2806 | 20.1086 | 19.9581 | 21.5806 | 21.4833 | 21.4326 | 19.787 | 19.6938 | 19.6292 | 21.7639 | 21.6537 | 21.5465 | 21.1886 | 21.0316 | 20.9139
313 | b_Spare1 (AI1) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
314 | c_Spare2 (AI2) |  | -9.9997 | -9.9997 | -9.9997 | -9.9996 | -9.9998 | -9.9999 | -9.9999 | -9.9997 | -9.9999 | -9.9998 | -9.9999 | -9.9999 | -9.9998 | -9.9996 | -9.9999 | -9.9999 | -9.9996 | -9.9997 | -9.9998 | -9.9998 | -9.9996 | -9.9999 | -9.9998 | -9.9998 | -9.9997 | -9.9999 | -9.9998 | -9.9997 | -9.9999 | -9.9998 | -9.9998 | -10 | -9.9998 | -9.9999 | -10 | -9.9998 | -9.9997 | -9.9998 | -9.9998 | -9.9996 | -10 | -9.9998 | -9.9998 | -9.9998 | -9.9998 | -9.9998 | -9.9996 | -9.9997 | -9.9999 | -9.9998 | -9.9999 | -9.9998 | -9.9996 | -10 | -9.9998 | -10 | -9.9998 | -9.9999 | -10.0002 | -9.9998 | -9.9997 | -9.9998 | -9.9999 | -9.9996 | -9.9998 | -9.9999 | -9.9998 | -9.9999 | -9.9999 | -9.9998 | -9.9997 | -9.9998 | -9.9998 | -9.9999 | -9.9997 | -9.9997 | -9.9998 | -9.9997 | -9.9997 | -9.9999 | -9.9997 | -9.9999 | -9.9997 | -9.9997 | -9.9998 | -9.9997 | -9.9996 | -9.9999 | -9.9997 | -10 | -9.9998 | -9.9998 | -9.9997 | -9.9999 | -9.9999 | -9.9999 | -9.9999 | -9.9998 | -10 | -9.9997 | -9.9999 | -9.9997 | -9.9997 | -9.9998 | -9.9999 | -9.9998 | -9.9998 | -9.9998 | -9.9998 | -9.9997 | -9.9998 | -9.9999 | -9.9998 | -10.0001 | -9.9998 | -9.9998 | -9.9998 | -10 | -9.9997 | -9.9998 | -9.9998 | -9.9999 | -9.9998 | -9.9998 | -10 | -9.9999 | -9.9998 | -9.9998 | -10.0001 | -9.9999 | -9.9998 | -9.9999 | -9.9996 | -9.9997 | -9.9997 | -9.9998 | -9.9999 | -9.9997 | -9.9996 | -9.9998 | -9.9998 | -10.0001 | -9.9997 | -9.9998 | -9.9997 | -9.9999 | -9.9997 | -9.9998 | -9.9998 | -9.9999 | -10 | -9.9997 | -9.9998 | -9.9996 | -9.9999 | -9.9998 | -9.9997 | -9.9998 | -9.9997 | -9.9998 | -9.9999 | -9.9998 | -9.9998 | -9.9999 | -9.9998 | -9.9998 | -10 | -10 | -9.9999 | -9.9998 | -9.9998 | -9.9998 | -9.9999 | -10 | -10 | -9.9999 | -9.9999 | -9.9998 | -9.9997 | -9.9998 | -9.9997 | -10 | -9.9999 | -9.9997 | -9.9999 | -9.9998 | -10 | -9.9998 | -9.9998 | -9.9999 | -9.9999 | -9.9997 | -9.9999 | -9.9998 | -9.9998 | -9.9999 | -9.9996 | -9.9999 | -9.9998 | -9.9998 | -9.9997 | -10 | -9.9997 | -9.9997 | -9.9997 | -10 | -9.9996 | -9.9998 | -9.9999 | -9.9997 | -9.9995 | -9.9999 | -9.9999 | -9.9997 | -10 | -9.9998 | -9.9998 | -9.9997 | -9.9998 | -9.9998 | -9.9999 | -9.9998 | -9.9997 | -9.9998 | -9.9999 | -9.9998 | -9.9998 | -9.9998 | -9.9997 | -9.9998 | -9.9998 | -9.9997 | -10.0001 | -10.0001 | -9.9997 | -9.9998
315 | d_Economiser Flowmeter Pressure (AI3) |  | 7.6213 | 7.615 | 7.6108 | 7.5349 | 7.5326 | 7.5086 | 7.4278 | 7.4088 | 7.391 | 7.2771 | 7.2611 | 7.2423 | 7.1383 | 7.1381 | 7.1304 | 6.6748 | 6.6614 | 6.6621 | 6.6293 | 6.6201 | 6.6157 | 6.7855 | 6.7787 | 6.7773 | 6.754 | 6.7478 | 6.7447 | 7.4415 | 7.4467 | 7.45 | 7.4573 | 7.4567 | 7.4574 | 7.4633 | 7.4622 | 7.4664 | 7.4771 | 7.4803 | 7.5051 | 7.5158 | 7.5238 | 7.5254 | 7.554 | 7.5632 | 7.5506 | 7.5466 | 7.5305 | 7.5299 | 7.5141 | 7.4386 | 7.423 | 7.3851 | 7.187 | 7.1513 | 7.0728 | 6.9131 | 6.8901 | 6.8654 | 6.7812 | 6.7618 | 6.73 | 7.3987 | 7.3728 | 7.3621 | 7.2829 | 7.2657 | 7.2618 | 7.0885 | 7.0812 | 7.0684 | 7.0478 | 7.038 | 7.0272 | 7.0084 | 6.9982 | 6.9897 | 6.8679 | 6.85 | 6.848 | 6.7473 | 6.7164 | 6.7132 | 7.3604 | 7.365 | 7.3608 | 7.3752 | 7.3774 | 7.3816 | 7.397 | 7.4019 | 7.3996 | 7.453 | 7.4581 | 7.4497 | 7.4268 | 7.4336 | 7.4394 | 7.4487 | 7.4235 | 7.4221 | 7.4199 | 7.3963 | 7.3907 | 7.3791 | 7.3677 | 7.3398 | 7.0745 | 7.0601 | 7.0301 | 6.8778 | 6.8631 | 6.841 | 6.7861 | 6.7562 | 6.7602 | 7.4586 | 7.4387 | 7.4301 | 7.2205 | 7.2101 | 7.2092 | 7.1564 | 7.1569 | 7.1468 | 6.9476 | 6.937 | 6.9344 | 6.7543 | 6.7489 | 6.739 | 6.7129 | 6.7045 | 7.2902 | 7.2815 | 7.2654 | 7.0752 | 7.0821 | 7.0727 | 7.0239 | 7.0105 | 7.0001 | 6.9979 | 6.8858 | 6.8826 | 6.8793 | 6.7531 | 6.7398 | 6.7385 | 6.7435 | 7.9831 | 7.9722 | 7.966 | 7.9634 | 7.8689 | 7.8536 | 7.8427 | 7.7352 | 7.7219 | 7.6659 | 7.8672 | 7.8566 | 7.8466 | 7.8466 | 7.8231 | 7.8053 | 7.7895 | 7.767 | 7.445 | 7.4311 | 7.4177 | 7.2924 | 7.2792 | 7.2588 | 7.2346 | 7.2181 | 7.2028 | 7.121 | 7.0849 | 7.0548 | 6.7305 | 6.7134 | 6.7123 | 7.4332 | 7.4099 | 7.3942 | 7.2865 | 7.2705 | 7.2619 | 7.1353 | 7.1196 | 7.1023 | 7.0614 | 7.0397 | 7.0129 | 6.5459 | 6.5369 | 6.521 | 6.8206 | 6.8111 | 6.7967 | 6.7396 | 6.7285 | 6.7126 | 7.053 | 7.0497 | 7.0493 | 7.0534 | 7.0483 | 7.0494 | 7.168 | 7.1566 | 7.1501 | 7.0592 | 7.0543 | 7.0381 | 7.4273 | 7.3741 | 7.3396 | 7.2563 | 7.2387 | 7.2069 | 7.1524 | 7.1207 | 7.0862 | 7.2778 | 7.264 | 7.2464 | 6.9069 | 6.8889 | 6.8819 | 7.4347 | 7.4143 | 7.3911 | 7.3323 | 7.3033 | 7.2807
316 | e_Economiser Flowmeter Temperature (AI4) |  | 21.2558 | 21.2081 | 21.1745 | 20.8263 | 20.7646 | 20.6499 | 20.3445 | 20.2453 | 20.1563 | 19.5587 | 19.4566 | 19.3985 | 18.8064 | 18.8039 | 18.7705 | 16.2135 | 16.1998 | 16.1716 | 15.962 | 15.9573 | 15.9064 | 16.8762 | 16.8481 | 16.824 | 16.7427 | 16.7122 | 16.6864 | 20.2822 | 20.2853 | 20.2947 | 20.3052 | 20.3371 | 20.3234 | 20.3603 | 20.3532 | 20.3469 | 20.4297 | 20.4537 | 20.5397 | 20.6495 | 20.6296 | 20.6726 | 20.8306 | 20.8493 | 20.8209 | 20.7947 | 20.6873 | 20.7126 | 20.6591 | 20.3165 | 20.2904 | 20.0562 | 19.0828 | 18.9286 | 18.5373 | 17.7225 | 17.5964 | 17.4583 | 17.0231 | 16.7869 | 16.6261 | 20.1535 | 20.0278 | 19.9371 | 19.5368 | 19.47 | 19.3929 | 18.4614 | 18.4495 | 18.3912 | 18.23 | 18.1992 | 18.1358 | 18.0441 | 18.0096 | 17.9529 | 17.222 | 17.1901 | 17.1633 | 16.6275 | 16.5101 | 16.3762 | 19.8748 | 19.8541 | 19.9038 | 19.9711 | 20.0154 | 20.0184 | 20.1064 | 20.165 | 20.1863 | 20.5085 | 20.5206 | 20.496 | 20.4816 | 20.4876 | 20.4556 | 20.5798 | 20.4911 | 20.4617 | 20.4527 | 20.314 | 20.3134 | 20.2445 | 20.1679 | 20.0281 | 18.6473 | 18.5668 | 18.421 | 17.626 | 17.5138 | 17.3988 | 17.1151 | 16.9485 | 16.8119 | 20.4248 | 20.3386 | 20.2922 | 19.1581 | 19.1341 | 19.0917 | 18.8376 | 18.791 | 18.7583 | 17.6398 | 17.6151 | 17.574 | 16.454 | 16.4191 | 16.3969 | 16.249 | 16.2016 | 19.3667 | 19.3183 | 19.2715 | 18.293 | 18.2607 | 18.2461 | 18.0021 | 17.8893 | 17.8928 | 17.8683 | 17.2925 | 17.2638 | 17.2338 | 16.4118 | 16.3593 | 16.3619 | 16.3501 | 22.7509 | 22.6864 | 22.669 | 22.6609 | 22.259 | 22.1419 | 22.1063 | 21.5907 | 21.4975 | 21.2153 | 22.2312 | 22.1809 | 22.1396 | 22.0743 | 22.0051 | 21.9113 | 21.866 | 21.7742 | 20.3673 | 20.2953 | 20.2134 | 19.6299 | 19.558 | 19.4647 | 19.3563 | 19.2454 | 19.1962 | 18.7113 | 18.5413 | 18.3979 | 16.5204 | 16.4726 | 16.4283 | 20.0736 | 19.9616 | 19.8733 | 19.3902 | 19.3205 | 19.2398 | 18.6629 | 18.5668 | 18.5253 | 18.3186 | 18.1914 | 18.0475 | 15.3278 | 15.2785 | 15.1971 | 16.9871 | 16.9418 | 16.845 | 16.3478 | 16.2808 | 16.2235 | 17.9042 | 17.9047 | 17.9032 | 17.8792 | 17.8524 | 17.8293 | 18.7127 | 18.6337 | 18.6054 | 18.1197 | 18.0648 | 18.0132 | 19.8962 | 19.6397 | 19.476 | 19.0832 | 19.0016 | 18.8722 | 18.5714 | 18.4379 | 18.2552 | 19.1342 | 19.1011 | 18.9822 | 17.1027 | 17.045 | 16.9975 | 19.8261 | 19.7168 | 19.6358 | 19.3129 | 19.2028 | 19.0622
317 | f_Economiser Flow (AI5) |  | 0.064297 | 0.76616 | -0.007497 | -0.036116 | -0.027314 | -0.044967 | -0.022593 | -0.024806 | -0.041476 | -0.030018 | -0.021905 | -0.027117 | -0.029674 | -0.01148 | -0.021462 | -0.005284 | 0.001502 | 0.007895 | -0.011283 | 0.000273 | 0.004108 | -0.012316 | -0.017676 | -0.006366 | -0.003514 | -0.016545 | -0.007349 | -0.03887 | -0.028051 | -0.039411 | -0.043787 | -0.037837 | -0.041132 | -0.026084 | -0.0341 | -0.036854 | -0.035034 | -0.029232 | -0.022839 | -0.043 | -0.031199 | -0.033608 | -0.040148 | -0.031149 | -0.038624 | -0.05013 | -0.044672 | -0.040886 | -0.034985 | 123.9109 | 123.9205 | 123.921 | -0.023478 | -0.022937 | -0.021954 | 0.19771 | 0.083376 | 0.055987 | -0.021806 | -0.007989 | -0.005136 | -0.025937 | -0.043148 | -0.031002 | -0.022691 | -0.036411 | -0.028543 | -0.029477 | -0.030018 | -0.008136 | -0.025593 | -0.025298 | -0.016643 | -0.028887 | -0.012808 | -0.012021 | -0.012168 | -0.040689 | -0.005235 | -0.012611 | -0.022937 | -0.003956 | -0.04541 | -0.021216 | -0.030412 | -0.047475 | -0.027412 | -0.035132 | -0.026035 | -0.033411 | -0.033805 | -0.033067 | -0.020429 | -0.043 | -0.031936 | -0.060654 | -0.03351 | -0.027166 | 30.7931 | 32.1068 | 29.751 | 41.5055 | 55.2093 | 43.9462 | 41.5772 | 39.9145 | -0.025396 | -0.027461 | -0.019594 | -0.021167 | -0.027068 | -0.012021 | -0.016496 | 0.008927 | -0.009169 | -0.024314 | -0.040247 | -0.038034 | -0.042902 | -0.01861 | -0.02633 | -0.035723 | -0.025347 | -0.016987 | -0.014627 | -0.006464 | -0.005874 | -0.002973 | 0.002338 | -0.005923 | -0.004497 | 0.003518 | -0.020479 | -0.025199 | -0.03705 | -0.004448 | -0.016545 | -0.022052 | -0.015955 | -0.028002 | -0.013496 | -0.018659 | -0.022888 | -0.021659 | -0.004596 | -0.004104 | -0.011529 | -0.009267 | -0.00848 | 35.002 | 29.0561 | 34.1746 | 30.6214 | -0.045016 | -0.039656 | -0.041427 | -0.031199 | -0.028789 | -0.038329 | -0.040148 | -0.047524 | -0.053769 | -0.035723 | -0.027855 | -0.059621 | -0.042509 | -0.023429 | -0.022691 | -0.033952 | -0.045016 | -0.010742 | -0.050868 | -0.024118 | -0.02515 | -0.036411 | -0.031641 | 29.5967 | 25.9915 | 29.7857 | 0.002043 | -0.012168 | -0.004104 | -0.043246 | -0.027215 | -0.03469 | -0.015512 | -0.017922 | 0.25583 | -0.023773 | -0.011234 | -0.027363 | 41.3327 | 41.3405 | 41.3113 | 0.006419 | -0.000612 | -0.008726 | -0.006267 | -0.00971 | -0.020577 | 0.008386 | 0.001404 | 0.004059 | -0.013889 | -0.00789 | -0.017135 | -0.027068 | -0.020036 | -0.004497 | -0.021413 | -0.02156 | -0.013791 | -0.009906 | -0.015414 | -0.027511 | -0.038919 | -0.013348 | -0.028543 | 1.1736 | 2.0966 | 1.7481 | -0.021511 | -0.005923 | -0.002924 | 38.8679 | 27.6776 | 27.6752 | -0.01802 | 0.004698 | -0.016004 | -0.029232 | -0.012562 | -0.021856 | -0.025347 | -0.02815 | -0.020184
318 | g_Spare6 (AI6) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
319 | pressure at comp top cover (before rotor) |  | 3.7223 | 3.7256 | 3.7084 | 3.0225 | 3.0265 | 3.0232 | 2.3784 | 2.4029 | 2.3954 | 1.8429 | 1.8462 | 1.8416 | 1.3689 | 1.3662 | 1.3591 | 2.8656 | 2.862 | 2.8562 | 2.8661 | 2.8697 | 2.8672 | 2.8581 | 2.8573 | 2.865 | 2.8622 | 2.8688 | 2.8677 | 2.7988 | 2.7946 | 2.8026 | 2.8087 | 2.8121 | 2.8066 | 2.784 | 2.7974 | 2.8026 | 2.7921 | 2.8083 | 2.7988 | 2.8066 | 2.7938 | 2.8045 | 2.57 | 2.5708 | 2.5669 | 2.572 | 2.5645 | 2.5698 | 2.5662 | 2.286 | 2.2822 | 2.2929 | 2.0091 | 2.0106 | 2.0135 | 2.2716 | 2.2681 | 2.2701 | 2.2611 | 2.2638 | 2.2726 | 2.5663 | 2.5535 | 2.5615 | 2.5624 | 2.5599 | 2.553 | 2.7924 | 2.7981 | 2.7965 | 2.7921 | 2.8135 | 2.8138 | 2.8133 | 2.8071 | 2.7995 | 2.8826 | 2.877 | 2.8674 | 2.8758 | 2.8756 | 2.8777 | 2.8013 | 2.8081 | 2.8069 | 2.7847 | 2.7887 | 2.7982 | 2.7956 | 2.795 | 2.8008 | 2.5724 | 2.5639 | 2.5509 | 2.551 | 2.5495 | 2.5497 | 2.5587 | 2.2834 | 2.2812 | 2.283 | 2.281 | 2.2845 | 2.2864 | 2.2885 | 2.2861 | 2.0118 | 2.002 | 2.0034 | 2.2626 | 2.2656 | 2.2611 | 2.2637 | 2.2603 | 2.2652 | 2.0374 | 2.0477 | 2.0431 | 2.6015 | 2.603 | 2.6012 | 2.606 | 2.6032 | 2.6004 | 2.8435 | 2.8438 | 2.8416 | 2.8902 | 2.8904 | 2.9056 | 2.9097 | 2.8973 | 2.5967 | 2.592 | 2.5985 | 2.8338 | 2.8372 | 2.8354 | 2.8458 | 2.8345 | 2.8394 | 2.8343 | 2.6353 | 2.6268 | 2.6373 | 2.8866 | 2.9164 | 2.9138 | 2.9129 | 2.2878 | 2.2982 | 2.3073 | 2.2966 | 2.2813 | 2.2944 | 2.3016 | 2.2973 | 2.2909 | 2.3095 | 2.2951 | 2.3026 | 2.2896 | 2.2866 | 2.2934 | 2.3023 | 2.2888 | 2.2971 | 2.0117 | 2.0162 | 2.0085 | 2.2691 | 2.2569 | 2.2631 | 2.2618 | 2.2571 | 2.2612 | 2.2817 | 2.2749 | 2.2839 | 2.8079 | 2.8026 | 2.7926 | 2.0191 | 2.0161 | 2.0158 | 2.2774 | 2.2689 | 2.2631 | 2.2635 | 2.2701 | 2.269 | 2.2945 | 2.2859 | 2.2855 | 2.7963 | 2.803 | 2.7985 | 2.8087 | 2.8131 | 2.8022 | 2.8143 | 2.8075 | 2.8057 | 2.8731 | 2.8699 | 2.8892 | 2.8687 | 2.8686 | 2.864 | 2.575 | 2.58 | 2.5772 | 2.5733 | 2.5751 | 2.5794 | 2.012 | 2.0033 | 2.0026 | 2.2619 | 2.2593 | 2.2523 | 2.2609 | 2.2602 | 2.2539 | 2.2962 | 2.2842 | 2.2907 | 2.789 | 2.7855 | 2.7891 | 2.256 | 2.2597 | 2.2525 | 2.2535 | 2.2625 | 2.2531
320 | i_Liquid Injection Flow (AI8) |  | 0.5215 | 0.52143 | 0.5229 | 0.52276 | 0.52041 | 0.52379 | 0.52125 | 0.51932 | 0.52194 | 0.52248 | 0.52357 | 0.52149 | 0.52087 | 0.52206 | 0.52314 | 0.52195 | 0.52278 | 0.52194 | 0.5234 | 0.52155 | 0.52218 | 0.5196 | 0.52034 | 0.52441 | 0.52248 | 0.52221 | 0.5244 | 0.52262 | 0.5214 | 0.52117 | 0.52186 | 0.52201 | 0.52363 | 0.52001 | 0.52309 | 0.5217 | 0.52114 | 0.52081 | 0.5241 | 0.51992 | 0.5227 | 0.52199 | 0.51909 | 0.52184 | 0.51934 | 0.5219 | 0.52291 | 0.52028 | 0.52302 | 0.52138 | 0.52345 | 0.51933 | 0.52037 | 0.52298 | 0.5212 | 0.52047 | 0.52194 | 0.52207 | 0.52077 | 0.5228 | 0.52026 | 0.52097 | 0.52228 | 0.51856 | 0.52383 | 0.51913 | 0.5219 | 0.52213 | 0.51969 | 0.52445 | 0.52287 | 0.52214 | 0.51881 | 0.52234 | 0.5214 | 0.52309 | 0.51901 | 0.52345 | 0.52259 | 0.52245 | 0.52425 | 2.1308 | 0.52363 | 0.52213 | 0.52231 | 0.51894 | 0.52252 | 0.52322 | 0.52084 | 0.52169 | 0.52331 | 0.52161 | 0.51954 | 0.52028 | 0.52225 | 0.51986 | 0.52168 | 0.52169 | 0.52185 | 0.51922 | 0.51902 | 0.52214 | 0.52263 | 0.52283 | 0.5233 | 0.52062 | 0.52139 | 0.52232 | 0.52261 | 0.52145 | 0.52158 | 0.52163 | 0.52302 | 0.52431 | 0.52138 | 0.52242 | 0.52038 | 0.5213 | 0.5199 | 0.52089 | 0.52049 | 0.52335 | 0.52231 | 0.52328 | 0.52227 | 0.5238 | 0.52209 | 0.52245 | 0.52199 | 0.52256 | 0.52208 | 0.51901 | 0.51943 | 0.52385 | 0.52362 | 0.52067 | 0.52138 | 0.52129 | 0.52197 | 0.52215 | 0.51988 | 0.52255 | 0.52247 | 0.52298 | 0.52265 | 0.5209 | 0.52151 | 0.52401 | 0.51914 | 0.5229 | 0.52214 | 0.5195 | 0.5228 | 0.5209 | 0.52272 | 0.5207 | 0.5215 | 0.52287 | 0.52322 | 0.52429 | 0.52376 | 0.52382 | 0.52088 | 0.52394 | 0.52282 | 0.52108 | 0.52184 | 0.52135 | 0.52159 | 0.51999 | 0.5222 | 0.52415 | 0.52191 | 0.52189 | 0.52089 | 0.5219 | 0.5234 | 0.52135 | 0.52375 | 0.5242 | 0.52244 | 0.52114 | 0.52244 | 0.51929 | 0.52193 | 0.52172 | 0.5215 | 0.52307 | 0.51997 | 0.52144 | 0.52251 | 0.52156 | 0.52188 | 0.52084 | 0.52181 | 0.52297 | 0.52365 | 0.52049 | 0.5225 | 0.52299 | 0.52258 | 0.52229 | 0.52073 | 0.52067 | 0.51994 | 0.52312 | 0.52106 | 0.52084 | 0.52164 | 0.5203 | 0.52059 | 0.52417 | 0.52014 | 0.52067 | 0.52106 | 0.52118 | 0.52294 | 0.52445 | 0.52109 | 0.52138 | 0.52066 | 0.52039 | 0.52342 | 0.52174 | 0.52093 | 0.52204 | 0.52173 | 0.52371 | 0.52104 | 0.52378 | 0.52293 | 0.5208 | 0.52315 | 0.52233 | 0.52189 | 0.52176
321 | j_Liquid Injection Temperature (AI9) |  | 19.9976 | 19.9571 | 19.9165 | 19.604 | 19.5857 | 19.4733 | 19.204 | 19.1215 | 19.0863 | 18.6193 | 18.5451 | 18.502 | 18.1762 | 18.1454 | 18.1113 | 16.1854 | 16.1827 | 16.1556 | 16.0152 | 15.9686 | 15.9338 | 16.8788 | 16.8624 | 16.8162 | 16.7861 | 16.719 | 16.7132 | 19.8074 | 19.7908 | 19.8266 | 19.8231 | 19.8121 | 19.82 | 19.8146 | 19.8123 | 19.7875 | 19.8428 | 19.8347 | 19.8826 | 19.9294 | 19.9439 | 19.9657 | 20.0031 | 19.9982 | 19.9548 | 19.9075 | 19.7527 | 19.7094 | 19.7109 | 19.3662 | 19.3065 | 19.1384 | 18.3278 | 18.1551 | 17.8645 | 17.2403 | 17.1464 | 17.0547 | 16.688 | 16.5026 | 16.3961 | 19.548 | 19.4774 | 19.3849 | 19.1152 | 19.0285 | 19.0063 | 18.2818 | 18.3 | 18.2472 | 18.1184 | 18.0892 | 18.0361 | 17.9758 | 17.9264 | 17.8939 | 17.3273 | 17.3199 | 17.2655 | 16.8168 | 16.7405 | 16.5886 | 19.3445 | 19.3337 | 19.3353 | 19.3593 | 19.3535 | 19.3783 | 19.4165 | 19.4233 | 19.4224 | 19.5129 | 19.5116 | 19.5024 | 19.4119 | 19.3997 | 19.4176 | 19.3965 | 19.2768 | 19.2536 | 19.2455 | 19.1201 | 19.1091 | 19.0841 | 19.0339 | 18.8962 | 17.8546 | 17.7969 | 17.7177 | 17.1293 | 17.0588 | 16.9646 | 16.7477 | 16.5877 | 16.519 | 19.4298 | 19.3557 | 19.3329 | 18.4754 | 18.4856 | 18.4406 | 18.2724 | 18.2217 | 18.2061 | 17.4242 | 17.3995 | 17.376 | 16.5334 | 16.5028 | 16.4883 | 16.3958 | 16.367 | 18.8189 | 18.7613 | 18.7005 | 17.9405 | 17.9163 | 17.9122 | 17.7416 | 17.6518 | 17.6321 | 17.5962 | 17.1716 | 17.1395 | 17.1223 | 16.4162 | 16.3613 | 16.3399 | 16.3208 | 21.7071 | 21.6477 | 21.6439 | 21.6178 | 21.2944 | 21.238 | 21.2058 | 20.8601 | 20.7562 | 20.5337 | 21.2526 | 21.2336 | 21.1573 | 21.1121 | 21.0328 | 20.9965 | 20.91 | 20.8537 | 19.2982 | 19.2382 | 19.1841 | 18.6755 | 18.6427 | 18.5464 | 18.4656 | 18.4145 | 18.3534 | 17.9906 | 17.8531 | 17.7346 | 16.3038 | 16.2771 | 16.256 | 18.9888 | 18.927 | 18.8385 | 18.47 | 18.3757 | 18.3022 | 17.6191 | 17.5737 | 17.4959 | 17.3445 | 17.2379 | 17.1583 | 15.1456 | 15.1224 | 15.0586 | 16.6793 | 16.6592 | 16.5676 | 16.2276 | 16.1804 | 16.1308 | 17.6817 | 17.667 | 17.6517 | 17.666 | 17.6471 | 17.6128 | 17.8378 | 17.8023 | 17.7745 | 17.4083 | 17.3497 | 17.2824 | 18.8091 | 18.6361 | 18.5005 | 18.2075 | 18.1209 | 18.0216 | 17.7946 | 17.6877 | 17.5445 | 18.3109 | 18.2849 | 18.2005 | 16.8673 | 16.8071 | 16.7826 | 18.641 | 18.577 | 18.5099 | 18.2821 | 18.1983 | 18.0989
322 | k_Liquid Injection Pressure (AI10) |  | 0.67156 | 0.66798 | 0.66685 | 0.66224 | 0.6603 | 0.65671 | 0.65351 | 0.64676 | 0.64485 | 0.63977 | 0.64046 | 0.63531 | 0.62459 | 0.62563 | 0.62583 | 0.59513 | 0.59361 | 0.59891 | 0.5899 | 0.59153 | 0.58761 | 0.6132 | 0.61292 | 0.61368 | 0.6076 | 0.61377 | 0.60967 | 0.67044 | 0.66825 | 0.67319 | 0.67313 | 0.67313 | 0.67471 | 0.67717 | 0.66989 | 0.67375 | 0.66985 | 0.67439 | 0.67502 | 0.67369 | 0.67004 | 0.67566 | 0.67083 | 0.67519 | 0.67582 | 0.67107 | 0.6692 | 0.66984 | 0.67085 | 0.65574 | 0.65437 | 0.65569 | 0.63744 | 0.63422 | 0.62186 | 0.61148 | 0.61204 | 0.60984 | 0.60332 | 0.60232 | 0.5973 | 0.66541 | 0.66666 | 0.65939 | 0.65434 | 0.65288 | 0.65138 | 0.64465 | 0.64095 | 0.6444 | 0.64573 | 0.64272 | 0.64013 | 0.64441 | 0.64257 | 0.63712 | 0.629 | 0.62668 | 0.62829 | 0.62215 | 0.62122 | 0.61718 | 0.68048 | 0.67539 | 0.67638 | 0.67923 | 0.68253 | 0.67867 | 0.68378 | 0.68192 | 0.68112 | 0.67864 | 0.68477 | 0.68417 | 0.68616 | 0.67771 | 0.68128 | 0.67871 | 0.67422 | 0.67955 | 0.67338 | 0.66587 | 0.66765 | 0.67128 | 0.66751 | 0.66338 | 0.63861 | 0.6364 | 0.63332 | 0.62536 | 0.61914 | 0.62362 | 0.61897 | 0.61433 | 0.60978 | 0.71964 | 0.71339 | 0.71655 | 0.70986 | 0.70798 | 0.70022 | 0.69912 | 0.69809 | 0.7002 | 0.68293 | 0.68031 | 0.68284 | 0.66986 | 0.66697 | 0.66676 | 0.67237 | 0.66607 | 0.72009 | 0.71252 | 0.71676 | 0.70007 | 0.70353 | 0.71126 | 0.69808 | 0.69899 | 0.69761 | 0.69868 | 0.68955 | 0.68253 | 0.68931 | 0.6778 | 0.67889 | 0.67703 | 0.67695 | 0.7674 | 0.76904 | 0.76593 | 0.76363 | 0.75758 | 0.76062 | 0.75796 | 0.75003 | 0.74833 | 0.74553 | 0.77448 | 0.77266 | 0.77073 | 0.76993 | 0.77105 | 0.77024 | 0.76732 | 0.76384 | 0.7343 | 0.73534 | 0.73369 | 0.72457 | 0.72031 | 0.71991 | 0.71705 | 0.7158 | 0.71694 | 0.70905 | 0.70646 | 0.70394 | 0.68388 | 0.6797 | 0.68129 | 0.74978 | 0.74838 | 0.74863 | 0.73664 | 0.73629 | 0.73699 | 0.71903 | 0.72064 | 0.71927 | 0.7131 | 0.71483 | 0.70659 | 0.67238 | 0.6719 | 0.67139 | 0.71793 | 0.71874 | 0.71453 | 0.70924 | 0.70505 | 0.70547 | 0.74533 | 0.74413 | 0.74684 | 0.74984 | 0.7494 | 0.74507 | 0.74907 | 0.74542 | 0.74249 | 0.73807 | 0.73359 | 0.73253 | 0.76002 | 0.75344 | 0.75142 | 0.74485 | 0.74296 | 0.74326 | 0.73433 | 0.73147 | 0.73174 | 0.74757 | 0.74565 | 0.74816 | 0.71665 | 0.72242 | 0.72395 | 0.79707 | 0.792 | 0.7894 | 0.78716 | 0.78184 | 0.78705
323 | l_Spare11 (AI11) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
324 | m_ spare12 (AI12) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
325 | n_Discharge Pressure (PT-53) (AI13) |  | 13.7337 | 13.7439 | 13.7006 | 13.7346 | 13.7509 | 13.7397 | 13.7659 | 13.7313 | 13.704 | 13.7558 | 13.765 | 13.7664 | 13.7403 | 13.7196 | 13.7051 | 7.2692 | 7.2694 | 7.2729 | 7.2925 | 7.2785 | 7.2488 | 7.2709 | 7.2702 | 7.274 | 7.2894 | 7.265 | 7.258 | 8.4236 | 8.4283 | 8.4355 | 8.4498 | 8.4489 | 8.4585 | 8.4445 | 8.4798 | 8.4593 | 8.4249 | 8.4574 | 8.4622 | 8.4462 | 8.4796 | 8.4741 | 10.7415 | 10.702 | 10.7289 | 10.6971 | 10.7705 | 10.7579 | 10.7193 | 13.3548 | 13.3595 | 13.3857 | 13.7844 | 13.74 | 13.7451 | 13.362 | 13.3646 | 13.352 | 13.1727 | 13.1489 | 13.2108 | 10.7394 | 10.715 | 10.7405 | 10.6993 | 10.719 | 10.6929 | 8.4618 | 8.4893 | 8.4636 | 8.4292 | 8.4677 | 8.4714 | 8.4773 | 8.4653 | 8.4388 | 7.2964 | 7.2976 | 7.2541 | 7.2574 | 7.285 | 7.2595 | 8.4489 | 8.4733 | 8.4528 | 8.435 | 8.4315 | 8.4407 | 8.4481 | 8.4501 | 8.4633 | 10.7535 | 10.7405 | 10.7212 | 10.7149 | 10.7299 | 10.7144 | 10.7206 | 13.3851 | 13.3886 | 13.3936 | 13.3867 | 13.3856 | 13.3864 | 13.3784 | 13.3776 | 13.745 | 13.7197 | 13.7147 | 13.4178 | 13.3795 | 13.3704 | 13.2181 | 13.1762 | 13.1516 | 13.7187 | 13.746 | 13.7199 | 10.7201 | 10.7179 | 10.7487 | 10.7184 | 10.7094 | 10.7013 | 8.4341 | 8.457 | 8.4502 | 7.2563 | 7.2664 | 7.2934 | 7.3274 | 7.271 | 10.7071 | 10.697 | 10.7165 | 8.4371 | 8.4414 | 8.4467 | 8.4713 | 8.4527 | 8.4438 | 8.4403 | 8.4262 | 8.4255 | 8.434 | 7.3284 | 7.3412 | 7.3145 | 7.2958 | 13.3169 | 13.3768 | 13.3935 | 13.3714 | 13.3907 | 13.3788 | 13.3652 | 13.1906 | 13.1972 | 13.2068 | 13.3664 | 13.389 | 13.3506 | 13.3523 | 13.2343 | 13.2717 | 13.2391 | 13.1672 | 13.7284 | 13.7237 | 13.7373 | 13.3937 | 13.3318 | 13.3524 | 13.1849 | 13.1481 | 13.1656 | 13.421 | 13.3407 | 13.3763 | 8.4878 | 8.4893 | 8.4299 | 13.7673 | 13.7713 | 13.7562 | 13.2264 | 13.1938 | 13.1836 | 13.3636 | 13.372 | 13.3756 | 13.3576 | 13.334 | 13.3241 | 8.4772 | 8.4949 | 8.4357 | 8.4877 | 8.451 | 8.4772 | 8.4476 | 8.4216 | 8.4372 | 7.2724 | 7.2728 | 7.2681 | 7.2915 | 7.2806 | 7.2693 | 10.7296 | 10.6876 | 10.683 | 10.7049 | 10.7139 | 10.6824 | 13.7816 | 13.7425 | 13.773 | 13.4206 | 13.421 | 13.3788 | 13.2315 | 13.1645 | 13.1949 | 13.4541 | 13.3976 | 13.362 | 8.4305 | 8.487 | 8.4393 | 13.2092 | 13.2131 | 13.2024 | 13.405 | 13.4526 | 13.4653
326 | o_LVDT (AI14) |  | -37.4322 | -37.4332 | -37.4324 | -37.4323 | -37.434 | -37.4331 | -37.433 | -37.4325 | -37.4334 | -37.4329 | -37.4335 | -37.4329 | -37.4328 | -37.4335 | -37.4329 | -37.4342 | -37.4333 | -37.4335 | -37.4337 | -37.4321 | -37.4325 | -37.4323 | -37.4339 | -37.4329 | -37.4327 | -37.4335 | -37.4328 | -37.4338 | -37.4332 | -37.4338 | -37.4335 | -37.4323 | -37.4332 | -37.4334 | -37.4324 | -37.4324 | -37.4328 | -37.4321 | -37.4331 | -37.4338 | -37.433 | -37.4329 | -37.433 | -37.434 | -37.4331 | -37.4316 | -37.4313 | -37.4331 | -37.4333 | -37.4328 | -37.4325 | -37.4335 | -37.4327 | -37.4324 | -37.4326 | -37.4322 | -37.4332 | -37.4317 | -37.4329 | -37.4323 | -37.4321 | -37.4319 | -37.4329 | -37.4326 | -37.432 | -37.4327 | -37.4326 | -37.4326 | -37.4331 | -37.4344 | -37.4323 | -37.4321 | -37.4333 | -37.4331 | -37.4328 | -37.4329 | -37.4325 | -37.4323 | -37.4326 | -37.4335 | -37.4338 | -37.4323 | -37.4334 | -37.4323 | -37.4335 | -37.4319 | -37.4339 | -37.4335 | -37.4317 | -37.4326 | -37.434 | -37.4321 | -37.4342 | -37.4334 | -37.4328 | -37.4333 | -37.4332 | -37.4332 | -37.4327 | -37.4334 | -37.4327 | -37.432 | -37.4335 | -37.4337 | -37.4326 | -37.4337 | -37.4323 | -37.432 | -37.4329 | -37.4331 | -37.4327 | -37.4326 | -37.4329 | -37.4324 | -37.4323 | -37.4335 | -37.433 | -37.4332 | -37.4326 | -37.4329 | -37.4327 | -37.4329 | -37.4324 | -37.4329 | -37.4328 | -37.4327 | -37.4319 | -37.4333 | -37.4329 | -37.4322 | -37.4319 | -37.4326 | -37.4328 | -37.433 | -37.4329 | -37.4324 | -37.4338 | -37.4325 | -37.4332 | -37.4326 | -37.4327 | -37.4328 | -37.4335 | -37.4328 | -37.4336 | -37.433 | -37.4331 | -37.4342 | -37.4333 | -37.4336 | -37.433 | -37.4328 | -37.4331 | -37.4325 | -37.4327 | -37.4323 | -37.4323 | -37.4329 | -37.4329 | -37.4324 | -37.4327 | -37.4318 | -37.4322 | -37.4332 | -37.4334 | -37.4334 | -37.4329 | -37.4326 | -37.4325 | -37.4321 | -37.4328 | -37.4331 | -37.4325 | -37.4327 | -37.4328 | -37.4323 | -37.4333 | -37.433 | -37.4327 | -37.433 | -37.4326 | -37.4323 | -37.4328 | -37.4328 | -37.4326 | -37.4324 | -37.4329 | -37.4321 | -37.4327 | -37.4334 | -37.4337 | -37.4329 | -37.4319 | -37.4328 | -37.4328 | -37.4324 | -37.4315 | -37.4328 | -37.4324 | -37.4327 | -37.4333 | -37.4332 | -37.4328 | -37.4329 | -37.4333 | -37.4338 | -37.433 | -37.4331 | -37.4328 | -37.4332 | -37.4321 | -37.4327 | -37.432 | -37.4325 | -37.4328 | -37.4323 | -37.4329 | -37.4326 | -37.4333 | -37.4323 | -37.4325 | -37.4332 | -37.4334 | -37.4327 | -37.433 | -37.4314 | -37.4332 | -37.434 | -37.4328 | -37.4335 | -37.4327 | -37.4323 | -37.4331 | -37.4333 | -37.4325 | -37.4323
327 | p_Spare15 (AI15) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
328 | a_Water Temp into Condenser (TE-82) (AI0) |  | 27.6021 | 27.1138 | 26.5739 | 20.0131 | 25.4186 | 44.8106 | 44.0981 | 44.3989 | 47.9532 | 20.627 | 24.847 | 28.8585 | 26.0266 | 25.979 | 25.8482 | 12.4576 | 12.4522 | 12.3534 | 11.7712 | 11.6617 | 11.542 | 13.0214 | 12.9077 | 12.7539 | 12.5297 | 12.4147 | 12.2925 | 11.6868 | 11.7121 | 11.6945 | 11.6133 | 11.5991 | 11.6294 | 11.621 | 11.7003 | 11.7871 | 12.0094 | 12.1021 | 12.2977 | 12.1133 | 12.2552 | 12.3396 | 17.8031 | 18.2117 | 20.2815 | 22.2195 | 20.2343 | 19.4981 | 18.7659 | 37.5454 | 35.5569 | 38.5649 | 28.5304 | 39.9277 | 44.2978 | 26.9598 | 30.973 | 28.1868 | 22.7969 | 18.2961 | 17.5048 | 19.1706 | 19.2579 | 19.2399 | 19.3284 | 19.195 | 19.2122 | 16.3518 | 16.3348 | 16.1146 | 15.946 | 15.8575 | 15.7966 | 15.5707 | 15.5261 | 15.421 | 15.5106 | 15.2922 | 14.4391 | 13.8599 | 16.2164 | 17.8913 | 13.3663 | 13.2669 | 13.1478 | 13.2412 | 13.371 | 13.4436 | 13.6418 | 13.7093 | 13.853 | 16.1733 | 16.0673 | 16.0418 | 16.064 | 16.1212 | 16.0748 | 17.7088 | 19.5885 | 19.5834 | 19.5744 | 19.5845 | 19.599 | 19.6388 | 19.6134 | 19.3662 | 19.8731 | 19.9867 | 20.0976 | 19.5893 | 19.5332 | 19.5603 | 19.4082 | 19.2273 | 19.0251 | 20.7719 | 20.7342 | 20.8174 | 15.4273 | 15.3216 | 15.2496 | 15.2471 | 15.1754 | 15.1093 | 13.9511 | 13.8172 | 13.6947 | 12.6948 | 13.0823 | 13.7749 | 18.1605 | 18.0699 | 17.7684 | 17.9092 | 17.8826 | 13.815 | 13.8442 | 13.8815 | 13.8543 | 13.8974 | 13.8801 | 13.8312 | 13.4268 | 13.3494 | 13.3756 | 15.9948 | 15.8921 | 15.852 | 15.8267 | 20.1856 | 20.0852 | 20.1214 | 20.136 | 20.5078 | 20.4149 | 20.3691 | 20.1037 | 19.9334 | 19.4516 | 28.874 | 28.8325 | 28.7274 | 28.699 | 28.4905 | 28.3242 | 28.2643 | 28.1149 | 21.4464 | 21.4876 | 21.5159 | 21.2924 | 21.2721 | 21.2758 | 21.2081 | 21.0269 | 20.8481 | 20.2567 | 19.6765 | 20.0889 | 13.6438 | 13.6113 | 13.5818 | 33.3389 | 36.6842 | 37.3747 | 37.4102 | 36.2679 | 35.6916 | 22.9187 | 37.6857 | 40.7735 | 40.0671 | 40.3214 | 40.6087 | 12.7142 | 12.6812 | 12.6039 | 13.639 | 13.5863 | 13.5706 | 12.6107 | 12.4486 | 12.2551 | 13.9622 | 13.9383 | 13.8689 | 13.8046 | 13.6867 | 13.6523 | 17.3045 | 17.5048 | 17.534 | 17.8022 | 17.7281 | 17.6796 | 19.6289 | 19.5284 | 19.3725 | 19.1337 | 19.015 | 18.9288 | 18.9337 | 18.8658 | 18.7066 | 18.1262 | 18.0776 | 18.0933 | 12.1947 | 11.0955 | 11.0197 | 22.8478 | 22.8397 | 22.8634 | 22.4285 | 22.2296 | 22.1522
329 | b_Water Temp out condenser (TE-83) (AI1) |  | 31.5564 | 30.0601 | 31.6703 | 39.6957 | 44.0714 | 30.3964 | 30.2094 | 29.9294 | 30.9877 | 32.1909 | 43.6189 | 33.9653 | 37.619 | 36.9253 | 33.4177 | 16.3561 | 16.3462 | 19.3143 | 18.3466 | 17.5733 | 15.8671 | 16.1684 | 16.8745 | 15.2569 | 16.5049 | 15.7798 | 16.5462 | 24.5081 | 26.209 | 24.9913 | 25.2999 | 25.2507 | 24.5418 | 24.6348 | 24.8275 | 27.3191 | 24.9972 | 26.8587 | 25.2799 | 27.744 | 28.1517 | 26.7868 | 33.9203 | 25.0308 | 38.5371 | 24.8292 | 22.9492 | 25.4844 | 21.6727 | 31.7105 | 31.934 | 40.3174 | 49.6287 | 36.9957 | 37.9361 | 39.2377 | 39.4004 | 41.8507 | 46.9558 | 33.0344 | 42.8495 | 44.9395 | 47.2846 | 45.8457 | 50.1188 | 47.1407 | 48.3521 | 36.4704 | 35.9823 | 36.2697 | 32.8356 | 34.3842 | 32.7164 | 31.7966 | 32.1115 | 32.9647 | 20.0584 | 15.5873 | 15.4895 | 16.5552 | 19.5249 | 15.1391 | 21.4277 | 19.7597 | 20.6889 | 24.9823 | 24.8287 | 29.4682 | 27.2473 | 25.5081 | 27.071 | 36.5213 | 42.202 | 37.9827 | 38.8177 | 36.3446 | 35.3697 | 37.5654 | 47.5238 | 45.5295 | 48.5766 | 50.1006 | 46.1432 | 46.632 | 49.6106 | 46.0687 | 53.156 | 53.7208 | 49.2415 | 52.4622 | 49.8108 | 48.4789 | 52.862 | 54.0405 | 50.7946 | 57.664 | 61.944 | 61.3853 | 38.7612 | 39.793 | 36.3515 | 40.8879 | 35.7884 | 37.9032 | 29.6009 | 30.4048 | 29.329 | 18.7343 | 18.253 | 19.3824 | 14.3899 | 15.2207 | 47.0884 | 47.5911 | 46.9919 | 30.6469 | 29.6385 | 29.7104 | 27.5687 | 28.6781 | 28.6398 | 29.7591 | 29.9805 | 30.0481 | 30.5321 | 12.702 | 13.6852 | 14.3204 | 13.0383 | 47.837 | 48.3072 | 34.9512 | 50.805 | 48.2934 | 49.9925 | 55.7676 | 59.7699 | 58.827 | 54.7037 | 34.7344 | 34.3884 | 34.4314 | 31.0737 | 38.1057 | 35.0242 | 33.4602 | 36.5148 | 39.1721 | 42.9336 | 39.0972 | 47.2853 | 42.5878 | 46.753 | 44.869 | 50.6929 | 51.1671 | 36.9144 | 48.3349 | 39.7977 | 25.8963 | 23.517 | 25.3456 | 49.6756 | 37.7648 | 40.5525 | 35.2966 | 37.0462 | 35.5421 | 42.004 | 47.9044 | 38.4117 | 40.1793 | 36.5618 | 39.2312 | 22.381 | 22.1141 | 22.1801 | 34.9776 | 35.7639 | 33.8167 | 33.5131 | 32.4609 | 33.0911 | 21.8727 | 21.3105 | 19.6911 | 20.9913 | 21.1958 | 20.5297 | 44.9197 | 47.9299 | 47.2804 | 48.4287 | 46.177 | 49.6908 | 53.6828 | 54.1247 | 53.4829 | 51.7569 | 51.2061 | 57.7445 | 56.3868 | 51.9502 | 54.8903 | 61.2735 | 56.6091 | 58.1285 | 33.711 | 33.8634 | 33.4014 | 61.5977 | 62.4826 | 61.2339 | 63.0719 | 63.2921 | 64.1162
330 | c_Condenser Temperature (TE-03) (AI2) |  | 62.9296 | 62.6659 | 62.5821 | 48.8505 | 58.461 | 63.2277 | 62.7848 | 61.703 | 61.6422 | 57.0884 | 62.7943 | 64.121 | 63.9272 | 63.4644 | 63.1777 | 19.9312 | 19.8616 | 19.815 | 19.3698 | 19.2681 | 19.1512 | 19.9629 | 19.8612 | 19.7566 | 19.5568 | 19.441 | 19.2885 | 27.0076 | 27.0194 | 27.0685 | 27.0808 | 27.1023 | 27.0191 | 27.1188 | 27.1549 | 27.0483 | 28.5324 | 28.7134 | 28.6271 | 28.5391 | 28.7299 | 28.5924 | 38.6037 | 38.5102 | 43.8063 | 44.3766 | 44.8269 | 44.8698 | 44.1927 | 58.3007 | 56.3818 | 60.5385 | 61.1673 | 64.9049 | 63.0149 | 48.0944 | 47.9626 | 47.7645 | 47.8734 | 46.5247 | 46.4833 | 37.2105 | 37.3423 | 37.2127 | 36.9054 | 36.8049 | 36.7335 | 24.0654 | 24.1051 | 24.0312 | 24.2811 | 24.4752 | 24.4257 | 24.376 | 24.2513 | 24.0958 | 21.9118 | 22.0541 | 22.3482 | 19.0591 | 18.4114 | 18.1483 | 27.4108 | 27.3923 | 27.2633 | 26.5907 | 26.6012 | 26.5479 | 26.7285 | 26.9909 | 27.5861 | 37.9778 | 37.8682 | 37.8861 | 37.8739 | 37.927 | 37.8274 | 38.0712 | 47.042 | 47.0223 | 47.0176 | 47.0333 | 47.0596 | 46.996 | 46.9506 | 46.9263 | 48.2574 | 48.2035 | 48.141 | 47.19 | 47.0855 | 47.0239 | 46.3966 | 46.255 | 46.1172 | 47.9247 | 47.9743 | 47.9002 | 37.6329 | 37.8385 | 37.8883 | 37.7473 | 37.7458 | 37.6416 | 24.1266 | 24.0718 | 24.0483 | 19.5164 | 19.3356 | 19.1964 | 18.6829 | 18.4405 | 36.5646 | 36.4489 | 36.7001 | 24.0822 | 24.0712 | 24.0346 | 24.2881 | 24.0144 | 23.9092 | 23.8813 | 23.7302 | 23.7073 | 23.6865 | 18.6384 | 18.5637 | 18.592 | 18.5524 | 47.0129 | 47.3693 | 47.1603 | 47.3929 | 46.9336 | 46.8659 | 47.1338 | 46.1954 | 46.3654 | 46.3368 | 66.6618 | 66.7422 | 66.7591 | 67.0782 | 66.1608 | 65.3907 | 65.4746 | 65.2492 | 62.4113 | 60.9815 | 57.1621 | 48.6308 | 48.5012 | 48.1724 | 46.2014 | 46.1408 | 46.2205 | 50.8492 | 54.2135 | 57.7275 | 28.564 | 28.5002 | 28.3152 | 59.874 | 60.8127 | 60.2066 | 58.2772 | 57.745 | 57.3838 | 48.0522 | 57.8868 | 57.3028 | 55.1901 | 55.1102 | 55.8277 | 28.7745 | 28.7561 | 28.5535 | 23.5561 | 23.3952 | 23.6325 | 23.9307 | 23.7626 | 23.2708 | 19.7988 | 19.7113 | 19.6105 | 19.4813 | 19.0958 | 18.9903 | 37.2631 | 37.0439 | 37.0999 | 37.1578 | 37.0797 | 36.9324 | 48.2986 | 48.117 | 48.1633 | 46.9718 | 46.9266 | 46.8632 | 46.1423 | 46.2223 | 46.2472 | 46.7232 | 46.5312 | 46.4658 | 23.7818 | 24.0447 | 23.7941 | 46.0836 | 46.1058 | 46.1002 | 46.693 | 46.9333 | 46.8215
331 | d_Condenser Pressure (PT-04) (AI3) |  | 11.9929 | 11.9913 | 11.9486 | 12.1829 | 12.1897 | 12.1758 | 12.3234 | 12.2986 | 12.247 | 12.3795 | 12.3763 | 12.3944 | 12.4321 | 12.4197 | 12.4183 | 6.1392 | 6.1391 | 6.1442 | 6.1582 | 6.1425 | 6.1118 | 6.1449 | 6.1444 | 6.1531 | 6.1653 | 6.1284 | 6.1278 | 7.2669 | 7.2594 | 7.2742 | 7.2789 | 7.2821 | 7.2779 | 7.2632 | 7.2931 | 7.2651 | 7.2577 | 7.2824 | 7.2833 | 7.2573 | 7.3099 | 7.2912 | 9.469 | 9.4358 | 9.4521 | 9.4273 | 9.4804 | 9.4698 | 9.4274 | 11.9682 | 11.9654 | 12.0007 | 12.4077 | 12.3619 | 12.3643 | 11.9259 | 11.9188 | 11.9041 | 11.7358 | 11.725 | 11.7686 | 9.4575 | 9.4474 | 9.4608 | 9.4097 | 9.4258 | 9.4157 | 7.2809 | 7.3048 | 7.2856 | 7.2512 | 7.296 | 7.2982 | 7.2917 | 7.2902 | 7.2674 | 6.1682 | 6.162 | 6.1299 | 6.1246 | 6.1495 | 6.1304 | 7.2764 | 7.3129 | 7.2779 | 7.2458 | 7.2321 | 7.2521 | 7.2639 | 7.2681 | 7.2748 | 9.4646 | 9.4568 | 9.4458 | 9.4211 | 9.4422 | 9.4284 | 9.447 | 11.9851 | 11.9757 | 11.9896 | 11.9809 | 11.9819 | 11.9632 | 11.9734 | 11.9787 | 12.3671 | 12.3495 | 12.3358 | 11.9933 | 11.9575 | 11.9404 | 11.7946 | 11.7399 | 11.7183 | 12.3818 | 12.4014 | 12.3889 | 9.4765 | 9.4692 | 9.4994 | 9.4585 | 9.4803 | 9.4576 | 7.2836 | 7.3135 | 7.2984 | 6.1465 | 6.1719 | 6.1916 | 6.2145 | 6.1589 | 9.4553 | 9.4339 | 9.4595 | 7.2835 | 7.2974 | 7.2894 | 7.3153 | 7.3022 | 7.2911 | 7.296 | 7.2606 | 7.2703 | 7.2746 | 6.2247 | 6.2416 | 6.2119 | 6.1975 | 11.9773 | 12.0291 | 12.0422 | 12.0188 | 11.9997 | 11.9718 | 11.971 | 11.8036 | 11.8139 | 11.7956 | 11.9435 | 11.9562 | 11.9185 | 11.9464 | 11.8135 | 11.8332 | 11.8035 | 11.7258 | 12.2648 | 12.3023 | 12.3003 | 11.9294 | 11.8706 | 11.897 | 11.6961 | 11.6503 | 11.6642 | 11.9938 | 11.9245 | 11.9493 | 7.3001 | 7.3065 | 7.2486 | 12.3752 | 12.3698 | 12.3444 | 11.7651 | 11.7256 | 11.7195 | 11.9014 | 11.9061 | 11.9013 | 11.9404 | 11.9234 | 11.9095 | 7.3014 | 7.3021 | 7.2585 | 7.3153 | 7.2716 | 7.296 | 7.2795 | 7.2583 | 7.2616 | 6.1551 | 6.1336 | 6.1437 | 6.1759 | 6.157 | 6.1401 | 9.4701 | 9.4141 | 9.4158 | 9.4246 | 9.4238 | 9.3933 | 12.3893 | 12.345 | 12.3691 | 11.9593 | 11.9658 | 11.9146 | 11.7701 | 11.7095 | 11.7228 | 12.0386 | 11.9782 | 11.9573 | 7.2411 | 7.302 | 7.2458 | 11.7421 | 11.7469 | 11.7364 | 11.9399 | 11.9883 | 12.0005
332 | e_Liquid Reciever Temperature (AI4) |  | 35.77 | 35.7491 | 35.387 | 36.7821 | 36.7457 | 35.8513 | 36.1013 | 36.1943 | 36.1801 | 35.9573 | 36.2061 | 36.3279 | 35.845 | 35.9299 | 35.9001 | 17.8168 | 17.8047 | 17.7367 | 17.8598 | 17.7771 | 17.6045 | 17.8895 | 17.8429 | 17.8426 | 17.8509 | 17.787 | 17.6719 | 20.9027 | 20.875 | 20.9086 | 20.9696 | 20.9914 | 21.049 | 20.583 | 20.6927 | 20.833 | 20.4365 | 20.6213 | 20.4039 | 20.3054 | 20.3683 | 20.3179 | 28.9708 | 28.7566 | 28.819 | 28.4852 | 28.3413 | 28.3495 | 28.1883 | 35.6903 | 35.5584 | 35.8228 | 36.6247 | 35.4899 | 35.9645 | 34.7294 | 34.68 | 34.6276 | 34.2346 | 34.1851 | 34.6106 | 29.7919 | 29.6403 | 29.7927 | 29.731 | 29.5642 | 29.455 | 21.8173 | 21.8672 | 21.609 | 21.6596 | 21.7639 | 21.7194 | 21.698 | 21.508 | 21.4127 | 17.2275 | 17.1544 | 17.0246 | 17.2791 | 17.2687 | 17.1197 | 19.3802 | 19.5041 | 19.4294 | 19.8333 | 19.9069 | 19.9265 | 19.9314 | 19.9789 | 19.9628 | 28.2511 | 28.1549 | 28.1877 | 27.7717 | 27.9333 | 27.8063 | 27.5638 | 35.1703 | 35.1374 | 35.1211 | 35.1275 | 35.1411 | 34.968 | 35.0275 | 35.0547 | 35.5169 | 35.4045 | 35.5792 | 34.0782 | 33.9412 | 33.8676 | 33.6533 | 33.4583 | 33.1871 | 35.291 | 35.3984 | 35.336 | 26.7387 | 27.0113 | 26.8133 | 26.5493 | 26.5671 | 26.4097 | 19.5811 | 19.5401 | 19.3927 | 16.1917 | 16.2726 | 16.384 | 16.6414 | 16.3755 | 27.8706 | 27.5711 | 27.7412 | 19.1731 | 19.1998 | 19.1668 | 19.0656 | 18.9145 | 18.8172 | 18.7174 | 18.1569 | 18.1129 | 18.0443 | 14.4297 | 14.4271 | 14.4092 | 14.451 | 33.076 | 33.2669 | 33.0264 | 33.2927 | 32.2822 | 32.212 | 32.5648 | 31.3818 | 32.2057 | 31.5219 | 35.9596 | 36.12 | 35.8515 | 35.8122 | 35.3043 | 35.5121 | 35.4678 | 35.1191 | 36.357 | 36.6341 | 36.6941 | 35.5966 | 35.2948 | 35.3649 | 34.878 | 34.9249 | 35.1476 | 36.6823 | 36.6097 | 36.3613 | 20.2797 | 20.2475 | 20.0054 | 37.6986 | 37.483 | 37.5144 | 35.1415 | 35.0416 | 35.0195 | 35.8057 | 35.6554 | 35.5957 | 36.7519 | 36.5958 | 36.5478 | 20.3036 | 20.4673 | 20.3016 | 22.6112 | 22.4146 | 22.4245 | 22.4484 | 22.279 | 22.4022 | 19.0951 | 19.0934 | 19.0829 | 19.1539 | 19.2934 | 19.1855 | 30.9115 | 30.6281 | 30.6611 | 30.2285 | 30.1831 | 30.0949 | 38.4898 | 38.181 | 38.1918 | 36.7929 | 36.7892 | 36.5988 | 35.9225 | 35.7306 | 35.7006 | 38.4095 | 38.1857 | 38.3361 | 21.6485 | 21.7534 | 21.5388 | 37.0339 | 36.9675 | 36.9494 | 37.5945 | 38.0217 | 38.2088
333 | f_Liquid Receiver Pressure (AI5) |  | 11.8361 | 11.8205 | 11.7817 | 12.0282 | 12.0407 | 12.0279 | 12.1775 | 12.1563 | 12.1147 | 12.2391 | 12.2478 | 12.2737 | 12.3062 | 12.3017 | 12.294 | 6.1313 | 6.1334 | 6.1218 | 6.1491 | 6.1417 | 6.0926 | 6.1336 | 6.127 | 6.1366 | 6.1488 | 6.1328 | 6.1328 | 7.2159 | 7.2193 | 7.2239 | 7.233 | 7.2347 | 7.2475 | 7.2225 | 7.2669 | 7.2384 | 7.2252 | 7.2503 | 7.2503 | 7.2287 | 7.273 | 7.2628 | 9.365 | 9.3366 | 9.3597 | 9.3326 | 9.3891 | 9.371 | 9.3278 | 11.8453 | 11.8269 | 11.8652 | 12.2716 | 12.2159 | 12.2319 | 11.7859 | 11.7801 | 11.7777 | 11.6087 | 11.5813 | 11.6373 | 9.3693 | 9.3499 | 9.3633 | 9.3259 | 9.3248 | 9.3142 | 7.245 | 7.2895 | 7.2573 | 7.2306 | 7.2798 | 7.2875 | 7.2777 | 7.2634 | 7.2565 | 6.1587 | 6.1432 | 6.1246 | 6.1205 | 6.121 | 6.1112 | 7.2537 | 7.2776 | 7.2363 | 7.2022 | 7.1896 | 7.1971 | 7.2233 | 7.2063 | 7.2423 | 9.3762 | 9.3518 | 9.3342 | 9.3318 | 9.3184 | 9.3197 | 9.3462 | 11.861 | 11.8484 | 11.8598 | 11.8638 | 11.8644 | 11.8453 | 11.8421 | 11.8404 | 12.2514 | 12.2132 | 12.1976 | 11.8811 | 11.8324 | 11.8124 | 11.664 | 11.6206 | 11.5772 | 12.2381 | 12.2675 | 12.269 | 9.3707 | 9.3969 | 9.4153 | 9.388 | 9.3863 | 9.3796 | 7.2553 | 7.2761 | 7.273 | 6.145 | 6.1545 | 6.1775 | 6.2213 | 6.1578 | 9.3429 | 9.3465 | 9.3464 | 7.2667 | 7.2714 | 7.2665 | 7.299 | 7.268 | 7.2699 | 7.259 | 7.2351 | 7.2382 | 7.2564 | 6.2136 | 6.2226 | 6.2047 | 6.1822 | 11.8405 | 11.9166 | 11.9325 | 11.9158 | 11.87 | 11.8491 | 11.8451 | 11.6693 | 11.6768 | 11.6704 | 11.7849 | 11.8095 | 11.7736 | 11.7846 | 11.646 | 11.6827 | 11.6451 | 11.5775 | 12.1282 | 12.1577 | 12.173 | 11.7633 | 11.71 | 11.7269 | 11.5349 | 11.5058 | 11.5369 | 11.8559 | 11.7879 | 11.828 | 7.2954 | 7.3009 | 7.2331 | 12.2308 | 12.219 | 12.2033 | 11.6237 | 11.5755 | 11.5648 | 11.7495 | 11.7487 | 11.7642 | 11.8015 | 11.7913 | 11.7835 | 7.2729 | 7.2907 | 7.2519 | 7.2819 | 7.2433 | 7.2773 | 7.2578 | 7.2244 | 7.2382 | 6.131 | 6.1472 | 6.1261 | 6.1583 | 6.1441 | 6.1279 | 9.3561 | 9.313 | 9.3083 | 9.3101 | 9.3258 | 9.2793 | 12.2321 | 12.2153 | 12.2155 | 11.8196 | 11.8128 | 11.7727 | 11.6261 | 11.5702 | 11.5826 | 11.8962 | 11.8464 | 11.8186 | 7.2041 | 7.2646 | 7.2147 | 11.5996 | 11.6046 | 11.5965 | 11.7805 | 11.8324 | 11.8661
334 | g_differential pressure (AI6) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.000872 | 0.00049 | 0.000292 | 0.000411 | 0.000514 | 0.000865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001686 | 0.001747 | 0.001749 | 0.004556 | 0.004408 | 0.004838 | 0.033904 | 0.033879 | 0.033606 | 0.033046 | 0.032879 | 0.032334
335 | h_Spare FLOWMETER (AI7) (AI7) |  | -10.0005 | -10.0007 | -10.0008 | -10.0003 | -10.0008 | -10.0009 | -10.0004 | -10.0004 | -10.0008 | -10.0002 | -10.0009 | -10.0007 | -10.0007 | -10.0008 | -10.0005 | -10.0008 | -10.0008 | -10.0004 | -10.0001 | -10.0008 | -10.0008 | -10.0001 | -10.0002 | -10.0002 | -10.0002 | -10.0008 | -10.0007 | -10.0007 | -10.0007 | -10.0009 | -10.0003 | -10.0007 | -10.0007 | -10.0004 | -10.0006 | -10.0006 | -10.0002 | -10.0008 | -10.0009 | -10.0006 | -10.0004 | -10.0005 | -10.0009 | -10.0003 | -10.0006 | -10.0005 | -10.0008 | -10 | -10.0007 | -10.0005 | -10.0009 | -10.0007 | -10.0007 | -10.0008 | -10.0003 | -10.0007 | -10.0005 | -10.0006 | -10.0007 | -10.0008 | -10.0003 | -10.0008 | -10.0004 | -10.0001 | -10.0007 | -10.0007 | -10.001 | -10.0006 | -10.0005 | -10.0006 | -10.0002 | -10.0006 | -10.0005 | -10 | -10 | -10.0001 | -10.0006 | -10.0001 | -10.0002 | -10.0005 | -10.0004 | -10.0007 | -10.0006 | -10.0003 | -10.0005 | -10.0003 | -10.001 | -10 | -10.0006 | -10.0008 | -10.0002 | -10.0003 | -10 | -10.0001 | -10.0005 | -10.0008 | -10.001 | -10.0004 | -10.0009 | -10.0008 | -10.0009 | -10.0004 | -10.0002 | -10.0006 | -10.0009 | -10.0001 | -10.0006 | -10.0007 | -10.0007 | -10.0007 | -10.0006 | -10.0006 | -10.0006 | -10.0005 | -10.0007 | -10.0007 | -10.0008 | -10.0005 | -10.0005 | -10.0009 | -10.001 | -10.0007 | -10.0008 | -10.0003 | -10.0007 | -10.0003 | -10.0006 | -10.0008 | -9.9999 | -10.0003 | -10.0003 | -10.0004 | -10.0007 | -10.0006 | -10.0003 | -10.0005 | -10.0007 | -10.0002 | -10.0006 | -10.0003 | -10.0003 | -10.0005 | -10.001 | -10.0003 | -10.0002 | -10.0006 | -10.0005 | -10.0006 | -10.0005 | -10.0005 | -10.0003 | -10.0005 | -10.0008 | -10.0006 | -10.0004 | -10.0007 | -10.0007 | -10.0003 | -10.0005 | -10.0008 | -10.0006 | -10.0007 | -10.0007 | -10.0004 | -10.0009 | -10.0005 | -10.0005 | -10.0003 | -10.0008 | -10.0004 | -10.0007 | -10.0007 | -10.0004 | -10.001 | -10.0003 | -10.0007 | -10.0007 | -10.0002 | -10.0004 | -10.0007 | -10.0007 | -10.0004 | -10.0009 | -10.0008 | -10.0004 | -10.0007 | -10.0004 | -10.0008 | -10.0007 | -10.0007 | -10.0001 | -10.0004 | -10.0006 | -10.0011 | -10.0003 | -10.0005 | -10.0007 | -10.0002 | -10.0006 | -10.0004 | -10.0002 | -10.0008 | -10.0004 | -10.0006 | -10.0004 | -10.0006 | -10.0003 | -10.0012 | -10.0006 | -10.0004 | -10.0005 | -10.0004 | -10.0007 | -10.0006 | -10.0007 | -10.0006 | -10.0006 | -10.0005 | -10.0005 | -10.0003 | -10.0006 | -10.0007 | -10.0003 | -10.0005 | -10.0004 | -10.0005 | -10.0009 | -10.0007 | -10.0004 | -10.0002 | -10.0006 | -10.0005 | -10.0006 | -10.0006 | -10.0006 | -10.0005
336 | i_Condenser Temperature Mixed Water (TE-99) (AI8) |  | 19.2906 | 19.3871 | 19.3458 | 19.4598 | 19.4978 | 18.8197 | 18.6569 | 18.2767 | 18.2431 | 18.384 | 18.5332 | 18.1784 | 17.6965 | 17.6994 | 17.7379 | 9.7819 | 9.7688 | 9.8142 | 9.7272 | 9.653 | 9.5889 | 9.5679 | 9.5816 | 9.5113 | 9.5575 | 9.5714 | 9.5761 | 11.1266 | 11.1376 | 11.1389 | 10.9727 | 11.003 | 11.1087 | 11.0127 | 11.085 | 11.0293 | 11.2877 | 11.4187 | 11.5735 | 12.1467 | 12.0594 | 11.9796 | 14.4067 | 14.0882 | 14.3368 | 13.7091 | 13.6761 | 13.6356 | 13.4691 | 17.4024 | 17.4241 | 17.7617 | 18.5737 | 18.0213 | 17.731 | 17.8724 | 17.7443 | 17.6769 | 17.7128 | 17.3317 | 17.4971 | 19.808 | 19.9041 | 19.9659 | 20.4077 | 20.2645 | 20.1412 | 17.0511 | 17.0484 | 16.9151 | 16.6319 | 16.6032 | 16.4211 | 16.2386 | 16.1021 | 16.1198 | 13.3157 | 13.2307 | 13.1771 | 13.5392 | 13.3848 | 13.0379 | 12.2625 | 12.1277 | 12.1264 | 12.7788 | 12.9195 | 13.0075 | 13.395 | 13.4606 | 13.4374 | 16.5466 | 16.3726 | 16.3156 | 16.2173 | 16.3049 | 16.3851 | 16.484 | 20.1125 | 20.1809 | 20.1349 | 20.106 | 20.1045 | 20.1726 | 20.0612 | 20.2161 | 20.3487 | 20.3079 | 20.4857 | 20.4433 | 20.3703 | 20.3401 | 20.4168 | 20.2551 | 20.2584 | 21.6441 | 21.8569 | 21.795 | 16.2158 | 16.3466 | 16.0156 | 15.6745 | 15.6702 | 15.6224 | 14.3486 | 14.3626 | 14.3192 | 11.6936 | 11.6831 | 11.5675 | 11.2354 | 11.1987 | 18.6854 | 18.7635 | 18.8396 | 13.8476 | 13.9453 | 14.0798 | 14.3295 | 14.2844 | 14.3086 | 14.2848 | 13.7626 | 13.8227 | 13.755 | 11.6006 | 11.5845 | 11.5873 | 11.6532 | 20.7456 | 20.7198 | 20.5122 | 20.7121 | 21.2238 | 21.0159 | 21.1353 | 20.9616 | 21.0294 | 20.5099 | 22.2594 | 22.3707 | 22.3793 | 22.2241 | 21.8315 | 21.857 | 21.8507 | 21.685 | 21.5696 | 21.698 | 21.667 | 22.1164 | 22.0407 | 21.9359 | 21.8219 | 21.9778 | 22.0802 | 20.8936 | 21.2423 | 20.7722 | 13.8517 | 13.7954 | 13.7348 | 20.1063 | 19.8598 | 19.6414 | 19.6878 | 19.685 | 19.6828 | 20.7625 | 20.6487 | 19.9174 | 19.5088 | 19.6435 | 19.6723 | 12.8433 | 12.8205 | 12.8107 | 14.3313 | 14.3257 | 14.3095 | 13.3425 | 13.2086 | 13.0198 | 13.3733 | 13.2899 | 13.2861 | 13.2935 | 13.1972 | 13.2637 | 17.7919 | 17.9882 | 18.3248 | 18.4825 | 18.5712 | 18.4993 | 20.2676 | 20.1839 | 20.1722 | 19.9194 | 19.8093 | 19.6875 | 19.4705 | 19.5432 | 19.5555 | 19.5099 | 19.366 | 19.3615 | 11.9983 | 11.7649 | 11.6452 | 24.2161 | 24.1472 | 24.1436 | 23.9249 | 23.6943 | 23.2803
337 | j_Condenser Water Pressure (AI9) |  | 0.85321 | 0.85122 | 0.85111 | 0.84233 | 0.83832 | 0.83227 | 0.85454 | 0.83891 | 0.83967 | 0.84913 | 0.85178 | 0.85083 | 0.86545 | 0.86356 | 0.86697 | 0.75514 | 0.76014 | 0.75889 | 0.7576 | 0.75877 | 0.76371 | 0.77231 | 0.77226 | 0.77313 | 0.77561 | 0.7745 | 0.77129 | 0.79165 | 0.79492 | 0.78755 | 0.7946 | 0.7891 | 0.78814 | 0.79494 | 0.7851 | 0.79458 | 0.78678 | 0.78851 | 0.7847 | 0.79285 | 0.79355 | 0.7985 | 0.80741 | 0.80061 | 0.80829 | 0.81589 | 0.81818 | 0.81505 | 0.80644 | 0.83505 | 0.83889 | 0.84101 | 0.85089 | 0.85682 | 0.84989 | 0.84845 | 0.83219 | 0.83379 | 0.82851 | 0.84821 | 0.84006 | 0.81011 | 0.82458 | 0.81364 | 0.81887 | 0.81031 | 0.81495 | 0.7859 | 0.77859 | 0.77429 | 0.78298 | 0.77174 | 0.77678 | 0.77665 | 0.78153 | 0.78145 | 0.76473 | 0.76053 | 0.76639 | 0.75385 | 0.76298 | 0.7556 | 0.8051 | 0.80852 | 0.79691 | 0.80054 | 0.81815 | 0.80575 | 0.82023 | 0.81863 | 0.80933 | 0.82356 | 0.81816 | 0.83035 | 0.83285 | 0.834 | 0.82575 | 0.8455 | 0.88602 | 0.88237 | 0.87022 | 0.88039 | 0.86953 | 0.88627 | 0.8798 | 0.87788 | 0.87946 | 0.86777 | 0.87987 | 0.88607 | 0.89074 | 0.88329 | 0.86734 | 0.87937 | 0.87234 | 0.88731 | 0.89129 | 0.88732 | 0.86359 | 0.86233 | 0.87498 | 0.86526 | 0.86759 | 0.85954 | 0.82908 | 0.81388 | 0.82749 | 0.79024 | 0.79195 | 0.78973 | 0.79159 | 0.78247 | 0.85953 | 0.85633 | 0.85664 | 0.84425 | 0.83871 | 0.8437 | 0.85928 | 0.85466 | 0.85649 | 0.85343 | 0.86557 | 0.86467 | 0.8636 | 0.84704 | 0.85785 | 0.86048 | 0.85771 | 0.94021 | 0.9453 | 0.93437 | 0.94139 | 0.94299 | 0.94473 | 0.9543 | 0.95188 | 0.94431 | 0.94414 | 0.89759 | 0.8997 | 0.88977 | 0.90285 | 0.89589 | 0.88882 | 0.8896 | 0.89979 | 0.88323 | 0.88674 | 0.88133 | 0.89194 | 0.89614 | 0.89232 | 0.88896 | 0.88111 | 0.89284 | 0.86052 | 0.8669 | 0.85092 | 0.80847 | 0.81164 | 0.80792 | 0.86945 | 0.86838 | 0.86886 | 0.86818 | 0.87061 | 0.88299 | 0.85572 | 0.86431 | 0.86321 | 0.83776 | 0.8445 | 0.84871 | 0.79177 | 0.78663 | 0.78521 | 0.78821 | 0.78602 | 0.7899 | 0.78688 | 0.78821 | 0.78488 | 0.78585 | 0.78518 | 0.78874 | 0.78623 | 0.78693 | 0.78641 | 0.79035 | 0.79254 | 0.79765 | 0.7922 | 0.7999 | 0.79644 | 0.84557 | 0.84405 | 0.84008 | 0.83645 | 0.83228 | 0.83336 | 0.82553 | 0.8334 | 0.83634 | 0.81804 | 0.82347 | 0.81361 | 0.78038 | 0.7799 | 0.77494 | 0.82771 | 0.82616 | 0.82535 | 0.82557 | 0.83138 | 0.81939
338 | k_spare (AI10) |  | -25.001 | -25.0005 | -25.0004 | -25.0007 | -24.9999 | -25.0005 | -25.0003 | -25.0008 | -25.0004 | -25.001 | -25.0004 | -25.0006 | -25.0005 | -25.0007 | -25.0006 | -25.0003 | -25.0003 | -25.0002 | -25.0012 | -25.0006 | -24.9999 | -25.0003 | -24.9997 | -25.0003 | -25.0006 | -25 | -25.0003 | -25.0005 | -25.0004 | -25.0007 | -25.0009 | -25.0007 | -25.0008 | -25.0007 | -25.0004 | -25.0005 | -25.0003 | -25.0005 | -25.0004 | -25.0005 | -25 | -25.0004 | -25.0002 | -24.9999 | -25.0006 | -25.0007 | -25.0007 | -25.0002 | -25.0006 | -25.0003 | -25.0002 | -25.001 | -25.0007 | -25.0001 | -25.0006 | -25.0001 | -25.0009 | -25.0005 | -25.0005 | -25.0003 | -25.001 | -25.0007 | -25.0011 | -25.0003 | -25.0004 | -25.0004 | -25.0009 | -25.0002 | -25.0007 | -25.0006 | -25.0006 | -24.9999 | -24.9999 | -25.0008 | -25.0005 | -25.0007 | -25.0004 | -25 | -25.0004 | -25 | -25.0006 | -25.0008 | -25.0007 | -25.0005 | -24.9999 | -24.9999 | -25.0006 | -25.0003 | -25.0002 | -25.0007 | -25.0005 | -25.0007 | -25.0005 | -25.0005 | -25.0002 | -25.0005 | -25.0007 | -25.0009 | -25.0005 | -25.0003 | -25.0001 | -25.001 | -25.0004 | -25.0006 | -25.0007 | -25.0002 | -25.0005 | -25.0006 | -25.0005 | -25.0005 | -25.0004 | -25.0004 | -25.0008 | -25.0007 | -24.9998 | -25.0005 | -25.0007 | -25.0005 | -25.0007 | -25.0003 | -25 | -25.0005 | -25.0006 | -25.0005 | -25 | -25.0004 | -25.0005 | -24.9997 | -25.0006 | -25.0001 | -25.0009 | -25.0002 | -24.9999 | -25.0004 | -25.0003 | -25.0005 | -25.0008 | -25.0005 | -24.9996 | -25.001 | -25.0005 | -25.0004 | -25.0006 | -25.0006 | -25.0001 | -25.0007 | -25.0002 | -25.0008 | -25.0004 | -25.0006 | -25.0007 | -25.0008 | -25.0003 | -25.0006 | -25.0013 | -25.0005 | -25.0007 | -25.0007 | -25.0003 | -25.0007 | -25.0012 | -25.0008 | -25.0002 | -25.0007 | -25.0001 | -25.0005 | -25.0007 | -25.0002 | -25.0006 | -25.0004 | -25.0008 | -25.0004 | -25.0008 | -25.0005 | -25.0003 | -25.0007 | -25.0012 | -25.0008 | -25.0001 | -25.0008 | -25.0003 | -24.9997 | -25.0007 | -25.0007 | -25.0013 | -25.0006 | -25.0008 | -25.0003 | -25.0003 | -25.0013 | -25.0003 | -25.0008 | -25.0005 | -25.0009 | -25.0005 | -25.0005 | -25.0001 | -25.0005 | -25.0004 | -25.0011 | -25.0004 | -25.0006 | -25.0006 | -25.0005 | -25.0003 | -25.0006 | -25.0001 | -25.0007 | -25.0002 | -25.0005 | -25.0005 | -25.0007 | -25.0001 | -25.0004 | -25.0004 | -25.0008 | -25.0006 | -25.0004 | -25.0006 | -25.0007 | -25.0008 | -25.0004 | -25.0002 | -25.0004 | -25.0003 | -25.0003 | -25.0006 | -25.0009 | -25.0009 | -25.0001 | -25.0002 | -25.0004 | -25.0003 | -25.0003 | -25.001 | -25.0005
339 | l_Oil flow_Coriolis (AI11) |  | 0.8232 | 1.2957 | 0.58466 | 2.5652 | 2.2198 | 3.585 | 3.2995 | 3.4562 | 3.4459 | 3.0125 | 3.3249 | 3.3453 | 2.6173 | 2.5554 | 2.548 | 1.7097 | 1.548 | 2.0649 | 2.4146 | 1.9063 | 2.8224 | 1.0809 | 3.3334 | 1.7294 | 2.1767 | 2.3383 | 2.6578 | 1.6925 | 1.7112 | 1.5511 | 1.7967 | 1.7283 | 1.7522 | 1.727 | 1.7675 | 1.7125 | 1.7026 | 1.7455 | 1.7419 | 1.6737 | 1.5884 | 1.6711 | 2.7545 | 2.391 | 2.5158 | 2.7106 | 2.8878 | 2.6815 | 3.077 | 3.449 | 3.4526 | 3.5135 | 3.3598 | 3.3923 | 3.2014 | 3.4012 | 3.2829 | 3.4435 | 3.1465 | 3.3399 | 3.4754 | 3.3203 | 3.1158 | 2.9665 | 3.3055 | 3.3343 | 3.4 | 1.2898 | -0.087323 | -0.087149 | -0.08721 | -0.087407 | -0.087445 | -0.087371 | -0.087287 | -0.087356 | -0.087435 | -0.08743 | -0.087407 | 1.1153 | 1.3586 | 0.95133 | 1.7877 | 1.7826 | 1.7745 | 1.8736 | 1.8327 | 1.798 | 1.7297 | 1.7758 | 1.8303 | 3.2635 | 2.9657 | 2.9667 | 3.4473 | 3.4487 | 3.4911 | 3.1709 | 3.5254 | 3.4988 | 3.4647 | 3.4244 | 3.5817 | 3.4874 | 3.396 | 3.5166 | 3.3631 | 3.4401 | 3.409 | 3.3709 | 3.4555 | 3.4289 | 3.3061 | 3.3695 | 3.2814 | 3.1415 | 3.227 | 3.4368 | 2.4513 | 2.8303 | 2.3925 | 2.7399 | 2.8007 | 2.6863 | 1.7121 | 1.6289 | 1.7105 | 0.95405 | 0.96186 | 0.9611 | 0.95635 | 0.94654 | 3.3347 | 3.225 | 2.9106 | 1.7246 | 1.6962 | 1.815 | 1.7036 | 1.7167 | 1.6121 | 1.6906 | 1.0886 | 0.97593 | 0.76148 | -0.087224 | 1.2108 | 1.632 | 1.2297 | 3.438 | 3.3868 | 3.4775 | 3.4096 | 3.4376 | 3.3661 | 3.1758 | 3.3718 | 3.434 | 3.3974 | 3.0165 | 3.2518 | 3.4668 | 3.1946 | 3.0268 | 3.0704 | 3.4377 | 2.8544 | 2.4486 | 2.4486 | 2.4395 | 2.2385 | 2.3954 | 2.4339 | 2.3551 | 2.33 | 2.3509 | 2.3829 | 2.6506 | 2.1368 | 1.0563 | 1.0465 | 1.0489 | 2.4192 | 2.4118 | 2.4414 | 2.8753 | 3.1463 | 2.9777 | 2.8234 | 2.9772 | 2.7899 | 2.4674 | 2.4217 | 2.4947 | 1.6339 | 1.7331 | 1.6461 | 1.087 | 1.0489 | 1.0594 | 1.0384 | 1.1851 | 0.99594 | -0.087317 | 0.63614 | -0.087444 | 0.64103 | -0.087417 | 1.1103 | 2.1786 | 2.1492 | 1.986 | 2.4165 | 2.3444 | 2.5862 | 2.5215 | 2.5056 | 2.6371 | 2.8738 | 3.0474 | 3.0115 | 2.8429 | 3.0321 | 3.1359 | 2.8283 | 3.2098 | 2.9735 | 1.668 | 1.7092 | 1.7219 | 3.1612 | 3.2919 | 3.3233 | 3.0149 | 3.2999 | 3.008
340 | m_Oil sep diff (Bar) (AI12) |  | 0.79045 | 0.72005 | 0.76726 | 0.51775 | 0.48466 | 0.46444 | 0.40864 | 0.4263 | 0.40514 | 0.37019 | 0.31952 | 0.32864 | 0.29945 | 0.29833 | 0.29661 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001155 | 0 | 0 | 0.001052 | 9.7e-05 | 0.001678 | 0.003164 | 0.001496 | 0.005355 | 0.006535 | 0.006495 | 0.01051 | 0.044663 | 0 | 0 | 0.016812 | 0.027744 | 0.028507 | 0.034682 | 0.03168 | 0.028812 | 0.10681 | 0.11532 | 0.10195 | 0.11842 | 0.10565 | 0.1139 | 0.078594 | 0.3052 | 0.29235 | 0.27241 | 0.43125 | 0.4614 | 0.41937 | 0.50425 | 0.49865 | 0.51214 | 0.50101 | 0.51848 | 0.47435 | 0.093556 | 0.09867 | 0.10041 | 0.10093 | 0.11432 | 0.11209 | 0.077079 | 0.071561 | 0.077607 | 0.062366 | 0.069865 | 0.056254 | 0.063103 | 0.078986 | 0.055828 | 0 | 0.00082 | 0 | 0 | 0 | 0 | 0.031969 | 0.036495 | 0.034924 | 0.060112 | 0.053141 | 0.047325 | 0.004242 | 0.009007 | 0.013462 | 0.13457 | 0.12815 | 0.14034 | 0.090137 | 0.13733 | 0.095501 | 0.1668 | 0.24342 | 0.23679 | 0.24947 | 0.25905 | 0.24585 | 0.25553 | 0.24384 | 0.25338 | 0.3772 | 0.3513 | 0.38186 | 0.42546 | 0.40708 | 0.4139 | 0.3909 | 0.38811 | 0.42512 | 0.49313 | 0.47948 | 0.46151 | 0.15795 | 0.14892 | 0.15673 | 0.12326 | 0.11522 | 0.12281 | 0.01977 | 0.027919 | 0.029386 | 0.007061 | 0.004924 | 0.004827 | 0.001013 | 0.005646 | 0.12563 | 0.13162 | 0.1274 | 0.054923 | 0.059711 | 0.057888 | 0.065692 | 0.066983 | 0.063541 | 0.066146 | 0.07618 | 0.074618 | 0.074094 | 0.018845 | 0.022384 | 0.021011 | 0.024074 | 0.23628 | 0.22893 | 0.2197 | 0.24641 | 0.45046 | 0.47701 | 0.47091 | 0.41928 | 0.41317 | 0.41487 | 0.30525 | 0.28362 | 0.28713 | 0.27381 | 0.27193 | 0.26487 | 0.27756 | 0.26839 | 0.38786 | 0.40328 | 0.38196 | 0.30537 | 0.28102 | 0.39082 | 0.42993 | 0.29048 | 0.31738 | 0.25459 | 0.24752 | 0.24943 | 0.10797 | 0.10809 | 0.10722 | 0.25992 | 0.35287 | 0.32717 | 0.37635 | 0.39385 | 0.39311 | 0.35351 | 0.28452 | 0.29439 | 0.40427 | 0.59507 | 0.36614 | 0.074257 | 0.07803 | 0.081209 | 0.051692 | 0.052651 | 0.043763 | 0.074811 | 0.074955 | 0.071221 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11782 | 0.12484 | 0.13066 | 0.057835 | 0.068343 | 0.088266 | 0.27622 | 0.33109 | 0.30478 | 0.48619 | 0.46368 | 0.47874 | 0.39781 | 0.36079 | 0.39341 | 0.26533 | 0.29668 | 0.26645 | 0.11069 | 0.10669 | 0.11003 | 0.43112 | 0.41194 | 0.41125 | 0.41837 | 0.41438 | 0.39435
341 | n_spare13 (AI13) |  | -9.8999 | -9.8999 | -9.9 | -9.8997 | -9.8999 | -9.9 | -9.9 | -9.8999 | -9.8997 | -9.8999 | -9.8999 | -9.8997 | -9.9 | -9.8998 | -9.8998 | -9.8999 | -9.8999 | -9.9 | -9.8999 | -9.9001 | -9.8999 | -9.8998 | -9.9 | -9.8999 | -9.8999 | -9.8998 | -9.9 | -9.8998 | -9.8999 | -9.9 | -9.8998 | -9.8999 | -9.8999 | -9.8998 | -9.8998 | -9.9 | -9.8997 | -9.9001 | -9.9 | -9.8998 | -9.9 | -9.8996 | -9.8999 | -9.9 | -9.9 | -9.8999 | -9.8999 | -9.9 | -9.8998 | -9.8999 | -9.9 | -9.8998 | -9.8999 | -9.9 | -9.8998 | -9.9 | -9.8998 | -9.8999 | -9.8998 | -9.8998 | -9.9 | -9.8997 | -9.9002 | -9.9 | -9.9 | -9.8998 | -9.9 | -9.8999 | -9.8999 | -9.9 | -9.9002 | -9.9 | -9.9002 | -9.9001 | -9.9 | -9.8999 | -9.9001 | -9.9002 | -9.9 | -9.9 | -9.9 | -9.9001 | -9.9 | -9.8999 | -9.8999 | -9.8998 | -9.8998 | -9.8999 | -9.9 | -9.8999 | -9.8998 | -9.9002 | -9.9002 | -9.8999 | -9.9 | -9.9 | -9.9 | -9.8999 | -9.8998 | -9.8998 | -9.8998 | -9.8998 | -9.8997 | -9.8999 | -9.8998 | -9.8998 | -9.9 | -9.8998 | -9.8999 | -9.8999 | -9.8998 | -9.8998 | -9.8999 | -9.8999 | -9.9 | -9.8999 | -9.8998 | -9.8997 | -9.9 | -9.8999 | -9.8998 | -9.9002 | -9.8999 | -9.8999 | -9.8999 | -9.9002 | -9.9001 | -9.8999 | -9.8999 | -9.9 | -9.8999 | -9.9001 | -9.8998 | -9.9 | -9.8999 | -9.8999 | -9.9 | -9.8999 | -9.8999 | -9.8999 | -9.9 | -9.9 | -9.8999 | -9.9 | -9.9001 | -9.8999 | -9.9001 | -9.8998 | -9.8998 | -9.9001 | -9.9 | -9.8999 | -9.8999 | -9.9 | -9.9001 | -9.8996 | -9.8997 | -9.8999 | -9.8998 | -9.9 | -9.9 | -9.8998 | -9.9 | -9.8999 | -9.8999 | -9.8999 | -9.8999 | -9.8998 | -9.8997 | -9.9 | -9.8998 | -9.8998 | -9.8998 | -9.9 | -9.8998 | -9.8999 | -9.8999 | -9.9 | -9.8999 | -9.9 | -9.9001 | -9.9001 | -9.8999 | -9.9 | -9.8999 | -9.9 | -9.8999 | -9.8999 | -9.9 | -9.8999 | -9.9 | -9.9 | -9.8999 | -9.9 | -9.9 | -9.8999 | -9.9001 | -9.8998 | -9.9 | -9.9 | -9.9 | -9.9 | -9.8999 | -9.8997 | -9.9001 | -9.8998 | -9.9001 | -9.9002 | -9.9 | -9.8998 | -9.9 | -9.9 | -9.8998 | -9.9 | -9.8999 | -9.8998 | -9.9 | -9.8999 | -9.8999 | -9.8999 | -9.8998 | -9.8999 | -9.8999 | -9.8999 | -9.8999 | -9.8999 | -9.8998 | -9.9001 | -9.8999 | -9.8999 | -9.8998 | -9.9001 | -9.9 | -9.8997 | -9.9 | -9.8999
342 | o_Oil sump pressure (AI14) |  | 14.3429 | 14.407 | 14.3632 | 14.2377 | 14.2554 | 14.2356 | 14.1253 | 14.0973 | 14.0754 | 14.0159 | 14.0146 | 14.0282 | 13.9525 | 13.9328 | 13.9229 | 7.3034 | 7.3127 | 7.3078 | 7.3291 | 7.3189 | 7.2838 | 7.3068 | 7.3087 | 7.3074 | 7.3223 | 7.3021 | 7.2899 | 8.5209 | 8.5256 | 8.5261 | 8.5339 | 8.5423 | 8.5531 | 8.5377 | 8.5769 | 8.5494 | 8.5225 | 8.5562 | 8.5474 | 8.5566 | 8.5953 | 8.5826 | 10.8948 | 10.8639 | 10.8874 | 10.8532 | 10.933 | 10.9281 | 10.8722 | 13.6738 | 13.6781 | 13.6875 | 14.0946 | 14.0536 | 14.0424 | 13.6929 | 13.7146 | 13.6904 | 13.4954 | 13.4744 | 13.5202 | 10.8801 | 10.8738 | 10.8964 | 10.8731 | 10.8853 | 10.8626 | 8.5692 | 8.5965 | 8.5772 | 8.5126 | 8.5586 | 8.5617 | 8.5665 | 8.5467 | 8.5287 | 7.3289 | 7.3305 | 7.287 | 7.2915 | 7.3183 | 7.2947 | 8.5406 | 8.5672 | 8.5365 | 8.5182 | 8.5203 | 8.5334 | 8.5412 | 8.542 | 8.5545 | 10.9645 | 10.9414 | 10.9327 | 10.9217 | 10.9291 | 10.9154 | 10.8961 | 13.7476 | 13.7561 | 13.7515 | 13.7525 | 13.7483 | 13.7416 | 13.7401 | 13.7381 | 14.1037 | 14.0787 | 14.0572 | 13.7728 | 13.7389 | 13.7222 | 13.5669 | 13.495 | 13.4872 | 13.9727 | 14.0051 | 14.0048 | 10.8588 | 10.8619 | 10.8836 | 10.8684 | 10.8587 | 10.8422 | 8.5148 | 8.5378 | 8.5269 | 7.2868 | 7.296 | 7.3226 | 7.3509 | 7.2995 | 10.8503 | 10.8239 | 10.8426 | 8.5272 | 8.5365 | 8.5307 | 8.5663 | 8.5572 | 8.5504 | 8.5481 | 8.5207 | 8.5199 | 8.525 | 7.3547 | 7.3694 | 7.3389 | 7.3258 | 13.5813 | 13.6297 | 13.651 | 13.638 | 13.6866 | 13.6796 | 13.6613 | 13.4842 | 13.4951 | 13.4864 | 13.6402 | 13.6635 | 13.6254 | 13.6329 | 13.5068 | 13.5369 | 13.4986 | 13.44 | 13.9733 | 14.0262 | 13.997 | 13.7762 | 13.7379 | 13.7303 | 13.513 | 13.5169 | 13.5334 | 13.7843 | 13.674 | 13.7188 | 8.5555 | 8.5596 | 8.4999 | 14.0165 | 14.0118 | 13.9882 | 13.512 | 13.4938 | 13.4706 | 13.6528 | 13.68 | 13.6575 | 13.6103 | 13.5785 | 13.5891 | 8.5403 | 8.5559 | 8.5039 | 8.5765 | 8.5417 | 8.5639 | 8.5333 | 8.5087 | 8.5188 | 7.2956 | 7.3009 | 7.2995 | 7.3229 | 7.3083 | 7.2952 | 10.8717 | 10.8204 | 10.8167 | 10.8627 | 10.8632 | 10.8306 | 14.0394 | 14.0159 | 14.0205 | 13.7144 | 13.6976 | 13.6893 | 13.5377 | 13.4648 | 13.4849 | 13.7127 | 13.6306 | 13.5994 | 8.5236 | 8.5925 | 8.5296 | 13.4781 | 13.5 | 13.4991 | 13.6896 | 13.7229 | 13.7414
343 | p_oil pump flow (AI15) |  | -4.4946 | -4.4946 | -4.4945 | -4.4941 | -4.4941 | -4.494 | -4.4937 | -4.4936 | -4.4936 | -4.4931 | -4.493 | -4.4929 | -4.4923 | -4.4923 | -4.4923 | -4.4883 | -4.4883 | -4.4882 | -4.4879 | -4.488 | -4.4879 | -4.4889 | -4.4888 | -4.4887 | -4.4887 | -4.4886 | -4.4885 | -4.4922 | -4.4922 | -4.4923 | -4.4922 | -4.4922 | -4.4922 | -4.4922 | -4.4922 | -4.4922 | -4.4923 | -4.4923 | -4.4924 | -4.4926 | -4.4926 | -4.4926 | -4.4934 | -4.4935 | -4.4934 | -4.4934 | -4.4933 | -4.4933 | -4.4932 | -4.494 | -4.494 | -4.4938 | -4.4928 | -4.4929 | -4.4926 | -4.4918 | -4.4917 | -4.4915 | -4.4909 | -4.4906 | -4.4904 | -4.4932 | -4.4931 | -4.493 | -4.4925 | -4.4925 | -4.4924 | -4.4909 | -4.4908 | -4.4907 | -4.4906 | -4.4906 | -4.4904 | -4.4903 | -4.4903 | -4.4902 | -4.4892 | -4.4892 | -4.4891 | -4.4887 | -4.4885 | -4.4882 | -4.4918 | -4.4919 | -4.4918 | -4.4919 | -4.492 | -4.4919 | -4.4921 | -4.4921 | -4.4923 | -4.4932 | -4.4932 | -4.4932 | -4.493 | -4.493 | -4.4931 | -4.4937 | -4.494 | -4.494 | -4.494 | -4.4939 | -4.4938 | -4.4938 | -4.4938 | -4.4936 | -4.4925 | -4.4925 | -4.4923 | -4.4914 | -4.4914 | -4.4912 | -4.4909 | -4.4906 | -4.4904 | -4.494 | -4.494 | -4.4939 | -4.492 | -4.492 | -4.492 | -4.4918 | -4.4917 | -4.4917 | -4.49 | -4.49 | -4.4899 | -4.4882 | -4.4882 | -4.4881 | -4.4879 | -4.4879 | -4.4922 | -4.4921 | -4.4921 | -4.4903 | -4.4902 | -4.4902 | -4.4899 | -4.4898 | -4.4898 | -4.4898 | -4.4893 | -4.4892 | -4.4893 | -4.4879 | -4.4879 | -4.4879 | -4.4879 | -4.4959 | -4.4959 | -4.4959 | -4.4958 | -4.4954 | -4.4954 | -4.4953 | -4.4948 | -4.4946 | -4.4942 | -4.4957 | -4.4957 | -4.4955 | -4.4955 | -4.4954 | -4.4952 | -4.4952 | -4.4951 | -4.4941 | -4.494 | -4.494 | -4.4934 | -4.4934 | -4.4933 | -4.4932 | -4.4931 | -4.493 | -4.4925 | -4.4923 | -4.4921 | -4.4888 | -4.4888 | -4.4887 | -4.4938 | -4.4937 | -4.4936 | -4.493 | -4.493 | -4.4929 | -4.4925 | -4.4924 | -4.4924 | -4.4922 | -4.4921 | -4.492 | -4.4877 | -4.4876 | -4.4876 | -4.4894 | -4.4891 | -4.4893 | -4.4886 | -4.4885 | -4.4884 | -4.4898 | -4.4898 | -4.4898 | -4.4897 | -4.4899 | -4.4896 | -4.4919 | -4.4918 | -4.4918 | -4.4915 | -4.4914 | -4.4913 | -4.494 | -4.4937 | -4.4936 | -4.4931 | -4.493 | -4.4929 | -4.4925 | -4.4924 | -4.4922 | -4.4929 | -4.4929 | -4.4927 | -4.4893 | -4.4892 | -4.4891 | -4.4938 | -4.4937 | -4.4936 | -4.4932 | -4.4931 | -4.4929
344 | a_Compressor Discharge Valve FCV-01 (AO0) |  | 36.9987 | 36.9987 | 36.9987 | 29.9996 | 29.9996 | 29.9996 | 15.9993 | 16.9997 | 16.9997 | 14.9989 | 14.9989 | 14.9989 | 14.9989 | 14.9989 | 14.9989 | 0.99861 | 0.99861 | 0.99861 | 0.99861 | 0.99861 | 0.99861 | 0.99861 | 0.99861 | 0.99861 | 0.99861 | 0.99861 | 0.99861 | 13 | 13 | 13 | 13 | 13 | 13 | 17.9982 | 17.9982 | 17.9982 | 17.9982 | 17.9982 | 17.9982 | 18.9986 | 17.9982 | 17.9982 | 4.9984 | 4.9984 | 4.9984 | 4.9984 | 7.9997 | 7.9997 | 7.9997 | 16.9997 | 16.9997 | 16.9997 | 7.9997 | 7.9997 | 7.9997 | 13.9984 | 13.9984 | 13.9984 | 13.9984 | 13 | 13 | 19.9991 | 19.9991 | 19.9991 | 19.9991 | 19.9991 | 19.9991 | 19.9991 | 19.9991 | 19.9991 | 10.9991 | 10.9991 | 10.9991 | 10.9991 | 10.9991 | 10.9991 | 7.9997 | 7.9997 | 7.9997 | 11.9995 | 11.9995 | 11.9995 | 3.9999 | 3.9999 | 3.9999 | 4.9984 | 4.9984 | 4.9984 | 4.9984 | 4.9984 | 4.9984 | 20.9995 | 20.9995 | 20.9995 | 24.9993 | 24.9993 | 24.9993 | 23.9989 | 19.9991 | 19.9991 | 19.9991 | 19.9991 | 19.9991 | 19.9991 | 19.9991 | 19.9991 | 10.9991 | 10.9991 | 10.9991 | 14.9989 | 14.9989 | 14.9989 | 14.9989 | 14.9989 | 14.9989 | 20.9995 | 20.9995 | 20.9995 | 2.9995 | 2.9995 | 2.9995 | 2.9995 | 2.9995 | 2.9995 | 2.9995 | 2.9995 | 2.9995 | 0.99861 | 0.99861 | 0.99861 | 0.99861 | 0.99861 | 16.9997 | 16.9997 | 16.9997 | 14.9989 | 14.9989 | 14.9989 | 14.9989 | 17.9982 | 17.9982 | 17.9982 | 17.9982 | 17.9982 | 17.9982 | 2.9995 | 2.9995 | 2.9995 | 2.9995 | 25.9998 | 25.9998 | 25.9998 | 25.9998 | 25.9998 | 23.9989 | 23.9989 | 26.9982 | 26.9982 | 27.9987 | 11.9995 | 11.9995 | 11.9995 | 11.9995 | 11.9995 | 11.9995 | 11.9995 | 11.9995 | 2.9995 | 2.9995 | 2.9995 | 14.9989 | 14.9989 | 14.9989 | 14.9989 | 14.9989 | 14.9989 | 11.9995 | 13 | 13 | 15.9993 | 15.9993 | 15.9993 | 11.9995 | 11.9995 | 11.9995 | 13.9984 | 13.9984 | 13.9984 | 17.9982 | 17.9982 | 17.9982 | 16.9997 | 16.9997 | 16.9997 | 16.9997 | 16.9997 | 16.9997 | 10.9991 | 10.9991 | 4.9984 | 9.9986 | 9.9986 | 9.9986 | 0.99861 | 0.99861 | 0.99861 | 0.99861 | 0.99861 | 0.99861 | 5.9988 | 5.9988 | 5.9988 | 8.9982 | 8.9982 | 8.9982 | 13 | 13 | 13 | 13.9984 | 13.9984 | 13.9984 | 13.9984 | 13.9984 | 13.9984 | 14.9989 | 14.9989 | 14.9989 | 19.9991 | 19.9991 | 19.9991 | 10.9991 | 10.9991 | 10.9991 | 11.9995 | 11.9995 | 11.9995
345 | b_Pneumatic Suction Valve FCV-02 (AO1) |  | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998 | 49.9998
346 | c_Condenser Water Outlet Valve TCV-31 (AO2) |  | 0.99835 | 0.99835 | 0.99835 | 3.9995 | 4.9999 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 2.9991 | 1.9987 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 4.9999 | 4.9999 | 4.9999 | 4.9999 | 4.9999 | 4.9999 | 6.9987 | 6.9987 | 5.9983 | 5.9983 | 5.9983 | 5.9983 | 6.9987 | 6.9987 | 6.9987 | 2.9991 | 1.9987 | 2.9991 | 1.9987 | 1.9987 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 2.9991 | 3.9995 | 0.99835 | 0.99835 | 1.9987 | 1.9987 | 1.9987 | 3.9995 | 0.99835 | 2.9991 | 10.9983 | 10.9983 | 9.9999 | 13.9995 | 11.9987 | 11.9987 | 12.9991 | 13.9995 | 12.9991 | 11.9987 | 11.9987 | 10.9983 | 10.9983 | 10.9983 | 10.9983 | 2.9991 | 1.9987 | 0.99835 | 0.99835 | 2.9991 | 0.99835 | 1.9987 | 1.9987 | 1.9987 | 3.9995 | 4.9999 | 4.9999 | 5.9983 | 5.9983 | 5.9983 | 2.9991 | 2.9991 | 2.9991 | 2.9991 | 2.9991 | 2.9991 | 3.9995 | 2.9991 | 2.9991 | 2.9991 | 2.9991 | 2.9991 | 2.9991 | 2.9991 | 2.9991 | 5.9983 | 5.9983 | 5.9983 | 5.9983 | 5.9983 | 5.9983 | 6.9987 | 6.9987 | 6.9987 | 7.9991 | 7.9991 | 7.9991 | 4.9999 | 5.9983 | 5.9983 | 5.9983 | 5.9983 | 5.9983 | 7.9991 | 7.9991 | 7.9991 | 2.9991 | 2.9991 | 2.9991 | 0.99835 | 0.99835 | 12.9991 | 12.9991 | 12.9991 | 8.9995 | 8.9995 | 8.9995 | 8.9995 | 8.9995 | 8.9995 | 8.9995 | 8.9995 | 8.9995 | 8.9995 | 11.9987 | 9.9999 | 4.9999 | 2.9991 | 4.9999 | 4.9999 | 2.9991 | 5.9983 | 6.9987 | 6.9987 | 8.9995 | 7.9991 | 6.9987 | 6.9987 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 1.9987 | 1.9987 | 1.9987 | 1.9987 | 2.9991 | 2.9991 | 1.9987 | 2.9991 | 0.99835 | 2.9991 | 2.9991 | 1.9987 | 2.9991 | 0.99835 | 0.99835 | 1.9987 | 0.99835 | 0.99835 | 0.99835 | 2.9991 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 1.9987 | 1.9987 | 1.9987 | 11.9987 | 11.9987 | 11.9987 | 10.9983 | 10.9983 | 10.9983 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 1.9987 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 0.99835 | 1.9987 | 1.9987 | 0.99835 | 1.9987 | 1.9987 | 1.9987 | 0.99835 | 0.99835 | 0.99835
347 | d_Spare1 (AO3) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
348 | a_Spare1 (AO0) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
349 | b_Spare2 (AO2) |  | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006 | -25.0006
350 | c_Spare3 (AO1) |  | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004 | -25.0004
351 | d_Spare4 (AO3) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
352 | a_Run Signal (DIO0) |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
353 | b_DIO1 (DIO1) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
354 | c_DIO2 (DIO2) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
355 | d_DIO3 (DIO3) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
356 | e_DIO4 (DIO4) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
357 | f_DIO5 (DIO5) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
358 | g_DIO6 (DIO6) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
359 | h_DIO7 (DIO7) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
360 | a_Suction Temperature (TE-60) (RTD0) |  | 25.0492 | 24.9605 | 24.7684 | 21.3108 | 20.8375 | 19.4422 | 16.3206 | 15.6208 | 15.0402 | 10.098 | 10.5134 | 9.7332 | 7.3524 | 7.2084 | 7.0618 | 18.4808 | 18.5859 | 18.8415 | 18.684 | 18.6889 | 18.6476 | 18.323 | 18.6046 | 18.8127 | 18.7143 | 18.7131 | 18.7292 | 16.6336 | 16.8627 | 16.9105 | 16.7911 | 16.6719 | 16.4341 | 17.5757 | 17.3977 | 17.2151 | 15.7404 | 15.4801 | 15.5112 | 15.6782 | 15.91 | 16.4212 | 15.0114 | 15.0351 | 14.7431 | 14.5322 | 14.934 | 14.876 | 14.748 | 13.313 | 13.2327 | 12.9854 | 11.7386 | 10.9293 | 12.2237 | 13.463 | 13.4539 | 13.5436 | 13.5748 | 14.9419 | 15.7748 | 15.2453 | 15.4783 | 15.4345 | 17.5607 | 17.521 | 17.4276 | 20.2842 | 20.2017 | 20.063 | 19.0741 | 18.9792 | 18.8013 | 18.5706 | 18.4883 | 18.493 | 17.1189 | 17.0125 | 16.7228 | 18.9759 | 18.5056 | 18.4042 | 17.3922 | 16.9391 | 16.7895 | 16.1943 | 16.1802 | 16.1937 | 16.3087 | 16.2008 | 16.1704 | 17.1666 | 17.0217 | 16.8172 | 16.5701 | 16.3831 | 16.1233 | 16.9093 | 14.3163 | 14.3056 | 14.2855 | 14.3732 | 14.3977 | 14.4554 | 14.6297 | 14.9905 | 12.1148 | 12.491 | 11.6225 | 14.4707 | 14.4767 | 14.447 | 15.2061 | 14.9845 | 14.7759 | 11.0711 | 11.1825 | 11.2949 | 16.9689 | 16.7949 | 16.82 | 17.2337 | 17.2418 | 17.2429 | 18.3113 | 18.719 | 19.14 | 18.3754 | 18.4238 | 18.4575 | 17.928 | 17.8053 | 15.2657 | 15.1213 | 14.6392 | 16.9474 | 16.8708 | 16.7454 | 16.3672 | 16.8494 | 16.8831 | 16.9756 | 16.818 | 16.8359 | 16.894 | 17.6224 | 18.5485 | 18.5994 | 18.336 | 13.6671 | 14.0142 | 14.3711 | 14.4289 | 13.5508 | 14.6941 | 15.0175 | 18.91 | 19.3815 | 18.9184 | 21.6936 | 21.6804 | 21.6293 | 21.5924 | 21.5042 | 21.445 | 21.4117 | 21.3538 | 12.1552 | 12.4514 | 12.4251 | 13.616 | 13.7924 | 14.5835 | 15.4833 | 15.6995 | 15.957 | 13.1966 | 13.8774 | 13.2902 | 17.6319 | 17.477 | 17.6169 | 11.4366 | 11.2606 | 11.0319 | 13.6057 | 13.3032 | 12.8859 | 14.7596 | 14.4407 | 14.5919 | 13.3308 | 13.5145 | 13.5078 | 16.7238 | 16.7508 | 16.4436 | 18.3129 | 18.5421 | 19.3375 | 19.1512 | 18.6899 | 18.3133 | 17.8738 | 18.0498 | 18.1805 | 18.1335 | 17.8199 | 17.7217 | 15.4962 | 15.4738 | 15.4137 | 16.3355 | 16.1358 | 15.6846 | 12.61 | 11.434 | 10.0759 | 13.2532 | 13.0466 | 13.0493 | 13.1758 | 12.8939 | 12.9535 | 14.8885 | 16.1038 | 15.307 | 18.7739 | 18.5876 | 18.4132 | 15.277 | 15.2205 | 15.4129 | 15.5764 | 15.5655 | 14.7076
361 | b_Discharge Temperature (TE-54) (RTD1) |  | 76.6687 | 76.5849 | 76.4228 | 78.8962 | 78.4349 | 77.2688 | 80.8742 | 80.232 | 79.7171 | 83.792 | 83.7771 | 83.3901 | 90.8678 | 90.7344 | 90.6054 | 47.9543 | 47.9974 | 48.0748 | 47.4335 | 47.1388 | 47.0256 | 47.2552 | 47.3039 | 46.71 | 47.0215 | 46.9679 | 46.7681 | 52.8733 | 53.0544 | 53.2342 | 53.9749 | 53.9215 | 53.8645 | 54.6573 | 54.2959 | 54.3258 | 51.741 | 51.8007 | 51.8306 | 52.1554 | 52.5743 | 52.653 | 63.6603 | 63.581 | 63.4182 | 63.2056 | 64.0455 | 63.8848 | 63.6064 | 77.5141 | 77.4408 | 77.2263 | 82.4291 | 81.9144 | 82.8346 | 78.711 | 78.7044 | 78.7812 | 78.5828 | 79.6879 | 79.9545 | 64.9206 | 65.4558 | 65.7251 | 67.6261 | 67.6046 | 67.6164 | 56.3924 | 56.3225 | 56.2193 | 56.017 | 55.9235 | 55.7537 | 55.4961 | 55.3446 | 55.1113 | 45.7004 | 45.4766 | 45.3926 | 46.4671 | 46.0189 | 45.609 | 53.5322 | 53.2481 | 53.3954 | 52.6919 | 52.6848 | 52.5961 | 53.6881 | 53.541 | 53.3669 | 66.9299 | 66.7963 | 66.7029 | 66.5891 | 66.413 | 66.1839 | 67.2566 | 79.4 | 79.3899 | 79.3811 | 79.4592 | 79.4766 | 79.5019 | 79.6386 | 79.8189 | 83.6596 | 83.69 | 83.1033 | 80.6129 | 80.5601 | 80.7132 | 80.4026 | 80.0417 | 79.8318 | 82.6253 | 82.7389 | 82.8015 | 66.8161 | 66.7456 | 66.7452 | 67.1784 | 67.198 | 67.1985 | 55.9889 | 56.3751 | 56.574 | 46.7646 | 46.6674 | 46.5323 | 45.7305 | 45.2656 | 65.4899 | 65.4777 | 65.9108 | 53.5212 | 53.4746 | 53.3858 | 53.0156 | 53.6689 | 53.7036 | 53.7298 | 56.208 | 56.2506 | 56.3103 | 47.6678 | 48.0269 | 47.9808 | 47.9414 | 79.0585 | 79.3621 | 79.6115 | 79.6811 | 80.2055 | 80.973 | 81.2442 | 84.6134 | 84.8795 | 84.1783 | 81.3351 | 81.2728 | 80.9674 | 80.7776 | 80.4931 | 80.4914 | 80.2766 | 79.5949 | 81.6492 | 81.8133 | 81.7659 | 78.36 | 78.5664 | 79.1082 | 79.3911 | 79.5723 | 79.7772 | 77.2175 | 77.1545 | 76.8154 | 54.0542 | 53.963 | 53.9896 | 81.1123 | 80.8792 | 80.8373 | 77.4235 | 77.1664 | 76.8264 | 79.0837 | 78.7779 | 79.2053 | 76.5866 | 76.7418 | 76.5902 | 52.7574 | 52.5277 | 52.4436 | 54.6356 | 55.0605 | 55.1597 | 54.7452 | 54.0465 | 53.7595 | 46.5342 | 46.5135 | 46.384 | 46.505 | 45.5963 | 45.1859 | 64.4279 | 64.2532 | 64.3681 | 65.2223 | 64.9016 | 64.4856 | 82.3417 | 81.291 | 80.4547 | 78.0616 | 77.9128 | 77.841 | 77.0956 | 77.092 | 77.3296 | 78.4717 | 79.1191 | 78.5143 | 54.4239 | 54.1733 | 53.8665 | 79.6024 | 79.6789 | 79.8482 | 80.4132 | 80.318 | 79.6525
362 | c_Suction Flowmeter Temperature Low Duty (RTD2) |  | 25.0695 | 25.0279 | 24.9531 | 24.3264 | 24.2797 | 24.1316 | 23.5377 | 23.4213 | 23.34 | 22.6807 | 22.5876 | 22.4853 | 21.5998 | 21.5538 | 21.5159 | 18.1515 | 18.121 | 18.0538 | 17.8513 | 17.8207 | 17.7615 | 18.7782 | 18.7339 | 18.6613 | 18.6012 | 18.5539 | 18.513 | 22.4896 | 22.5012 | 22.508 | 22.519 | 22.5241 | 22.5216 | 22.4928 | 22.4989 | 22.4822 | 22.556 | 22.5896 | 22.6653 | 22.7679 | 22.7808 | 22.8072 | 22.9038 | 22.8948 | 22.8896 | 22.9012 | 22.933 | 22.9577 | 22.9945 | 23.3475 | 23.2942 | 23.148 | 22.3854 | 22.2278 | 21.8496 | 21 | 20.8452 | 20.6619 | 20.0258 | 19.6257 | 19.3737 | 23.5147 | 23.4328 | 23.3883 | 22.9184 | 22.8296 | 22.7641 | 21.2502 | 21.2102 | 21.1259 | 20.913 | 20.8716 | 20.7969 | 20.6793 | 20.5983 | 20.5379 | 19.7559 | 19.7553 | 19.741 | 18.9023 | 18.6581 | 18.3921 | 22.3693 | 22.388 | 22.3845 | 22.4817 | 22.5132 | 22.542 | 22.6549 | 22.6767 | 22.7055 | 23.3211 | 23.3074 | 23.2991 | 23.2309 | 23.2364 | 23.2459 | 23.7533 | 23.7272 | 23.714 | 23.6977 | 23.5702 | 23.5569 | 23.5119 | 23.4423 | 23.2982 | 22.3945 | 22.3239 | 22.2083 | 21.0039 | 20.8648 | 20.7187 | 20.3358 | 20.0463 | 19.8197 | 23.4144 | 23.3217 | 23.2528 | 21.6434 | 21.6334 | 21.607 | 21.4336 | 21.4112 | 21.3888 | 20.0598 | 20.0167 | 19.9864 | 17.9231 | 17.8527 | 17.7983 | 17.5471 | 17.4421 | 22.4259 | 22.3736 | 22.3127 | 20.8064 | 20.7962 | 20.7794 | 20.5932 | 20.5328 | 20.5193 | 20.5045 | 19.9872 | 19.9415 | 19.9055 | 18.7521 | 18.6795 | 18.665 | 18.6497 | 26.1837 | 26.1401 | 26.1129 | 26.0928 | 25.9967 | 25.9339 | 25.9055 | 25.1433 | 24.9805 | 24.3988 | 25.1837 | 25.1726 | 25.0833 | 25.0247 | 24.8882 | 24.7915 | 24.7017 | 24.6017 | 23.3242 | 23.2553 | 23.1951 | 22.7517 | 22.6698 | 22.5846 | 22.4558 | 22.354 | 22.258 | 21.7372 | 21.5049 | 21.3427 | 18.9132 | 18.8514 | 18.7742 | 23.0502 | 22.933 | 22.8201 | 22.2498 | 22.1316 | 22.046 | 21.4822 | 21.3977 | 21.3175 | 21.0842 | 20.9579 | 20.8466 | 17.4399 | 17.384 | 17.2631 | 19.094 | 19.0085 | 18.8638 | 17.8161 | 17.6353 | 17.4635 | 19.5179 | 19.4865 | 19.4576 | 19.451 | 19.392 | 19.3776 | 21.1707 | 21.1609 | 21.1385 | 20.7782 | 20.7431 | 20.7168 | 22.9411 | 22.7288 | 22.594 | 22.2581 | 22.1752 | 22.0486 | 21.7812 | 21.6279 | 21.4427 | 22.0095 | 21.928 | 21.811 | 19.1893 | 19.053 | 18.9404 | 23.1801 | 23.0555 | 22.9106 | 22.49 | 22.3149 | 22.1282
363 | d__Suction Flowmeter Temperature High Duty (RTD3) |  | 25.9109 | 25.8124 | 25.5781 | 22.197 | 21.9077 | 20.0413 | 17.0498 | 16.3563 | 15.7449 | 10.1125 | 10.8025 | 10.6209 | 7.7482 | 7.5782 | 7.4421 | 18.2387 | 18.3291 | 18.7295 | 18.6987 | 18.7376 | 18.7217 | 17.8876 | 18.2877 | 18.8424 | 18.653 | 18.6247 | 18.6285 | 16.3609 | 16.6406 | 16.8161 | 16.7337 | 16.6356 | 16.3679 | 17.5771 | 17.4449 | 17.233 | 15.6855 | 15.3842 | 15.039 | 15.4347 | 15.3707 | 16.0669 | 15.0017 | 15.0318 | 14.6919 | 14.6098 | 15.0736 | 14.9495 | 14.9655 | 13.6921 | 13.5696 | 13.4204 | 12.5787 | 11.3295 | 13.3369 | 14.0076 | 13.8764 | 13.8043 | 14.0072 | 15.156 | 16.3903 | 15.2297 | 15.3698 | 15.5567 | 17.6118 | 17.6091 | 17.5038 | 20.4014 | 20.3128 | 20.1394 | 19.1442 | 19.0634 | 18.8666 | 18.6152 | 18.4872 | 18.5596 | 17.037 | 16.9921 | 16.7394 | 19.1675 | 18.549 | 18.3818 | 17.5931 | 16.9054 | 16.7132 | 16.0549 | 16.0284 | 16.0511 | 16.2887 | 16.1463 | 16.0964 | 17.3012 | 17.1679 | 17.0034 | 16.7474 | 16.5928 | 16.3034 | 16.988 | 14.6452 | 14.6343 | 14.6348 | 14.6544 | 14.7171 | 14.7525 | 14.8143 | 15.3291 | 12.3966 | 12.7973 | 12.2684 | 14.9808 | 14.9493 | 14.7773 | 15.7954 | 15.5731 | 15.2555 | 11.3692 | 11.4864 | 11.5449 | 17.1477 | 16.8812 | 16.8236 | 17.2557 | 17.2695 | 17.263 | 17.9453 | 18.2663 | 18.7981 | 18.3316 | 18.467 | 18.6333 | 18.0898 | 17.93 | 15.3888 | 15.2316 | 14.376 | 16.9786 | 16.8976 | 16.7832 | 16.4797 | 16.7158 | 16.7295 | 16.7941 | 16.6939 | 16.6729 | 16.7389 | 17.1019 | 18.4491 | 18.8525 | 18.7704 | 13.8548 | 14.3446 | 14.6265 | 14.9816 | 13.5804 | 14.8653 | 15.1748 | 19.2237 | 20.0499 | 19.3508 | 15.5393 | 15.5293 | 15.1965 | 14.9407 | 15.1549 | 15.2405 | 15.1364 | 14.6628 | 12.468 | 12.9078 | 13.2549 | 14.0641 | 14.1239 | 14.8673 | 16.0009 | 16.1561 | 16.361 | 13.0496 | 14.5876 | 13.6658 | 17.8229 | 17.3381 | 17.6227 | 12.0038 | 11.7832 | 11.4284 | 14.2679 | 13.9934 | 13.5985 | 15.6402 | 14.9683 | 15.186 | 13.7282 | 13.9645 | 14.0237 | 16.7333 | 16.8359 | 16.6708 | 18.177 | 18.2612 | 19.2329 | 19.4394 | 19.0394 | 18.4852 | 17.5775 | 17.7874 | 18.1119 | 18.222 | 17.8873 | 17.7857 | 15.5527 | 15.514 | 15.4571 | 16.5659 | 16.4167 | 16.2779 | 13.2602 | 12.073 | 10.0483 | 13.7469 | 13.6043 | 13.481 | 13.5088 | 13.6009 | 13.1505 | 14.7542 | 16.5898 | 15.9957 | 18.983 | 18.7162 | 18.4693 | 15.8354 | 15.7533 | 15.8323 | 16.0615 | 16.3192 | 15.4266
364 | AI0 |  | 14/05/2020 | 14/05/2020 | 14/05/2020 | 14/05/2020 | 14/05/2020 | 14/05/2020 | 14/05/2020 | 14/05/2020 | 14/05/2020 | 14/05/2020 | 14/05/2020 | 14/05/2020 | 14/05/2020 | 14/05/2020 | 14/05/2020 | 14/05/2020 | 14/05/2020 | 14/05/2020 | 14/05/2020 | 14/05/2020 | 14/05/2020 | 13/05/2020 | 13/05/2020 | 13/05/2020 | 13/05/2020 | 13/05/2020 | 13/05/2020 | 44170 | 44170 | 44170 | 44170 | 44170 | 44170 | 44170 | 44170 | 44170 | 44170 | 44170 | 44170 | 44170 | 44170 | 44170 | 44170 | 44170 | 44170 | 44170 | 44170 | 44170 | 44170 | 44170 | 44170 | 44170 | 44170 | 44170 | 44170 | 44170 | 44170 | 44170 | 44170 | 44170 | 44170 | 44017 | 44017 | 44017 | 44017 | 44017 | 44017 | 44017 | 44017 | 44017 | 44017 | 44017 | 44017 | 44017 | 44017 | 44017 | 44017 | 44017 | 44017 | 44017 | 44017 | 44017 | 43987 | 43987 | 43987 | 43987 | 43987 | 43987 | 43987 | 43987 | 43987 | 43987 | 43987 | 43987 | 43987 | 43987 | 43987 | 43987 | 43987 | 43987 | 43987 | 43987 | 43987 | 43987 | 43987 | 43987 | 43987 | 43987 | 43987 | 43987 | 43987 | 43987 | 43987 | 43987 | 43987 | 43835 | 43835 | 43835 | 43835 | 43835 | 43835 | 43835 | 43835 | 43835 | 43835 | 43835 | 43835 | 43835 | 43835 | 43835 | 43835 | 43835 | 30/04/2020 | 30/04/2020 | 30/04/2020 | 30/04/2020 | 30/04/2020 | 30/04/2020 | 30/04/2020 | 30/04/2020 | 30/04/2020 | 30/04/2020 | 30/04/2020 | 30/04/2020 | 30/04/2020 | 30/04/2020 | 30/04/2020 | 30/04/2020 | 30/04/2020 | 29/04/2020 | 29/04/2020 | 29/04/2020 | 29/04/2020 | 29/04/2020 | 29/04/2020 | 29/04/2020 | 29/04/2020 | 29/04/2020 | 29/04/2020 | 28/04/2020 | 28/04/2020 | 28/04/2020 | 28/04/2020 | 28/04/2020 | 28/04/2020 | 28/04/2020 | 28/04/2020 | 22/04/2020 | 22/04/2020 | 22/04/2020 | 22/04/2020 | 22/04/2020 | 22/04/2020 | 22/04/2020 | 22/04/2020 | 22/04/2020 | 22/04/2020 | 22/04/2020 | 22/04/2020 | 22/04/2020 | 22/04/2020 | 22/04/2020 | 20/04/2020 | 20/04/2020 | 20/04/2020 | 20/04/2020 | 20/04/2020 | 20/04/2020 | 20/04/2020 | 20/04/2020 | 20/04/2020 | 20/04/2020 | 20/04/2020 | 20/04/2020 | 20/04/2020 | 20/04/2020 | 20/04/2020 | 17/04/2020 | 17/04/2020 | 17/04/2020 | 17/04/2020 | 17/04/2020 | 17/04/2020 | 16/04/2020 | 16/04/2020 | 16/04/2020 | 16/04/2020 | 16/04/2020 | 16/04/2020 | 16/04/2020 | 16/04/2020 | 16/04/2020 | 16/04/2020 | 16/04/2020 | 16/04/2020 | 15/04/2020 | 15/04/2020 | 15/04/2020 | 15/04/2020 | 15/04/2020 | 15/04/2020 | 15/04/2020 | 15/04/2020 | 15/04/2020 | 14/04/2020 | 14/04/2020 | 14/04/2020 | 14/04/2020 | 14/04/2020 | 14/04/2020 | 44078 | 44078 | 44078 | 44078 | 44078 | 44078
365 | AI1 |  | 0.66875 | 0.66667 | 0.66458 | 0.64375 | 0.64167 | 0.63681 | 0.62361 | 0.62083 | 0.61806 | 0.60069 | 0.59861 | 0.59653 | 0.57986 | 0.57917 | 0.57847 | 0.50347 | 0.50208 | 0.49861 | 0.48819 | 0.48611 | 0.48333 | 0.48611 | 0.48403 | 0.48056 | 0.47569 | 0.47292 | 0.47014 | 0.675 | 0.67153 | 0.66944 | 0.66667 | 0.66458 | 0.66181 | 0.65 | 0.64722 | 0.64514 | 0.63125 | 0.62708 | 0.61875 | 0.60903 | 0.60694 | 0.60486 | 0.57222 | 0.57083 | 0.56806 | 0.5625 | 0.54931 | 0.54722 | 0.54444 | 0.50556 | 0.50278 | 0.49653 | 0.47222 | 0.46875 | 0.4625 | 0.44792 | 0.44583 | 0.44306 | 0.43611 | 0.43264 | 0.43056 | 0.60972 | 0.60486 | 0.60208 | 0.5875 | 0.58542 | 0.58333 | 0.55278 | 0.55139 | 0.54861 | 0.54167 | 0.53958 | 0.5375 | 0.53333 | 0.53125 | 0.52917 | 0.49236 | 0.49028 | 0.4875 | 0.45347 | 0.44653 | 0.43958 | 0.68958 | 0.68681 | 0.68472 | 0.66875 | 0.66458 | 0.6625 | 0.65139 | 0.64931 | 0.64722 | 0.60556 | 0.60347 | 0.60139 | 0.57639 | 0.57361 | 0.57153 | 0.53542 | 0.52083 | 0.52014 | 0.51944 | 0.5125 | 0.51181 | 0.50972 | 0.50694 | 0.50139 | 0.45625 | 0.45347 | 0.45139 | 0.43542 | 0.43333 | 0.43125 | 0.42639 | 0.42361 | 0.42083 | 0.62847 | 0.62569 | 0.62361 | 0.58542 | 0.58403 | 0.58125 | 0.56528 | 0.56319 | 0.56111 | 0.51528 | 0.51319 | 0.51111 | 0.45625 | 0.45417 | 0.45278 | 0.44306 | 0.44028 | 0.68958 | 0.68681 | 0.68472 | 0.63889 | 0.63819 | 0.63611 | 0.59861 | 0.58403 | 0.58125 | 0.57917 | 0.52292 | 0.52014 | 0.51806 | 0.47014 | 0.4625 | 0.46042 | 0.45833 | 0.67986 | 0.67708 | 0.675 | 0.67292 | 0.64028 | 0.63472 | 0.63264 | 0.60972 | 0.60625 | 0.59653 | 0.69236 | 0.69167 | 0.6875 | 0.68472 | 0.67917 | 0.675 | 0.67083 | 0.66597 | 0.55069 | 0.54861 | 0.54653 | 0.53125 | 0.52917 | 0.52639 | 0.52361 | 0.52153 | 0.51944 | 0.50972 | 0.50625 | 0.50347 | 0.45972 | 0.45764 | 0.45486 | 0.68472 | 0.68125 | 0.67778 | 0.66181 | 0.65972 | 0.65764 | 0.53264 | 0.52986 | 0.52778 | 0.52222 | 0.51875 | 0.51597 | 0.45069 | 0.44861 | 0.44444 | 0.45486 | 0.45139 | 0.44653 | 0.42431 | 0.42153 | 0.41806 | 0.67639 | 0.67361 | 0.67083 | 0.66667 | 0.65972 | 0.65764 | 0.51806 | 0.51528 | 0.5125 | 0.49236 | 0.49028 | 0.48819 | 0.48264 | 0.47639 | 0.47222 | 0.46389 | 0.46181 | 0.45903 | 0.45278 | 0.45 | 0.44653 | 0.69028 | 0.68889 | 0.68681 | 0.63819 | 0.63472 | 0.63194 | 0.49444 | 0.49167 | 0.48819 | 0.48056 | 0.47708 | 0.47431
366 | AI2 |  | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL
367 | AI3 |  | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL
368 | AI4 |  | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL | F3BL
369 | AI5 |  | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 1.6 | 1.6 | 1.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 2.6 | 2.6 | 2.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 1 2 2.6 | 1 2 2.6 | 1 2 2.6 | 1 2 2.6 | 1 2 2.6 | 1 2 2.6 | 1 2 2.6 | 1 2 2.6 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 1.6 | 1.6 | 1.6 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 1.6 | 1.6 | 1.6 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8 | 2.8
370 | AI6 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
371 | AI7 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
372 | AI8 |  | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | AS | AS | AS | AS | AS | AS | AS | AS | AS | AS | AS | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | AS | AS | AS | AS | AS | AS | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | AS | AS | AS | AS | AS | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | AS + MJ | AS + MJ | AS + MJ | AS | AS | AS | AS | AS + MJ | AS + MJ | AS + MJ | AS + MJ | AS + MJ | AS + MJ | AS | AS | AS | AS | AS | AS | AS | AS | AS | AS | AS | AS | AS | AS | AS | AS | AS | AS | AS | AS | AS | AS | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ | MJ
373 | AI9 |  | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice Retaining plate (centre) blanked 3rd oil injection point 1.2 orifice Centre Bearing 0.8 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star VVR control valves shut | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR New star | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR Test @20Hz (higher duty) | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR Test @20Hz (higher duty) | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR Test @20Hz (higher duty) | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR Test @20Hz (higher duty) | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR Test @20Hz (higher duty) | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft open suction end Retaining plate (centre) 1.2 orifice Retaining plate (bottom) 1.2 orifice 3rd oil injection point 1.2 orifice Oil drain open Suction Gauge: Before strainer econ plug fitted OIL controlled VVR Slide modified to 1.6/2.6VR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer Withour econ plug OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer Withour econ plug OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer Withour econ plug OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer Withour econ plug OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer Withour econ plug OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer Withour econ plug OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer Withour econ plug OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer Withour econ plug OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer Withour econ plug OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer Withour econ plug OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer Withour econ plug OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer Withour econ plug OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer Withour econ plug OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer Withour econ plug OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer Withour econ plug OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice + plug Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice + plug Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice + plug Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice + plug Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice + plug Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice + plug Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice + plug Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice + plug Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice + plug Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice + plug Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice + plug Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice + plug Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice + plug Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice + plug Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Retaining plate (centre) 1.2 orifice Retaining plate (bottom) blanked econ (3rd oil injection point) 1.2 orifice + plug Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Shaft blanked Centre bearing blanked Retaining plate blanked econ (3rd oil injection point) 1.2 orifice Oil drain blanked Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Center Bearing orifice 3rd Bearing oil feed orifice Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Center Bearing orifice 3rd Bearing oil feed orifice Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Center Bearing orifice 3rd Bearing oil feed orifice Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Center Bearing orifice 3rd Bearing oil feed orifice Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Center Bearing orifice 3rd Bearing oil feed orifice Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR | No relief valves Damage to main rotor Center Bearing orifice 3rd Bearing oil feed orifice Oil drain valve plugged Suction Gauge: Before strainer econ plugged OIL controlled VVR
374 | AI10 |  | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD, New star | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD - target duty 524 kW | 310-240FS, 2.6VR MOD - target duty 524 kW | 310-240FS, 2.6VR MOD - target duty 524 kW | 310-240FS, 2.6VR MOD - target duty 524 kW | 310-240FS, 2.6VR MOD - target duty 524 kW | 310-240FS, 2.6VR MOD - target duty 332 kW | 310-240FS, 2.6VR MOD - target duty 332 kW | 310-240FS, 2.6VR MOD - target duty 332 kW | 310-240FS, 2.6VR MOD - target duty 332 kW | 310-240FS, 2.6VR MOD - target duty 148 kW | 310-240FS, 2.6VR MOD - target duty 148 kW | 310-240FS, 2.6VR MOD - target duty 148 kW | 310-240FS, 2.6VR MOD - target duty 148 kW | 310-240FS, 2.6VR MOD - target duty 148 kW | 310-240FS, 2.6VR MOD - target duty 569kW | 310-240FS, 2.6VR MOD - target duty 569kW | 310-240FS, 2.6VR MOD - target duty 569kW | 310-240FS, 2.6VR MOD - target duty 361kW | 310-240FS, 2.6VR MOD - target duty 361kW | 310-240FS, 2.6VR MOD - target duty 361kW | 310-240FS, 2.6VR MOD - target duty 361kW | 310-240FS, 2.6VR MOD - target duty 361kW | 310-240FS, 2.6VR MOD - target duty 361kW | 310-240FS, 2.6VR MOD - target duty 361kW | 310-240FS, 2.6VR MOD - target duty 361kW | 310-240FS, 2.6VR MOD - target duty 361kW | 310-240FS, 2.6VR MOD - target duty 361kW | 310-240FS, 2.6VR MOD - target duty 161kW | 310-240FS, 2.6VR MOD - target duty 161kW | 310-240FS, 2.6VR MOD - target duty 161kW | 310-240FS, 2.6VR MOD - target duty 161kW | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD | 310-240FS, 2.6VR MOD | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE - Target duty 347.6 | 310240FS - DAE - Target duty 347.6 | 310240FS - DAE - Target duty 347.6 | 310240FS - DAE - Target duty 347.6 | 310240FS - DAE - Target duty 347.6 | 310240FS - DAE - Target duty 347.6 | 310240FS - DAE - Target duty 547.2 | 310240FS - DAE - Target duty 547.2 | 310240FS - DAE - Target duty 547.2 | 310240FS - DAE - Target duty 547.2 | 310240FS - DAE - Target duty 547.2 | 310240FS - DAE - Target duty 547.2 | 310240FS - DAE - Target duty 585.8 | 310240FS - DAE - Target duty 585.8 | 310240FS - DAE - Target duty 585.8 | 310240FS - DAE - Target duty 585.8 | 310240FS - DAE - Target duty 585.8 | 310240FS - DAE - Target duty 585.8 | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE | 310240FS - DAE
375 | AI11 |  | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134 | 134
376 | AI12 |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
377 | AI13 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
378 | AI14 |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
379 | AI15 |  | 388.2641 | 387.5511 | 386.9174 | 387.7073 | 387.4836 | 387.6315 | 388.9334 | 388.3397 | 389.2479 | 388.2533 | 388.1513 | 386.7704 | 386.3423 | 387.1246 | 386.7847 | 388.4051 | 388.6947 | 388.5928 | 389.117 | 389.2523 | 389.0602 | 389.5085 | 390.2503 | 390.4623 | 390.0238 | 391.6401 | 391.7716 | 393.81 | 394.7434 | 393.7436 | 394.4654 | 393.6258 | 394.1695 | 395.1822 | 394.5129 | 394.7791 | 393.8401 | 393.6881 | 392.6435 | 393.0159 | 392.3616 | 393.5795 | 383.9394 | 383.481 | 383.3707 | 382.9747 | 380.8294 | 381.8098 | 381.0662 | 385.5022 | 386.0101 | 385.6754 | 386.0428 | 385.6537 | 386.6274 | 385.4451 | 385.1793 | 385.8975 | 394.4695 | 385.4119 | 385.6476 | 385.735 | 385.1328 | 384.3926 | 383.1533 | 386.387 | 386.29 | 393.3895 | 393.2566 | 392.8126 | 392.4107 | 392.1945 | 392.5252 | 392.59 | 391.3191 | 391.7668 | 392.815 | 393.0038 | 392.2923 | 391.7883 | 392.8479 | 393.6353 | 391.1621 | 391.4827 | 391.6231 | 394.8878 | 395.919 | 395.5744 | 395.6564 | 395.4878 | 395.7836 | 386.4995 | 387.2161 | 386.209 | 383.9177 | 383.451 | 383.5436 | 380.266 | 387.0678 | 387.1141 | 386.715 | 388.3051 | 388.6003 | 386.9339 | 388.0573 | 386.8793 | 386.1083 | 387.2325 | 387.2848 | 387.661 | 387.3199 | 389.1295 | 389.3866 | 388.0535 | 387.9746 | 386.0808 | 390.3037 | 393.3854 | 384.4915 | 382.6445 | 387.1941 | 388.041 | 386.3311 | 385.9894 | 392.2217 | 392.497 | 393.0242 | 393.0669 | 392.8805 | 392.1883 | 392.9397 | 392.9462 | 385.4534 | 385.9318 | 385.4666 | 391.3109 | 392.0096 | 392.3896 | 391.8893 | 391.1028 | 391.6318 | 391.0598 | 389.1586 | 388.2585 | 388.0193 | 391.5457 | 391.7004 | 391.6513 | 391.6281 | 394.1862 | 394.0377 | 394.0753 | 393.7108 | 390.3849 | 390.0565 | 390.0321 | 387.9602 | 387.6589 | 386.748 | 391.1575 | 391.2625 | 391.8539 | 391.0021 | 390.918 | 390.7022 | 390.0443 | 390.6852 | 386.2664 | 387.7201 | 386.4187 | 385.6258 | 386.2263 | 386.3082 | 385.8322 | 386.313 | 386.077 | 387.1243 | 384.8367 | 385.8713 | 389.9212 | 390.6934 | 390.4132 | 388.0284 | 387.7968 | 385.5854 | 391.2403 | 390.3618 | 390.6406 | 388.0632 | 387.6086 | 388.1396 | 388.5059 | 389.1731 | 388.4681 | 392.7734 | 392.2895 | 392.4039 | 389.1583 | 388.4236 | 388.9763 | 386.8425 | 387.427 | 388.3141 | 394.2373 | 392.8414 | 394.1276 | 394.1279 | 393.7126 | 393.8521 | 384.4383 | 382.4084 | 382.4591 | 380.6678 | 380.8088 | 380.7841 | 385.9788 | 388.4112 | 386.6851 | 387.3548 | 388.1031 | 385.9949 | 383.6124 | 383.9015 | 383.8327 | 393.0576 | 393.307 | 392.1948 | 393.6078 | 394.125 | 393.3839 | 387.068 | 387.3742 | 387.6238 | 387.2894 | 387.2281 | 387.8787
380 | Date |  | 386.1162 | 386.7173 | 385.7052 | 384.607 | 384.7304 | 384.5691 | 386.1375 | 383.432 | 386.4496 | 385.2595 | 384.0411 | 384.9908 | 383.5101 | 382.5452 | 382.7686 | 389.7695 | 389.6612 | 389.8767 | 390.6935 | 390.7328 | 390.2552 | 389.9034 | 391.1307 | 390.639 | 391.3562 | 392.4185 | 392.1262 | 391.8075 | 392.4583 | 391.7868 | 392.6043 | 391.5729 | 392.4397 | 393.8799 | 393.8447 | 394.2563 | 392.5451 | 392.3977 | 392.6408 | 392.4468 | 392.3472 | 393.2294 | 391.9056 | 390.4816 | 391.5342 | 390.4335 | 389.286 | 389.964 | 389.7982 | 381.7107 | 381.4735 | 382.4637 | 385.0928 | 383.965 | 384.1287 | 383.8629 | 383.2989 | 384.0186 | 390.6887 | 382.502 | 383.1293 | 393.9749 | 393.4142 | 392.2578 | 390.9904 | 394.8124 | 394.7076 | 392.6014 | 392.91 | 392.6588 | 391.0334 | 390.9886 | 390.7425 | 391.3545 | 389.3866 | 390.6586 | 394.0321 | 394.265 | 393.2913 | 392.836 | 394.2957 | 394.9097 | 389.1173 | 388.9279 | 389.3839 | 393.8973 | 394.2282 | 394.0718 | 394.6437 | 394.13 | 394.9829 | 394.5494 | 394.8925 | 393.8838 | 392.0005 | 392.5687 | 392.052 | 388.3751 | 381.3617 | 382.4113 | 380.4896 | 383.0838 | 382.5013 | 382.6371 | 382.0497 | 381.9776 | 382.4868 | 383.7468 | 384.1285 | 383.8503 | 385.13 | 385.1713 | 385.1044 | 383.2865 | 383.0254 | 381.8683 | 386.4217 | 387.2332 | 392.6136 | 391.3571 | 394.3681 | 395.2393 | 393.9332 | 393.6915 | 390.1962 | 390.1006 | 390.6992 | 393.2138 | 392.9273 | 392.4963 | 393.7762 | 393.3405 | 393.7981 | 393.7752 | 393.8197 | 389.7375 | 389.7364 | 390.5642 | 389.8905 | 390.2445 | 390.8649 | 390.3955 | 388.7134 | 387.4984 | 387.3201 | 392.7039 | 393.0231 | 392.7546 | 392.6679 | 389.1196 | 386.8175 | 386.186 | 386.4724 | 386.8192 | 384.3913 | 384.1288 | 383.4532 | 381.8725 | 383.0827 | 387.6346 | 385.6198 | 386.3508 | 385.4752 | 384.74 | 385.4522 | 384.3005 | 384.2383 | 384.4596 | 384.53 | 382.136 | 382.6006 | 380.7853 | 382.1909 | 381.5777 | 382.6405 | 382.0448 | 382.3062 | 379.0173 | 380.6895 | 389.8078 | 390.872 | 390.9857 | 385.1261 | 386.0327 | 383.0533 | 387.1915 | 386.4386 | 385.0125 | 385.0146 | 384.1147 | 383.7226 | 384.1563 | 382.2769 | 383.7354 | 392.2608 | 391.4256 | 392.2731 | 386.9452 | 386.1435 | 386.5744 | 384.1817 | 385.0788 | 386.017 | 394.5173 | 393.1307 | 394.3738 | 394.4861 | 393.8972 | 394.4909 | 392.2379 | 389.9401 | 390.2834 | 388.3575 | 388.4059 | 388.4544 | 383.8016 | 384.6028 | 384.0892 | 383.3555 | 384.4915 | 384.8742 | 380.9635 | 380.8886 | 381.7089 | 386.5121 | 386.6692 | 386.2132 | 392.8599 | 393.3441 | 392.0817 | 383.3045 | 384.9562 | 384.4667 | 385.0195 | 384.72 | 386.0963
381 | Time |  | 379.1138 | 378.9259 | 377.6324 | 378.3299 | 378.3192 | 378.2905 | 379.3436 | 379.4761 | 379.6882 | 379.214 | 378.9702 | 377.5803 | 377.8619 | 377.9436 | 378.0915 | 388.9507 | 388.8455 | 389.296 | 390.3522 | 389.9539 | 389.0529 | 388.7398 | 389.917 | 389.0869 | 390.2733 | 390.7001 | 390.5761 | 393.0031 | 393.3387 | 392.3907 | 391.6277 | 391.6095 | 391.2347 | 391.2354 | 390.9169 | 390.7461 | 389.7799 | 390.2195 | 388.9976 | 388.9171 | 388.3301 | 389.4741 | 388.0332 | 387.1348 | 388.4244 | 387.8673 | 387.8373 | 388.9896 | 389.0546 | 377.1345 | 378.0223 | 377.2223 | 377.6215 | 377.0165 | 378.1057 | 377.3684 | 377.8238 | 377.0073 | 385.1087 | 376.6192 | 376.9174 | 391.2808 | 391.6155 | 390.5056 | 391.4287 | 393.5194 | 393.2478 | 389.2656 | 388.8925 | 388.3023 | 388.5757 | 388.3694 | 388.6977 | 388.6993 | 387.3777 | 388.3758 | 392.0933 | 392.26 | 391.281 | 391.1024 | 392.7999 | 392.9307 | 389.6655 | 389.4943 | 389.5616 | 392.2081 | 392.6364 | 392.5833 | 391.8213 | 391.5823 | 391.8355 | 390.504 | 389.7223 | 390.6406 | 390.1956 | 391.4757 | 389.4873 | 388.5945 | 378.2448 | 378.4693 | 378.7195 | 380.1138 | 379.8886 | 378.0668 | 379.1275 | 377.8041 | 377.9981 | 378.4664 | 378.1517 | 378.7359 | 378.3372 | 379.3531 | 380.1629 | 379.5038 | 378.6259 | 376.8959 | 380.4741 | 383.6371 | 389.4464 | 388.6583 | 390.8068 | 391.7011 | 390.6139 | 392.7518 | 390.3921 | 391.5788 | 391.7321 | 392.6519 | 391.7614 | 391.829 | 392.9538 | 392.1305 | 392.1866 | 391.8255 | 391.5054 | 388.5952 | 389.0021 | 389.4646 | 388.8311 | 387.4098 | 388.0265 | 387.5187 | 385.4316 | 384.5835 | 384.5211 | 392.9779 | 392.6905 | 392.4282 | 392.4696 | 384.3642 | 385.4394 | 385.7145 | 384.8034 | 381.5387 | 381.4186 | 380.8696 | 379.7609 | 380.144 | 378.1388 | 381.3724 | 382.0777 | 382.6908 | 382.0544 | 383.4097 | 383.0437 | 382.4328 | 383.8591 | 376.816 | 378.1704 | 377.0081 | 376.334 | 376.3874 | 376.6089 | 377.3972 | 376.5607 | 376.067 | 377.8738 | 375.5023 | 377.1144 | 385.2007 | 385.8763 | 385.6395 | 377.9299 | 378.2784 | 375.522 | 381.5492 | 380.4007 | 380.6953 | 378.4195 | 378.381 | 377.9886 | 379.1902 | 380.4515 | 379.6748 | 388.3934 | 387.6425 | 387.5642 | 386.1824 | 385.7353 | 386.064 | 385.3956 | 386.3858 | 387.1795 | 393.0236 | 391.7246 | 393.1274 | 392.8652 | 391.8794 | 392.5566 | 388.8506 | 386.3064 | 387.4751 | 388.7902 | 387.4941 | 388.4305 | 377.1754 | 378.5501 | 377.6105 | 377.6129 | 378.8078 | 377.4156 | 375.1075 | 375.1915 | 375.0409 | 385.1267 | 385.8653 | 384.0839 | 389.409 | 390.002 | 390.1587 | 377.7938 | 378.6241 | 378.7119 | 378.1399 | 378.0881 | 378.6528
382 | Compressor Type |  | 388.2641 | 387.5511 | 386.9174 | 387.7073 | 387.4836 | 387.6315 | 388.9334 | 388.3397 | 389.2479 | 388.2533 | 388.1513 | 386.7704 | 386.3423 | 387.1246 | 386.7847 | 388.4051 | 388.6947 | 388.5928 | 389.117 | 389.2523 | 389.0602 | 389.5085 | 390.2503 | 390.4623 | 390.0238 | 391.6401 | 391.7716 | 393.81 | 394.7434 | 393.7436 | 394.4654 | 393.6258 | 394.1695 | 395.1822 | 394.5129 | 394.7791 | 393.8401 | 393.6881 | 392.6435 | 393.0159 | 392.3616 | 393.5795 | 383.9394 | 383.481 | 383.3707 | 382.9747 | 380.8294 | 381.8098 | 381.0662 | 385.5022 | 386.0101 | 385.6754 | 386.0428 | 385.6537 | 386.6274 | 385.4451 | 385.1793 | 385.8975 | 394.4695 | 385.4119 | 385.6476 | 385.735 | 385.1328 | 384.3926 | 383.1533 | 386.387 | 386.29 | 393.3895 | 393.2566 | 392.8126 | 392.4107 | 392.1945 | 392.5252 | 392.59 | 391.3191 | 391.7668 | 392.815 | 393.0038 | 392.2923 | 391.7883 | 392.8479 | 393.6353 | 391.1621 | 391.4827 | 391.6231 | 394.8878 | 395.919 | 395.5744 | 395.6564 | 395.4878 | 395.7836 | 386.4995 | 387.2161 | 386.209 | 383.9177 | 383.451 | 383.5436 | 380.266 | 387.0678 | 387.1141 | 386.715 | 388.3051 | 388.6003 | 386.9339 | 388.0573 | 386.8793 | 386.1083 | 387.2325 | 387.2848 | 387.661 | 387.3199 | 389.1295 | 389.3866 | 388.0535 | 387.9746 | 386.0808 | 390.3037 | 393.3854 | 384.4915 | 382.6445 | 387.1941 | 388.041 | 386.3311 | 385.9894 | 392.2217 | 392.497 | 393.0242 | 393.0669 | 392.8805 | 392.1883 | 392.9397 | 392.9462 | 385.4534 | 385.9318 | 385.4666 | 391.3109 | 392.0096 | 392.3896 | 391.8893 | 391.1028 | 391.6318 | 391.0598 | 389.1586 | 388.2585 | 388.0193 | 391.5457 | 391.7004 | 391.6513 | 391.6281 | 394.1862 | 394.0377 | 394.0753 | 393.7108 | 390.3849 | 390.0565 | 390.0321 | 387.9602 | 387.6589 | 386.748 | 391.1575 | 391.2625 | 391.8539 | 391.0021 | 390.918 | 390.7022 | 390.0443 | 390.6852 | 386.2664 | 387.7201 | 386.4187 | 385.6258 | 386.2263 | 386.3082 | 385.8322 | 386.313 | 386.077 | 387.1243 | 384.8367 | 385.8713 | 389.9212 | 390.6934 | 390.4132 | 388.0284 | 387.7968 | 385.5854 | 391.2403 | 390.3618 | 390.6406 | 388.0632 | 387.6086 | 388.1396 | 388.5059 | 389.1731 | 388.4681 | 392.7734 | 392.2895 | 392.4039 | 389.1583 | 388.4236 | 388.9763 | 386.8425 | 387.427 | 388.3141 | 394.2373 | 392.8414 | 394.1276 | 394.1279 | 393.7126 | 393.8521 | 384.4383 | 382.4084 | 382.4591 | 380.6678 | 380.8088 | 380.7841 | 385.9788 | 388.4112 | 386.6851 | 387.3548 | 388.1031 | 385.9949 | 383.6124 | 383.9015 | 383.8327 | 393.0576 | 393.307 | 392.1948 | 393.6078 | 394.125 | 393.3839 | 387.068 | 387.3742 | 387.6238 | 387.2894 | 387.2281 | 387.8787
383 | Compressor ID |  | 386.1162 | 386.7173 | 385.7052 | 384.607 | 384.7304 | 384.5691 | 386.1375 | 383.432 | 386.4496 | 385.2595 | 384.0411 | 384.9908 | 383.5101 | 382.5452 | 382.7686 | 389.7695 | 389.6612 | 389.8767 | 390.6935 | 390.7328 | 390.2552 | 389.9034 | 391.1307 | 390.639 | 391.3562 | 392.4185 | 392.1262 | 391.8075 | 392.4583 | 391.7868 | 392.6043 | 391.5729 | 392.4397 | 393.8799 | 393.8447 | 394.2563 | 392.5451 | 392.3977 | 392.6408 | 392.4468 | 392.3472 | 393.2294 | 391.9056 | 390.4816 | 391.5342 | 390.4335 | 389.286 | 389.964 | 389.7982 | 381.7107 | 381.4735 | 382.4637 | 385.0928 | 383.965 | 384.1287 | 383.8629 | 383.2989 | 384.0186 | 390.6887 | 382.502 | 383.1293 | 393.9749 | 393.4142 | 392.2578 | 390.9904 | 394.8124 | 394.7076 | 392.6014 | 392.91 | 392.6588 | 391.0334 | 390.9886 | 390.7425 | 391.3545 | 389.3866 | 390.6586 | 394.0321 | 394.265 | 393.2913 | 392.836 | 394.2957 | 394.9097 | 389.1173 | 388.9279 | 389.3839 | 393.8973 | 394.2282 | 394.0718 | 394.6437 | 394.13 | 394.9829 | 394.5494 | 394.8925 | 393.8838 | 392.0005 | 392.5687 | 392.052 | 388.3751 | 381.3617 | 382.4113 | 380.4896 | 383.0838 | 382.5013 | 382.6371 | 382.0497 | 381.9776 | 382.4868 | 383.7468 | 384.1285 | 383.8503 | 385.13 | 385.1713 | 385.1044 | 383.2865 | 383.0254 | 381.8683 | 386.4217 | 387.2332 | 392.6136 | 391.3571 | 394.3681 | 395.2393 | 393.9332 | 393.6915 | 390.1962 | 390.1006 | 390.6992 | 393.2138 | 392.9273 | 392.4963 | 393.7762 | 393.3405 | 393.7981 | 393.7752 | 393.8197 | 389.7375 | 389.7364 | 390.5642 | 389.8905 | 390.2445 | 390.8649 | 390.3955 | 388.7134 | 387.4984 | 387.3201 | 392.7039 | 393.0231 | 392.7546 | 392.6679 | 389.1196 | 386.8175 | 386.186 | 386.4724 | 386.8192 | 384.3913 | 384.1288 | 383.4532 | 381.8725 | 383.0827 | 387.6346 | 385.6198 | 386.3508 | 385.4752 | 384.74 | 385.4522 | 384.3005 | 384.2383 | 384.4596 | 384.53 | 382.136 | 382.6006 | 380.7853 | 382.1909 | 381.5777 | 382.6405 | 382.0448 | 382.3062 | 379.0173 | 380.6895 | 389.8078 | 390.872 | 390.9857 | 385.1261 | 386.0327 | 383.0533 | 387.1915 | 386.4386 | 385.0125 | 385.0146 | 384.1147 | 383.7226 | 384.1563 | 382.2769 | 383.7354 | 392.2608 | 391.4256 | 392.2731 | 386.9452 | 386.1435 | 386.5744 | 384.1817 | 385.0788 | 386.017 | 394.5173 | 393.1307 | 394.3738 | 394.4861 | 393.8972 | 394.4909 | 392.2379 | 389.9401 | 390.2834 | 388.3575 | 388.4059 | 388.4544 | 383.8016 | 384.6028 | 384.0892 | 383.3555 | 384.4915 | 384.8742 | 380.9635 | 380.8886 | 381.7089 | 386.5121 | 386.6692 | 386.2132 | 392.8599 | 393.3441 | 392.0817 | 383.3045 | 384.9562 | 384.4667 | 385.0195 | 384.72 | 386.0963
384 | Compressor Size |  | 379.1138 | 378.9259 | 377.6324 | 378.3299 | 378.3192 | 378.2905 | 379.3436 | 379.4761 | 379.6882 | 379.214 | 378.9702 | 377.5803 | 377.8619 | 377.9436 | 378.0915 | 388.9507 | 388.8455 | 389.296 | 390.3522 | 389.9539 | 389.0529 | 388.7398 | 389.7605 | 389.0869 | 390.2733 | 390.7001 | 390.5761 | 393.0031 | 393.3387 | 392.3907 | 391.6277 | 391.6095 | 391.2347 | 391.2354 | 390.9169 | 390.7461 | 389.7799 | 390.2195 | 388.9201 | 388.9171 | 388.3301 | 389.4741 | 388.0332 | 387.1348 | 388.4244 | 387.8673 | 387.8373 | 388.9896 | 389.0546 | 377.1345 | 378.0223 | 377.2223 | 377.6215 | 377.0165 | 378.1057 | 377.3684 | 377.8238 | 377.0073 | 385.1087 | 376.6192 | 376.9174 | 391.2808 | 391.6155 | 390.5056 | 391.4287 | 393.5194 | 393.2478 | 389.2656 | 388.8925 | 388.3023 | 388.5757 | 388.3694 | 388.6977 | 388.6993 | 387.3777 | 388.3758 | 392.0933 | 392.26 | 391.281 | 391.1024 | 392.7999 | 392.9307 | 389.6655 | 389.4943 | 389.5616 | 392.2081 | 392.6364 | 392.5833 | 391.8213 | 391.5823 | 391.8355 | 390.504 | 389.7223 | 390.6406 | 390.1956 | 391.4757 | 389.4873 | 388.5945 | 378.2448 | 378.4693 | 378.7195 | 380.1138 | 379.8886 | 378.0668 | 379.1275 | 377.8041 | 377.9981 | 378.4664 | 378.1517 | 378.7359 | 378.3372 | 379.3531 | 380.1629 | 379.5038 | 378.6259 | 376.8959 | 380.4741 | 383.6371 | 389.4464 | 388.6583 | 390.8068 | 391.7011 | 390.6139 | 392.7518 | 390.3921 | 391.5788 | 391.7321 | 392.6519 | 391.7614 | 391.829 | 392.9538 | 392.1305 | 392.1866 | 391.8255 | 391.5054 | 388.5952 | 389.0021 | 389.4646 | 388.8311 | 387.4098 | 388.0265 | 387.5187 | 385.4316 | 384.5835 | 384.5211 | 392.9779 | 392.6905 | 392.4282 | 392.4696 | 384.3642 | 385.4394 | 385.7145 | 384.8034 | 381.5387 | 381.4186 | 380.8696 | 379.7609 | 380.144 | 378.1388 | 381.3724 | 382.0777 | 382.6908 | 382.0544 | 383.4097 | 383.0437 | 382.4328 | 383.8591 | 376.816 | 378.1704 | 377.0081 | 376.334 | 376.3874 | 376.6089 | 377.3972 | 376.5607 | 376.067 | 377.8738 | 375.5023 | 377.1144 | 385.2007 | 385.8763 | 385.6395 | 377.9299 | 378.2784 | 375.522 | 381.5492 | 380.4007 | 380.6953 | 378.4195 | 378.381 | 377.9886 | 379.1902 | 380.4515 | 379.6748 | 388.3934 | 387.6425 | 387.5642 | 386.1824 | 385.7353 | 386.064 | 385.3956 | 386.3858 | 387.1795 | 393.0236 | 391.7246 | 393.1274 | 392.8652 | 391.8794 | 392.5566 | 388.8506 | 386.3064 | 387.4751 | 388.7902 | 387.4941 | 388.4305 | 377.1754 | 378.5501 | 377.6105 | 377.6129 | 378.8078 | 377.4156 | 375.1075 | 375.1915 | 375.0409 | 385.1267 | 385.8653 | 384.0839 | 389.409 | 390.002 | 390.1587 | 377.7938 | 378.6241 | 378.7119 | 378.1399 | 378.0881 | 378.6528
385 | VR |  | 465.1295 | 464.8799 | 465.8368 | 437.4373 | 437.676 | 436.8455 | 416.5579 | 417.0422 | 415.9942 | 402.7699 | 397.7957 | 400.1176 | 389.0216 | 390.2095 | 387.0678 | 42.586 | 41.959 | 42.5356 | 45.3282 | 44.7879 | 44.038 | 42.6811 | 42.1287 | 42.2137 | 43.8151 | 43.3754 | 43.6574 | 99.2111 | 98.9238 | 98.3653 | 102.3643 | 102.9821 | 102.4508 | 106.7071 | 105.5787 | 105.2498 | 102.7369 | 102.9341 | 103.6481 | 104.978 | 105.5759 | 106.0849 | 192.6172 | 193.5763 | 192.5488 | 195.5211 | 206.7732 | 208.264 | 207.1958 | 369.7401 | 370.321 | 370.494 | 407.8381 | 407.2542 | 409.3835 | 409.7164 | 405.5536 | 406.4679 | 398.9392 | 405.7748 | 409.4698 | 197.2947 | 195.4498 | 197.3222 | 211.1828 | 208.877 | 210.4298 | 107.5964 | 106.9401 | 105.8934 | 100.6003 | 100.9459 | 101.1183 | 100.8844 | 101.1716 | 100.58 | 41.196 | 41.9138 | 40.9422 | 44.0314 | 43.6532 | 44.268 | 100.0473 | 100.38 | 98.9103 | 104.9581 | 104.3297 | 104.139 | 106.6916 | 106.7099 | 105.8669 | 199.0384 | 201.7561 | 201.35 | 208.8348 | 210.6616 | 208.1948 | 208.9447 | 367.1387 | 366.6719 | 369.4891 | 366.4696 | 366.1901 | 369.475 | 367.8917 | 371.4444 | 410.3301 | 409.7719 | 405.7678 | 403.7374 | 406.6094 | 411.0409 | 401.9374 | 404.1312 | 401.8522 | 402.7253 | 404.2369 | 399.5616 | 193.9173 | 195.5197 | 193.944 | 194.6697 | 197.6336 | 194.3211 | 98.5969 | 98.2443 | 97.7495 | 42.4155 | 41.7892 | 42.6723 | 44.2199 | 43.9915 | 208.5746 | 204.8336 | 208.2424 | 104.0913 | 105.5597 | 105.3829 | 104.5507 | 107.3508 | 107.072 | 106.3972 | 106.4333 | 108.8735 | 107.9682 | 44.8417 | 44.1796 | 43.6032 | 44.4289 | 359.6462 | 360.3393 | 359.8021 | 360.1237 | 399.3037 | 401.4624 | 403.23 | 397.5884 | 398.5031 | 398.1938 | 403.9355 | 401.7544 | 400.4796 | 401.166 | 395.7559 | 398.2029 | 397.6313 | 393.9594 | 399.9829 | 400.6167 | 402.3714 | 403.8621 | 407.6304 | 410.6779 | 402.6581 | 403.8256 | 405.5116 | 364.8774 | 367.6853 | 365.4373 | 104.3809 | 104.141 | 102.6989 | 405.2731 | 405.2249 | 406.6244 | 398.846 | 400.5182 | 398.1597 | 403.2951 | 406.8945 | 403.5141 | 363.4616 | 361.5596 | 364.7188 | 106.2106 | 105.6429 | 103.9087 | 105.7443 | 105.7645 | 106.3692 | 100.2501 | 100.0857 | 99.2755 | 41.9809 | 42.1843 | 41.7606 | 44.2636 | 44.2237 | 43.6761 | 196.7158 | 198.2908 | 197.806 | 208.0993 | 208.3936 | 209.2083 | 401.1018 | 395.487 | 399.3512 | 402.4721 | 400.7401 | 398.0508 | 402.9233 | 399.3172 | 403.7615 | 359.0219 | 355.6795 | 354.856 | 106.6884 | 106.7749 | 106.9056 | 401.6338 | 405.6702 | 401.1818 | 405.4443 | 407.9586 | 403.714
386 | Motor Size |  | 470.4061 | 469.462 | 468.8062 | 444.6569 | 446.6448 | 442.2544 | 422.0802 | 421.7105 | 422.262 | 410.938 | 405.8891 | 407.5797 | 397.4424 | 392.2914 | 390.2926 | 41.5347 | 40.3505 | 41.0147 | 43.0164 | 42.9556 | 42.6223 | 41.637 | 40.8221 | 42.4374 | 42.3453 | 42.6942 | 43.5303 | 96.2361 | 96.872 | 96.0853 | 100.4163 | 100.415 | 100.3219 | 107.169 | 105.9392 | 107.2016 | 103.9149 | 103.5846 | 105.1416 | 107.094 | 108.0093 | 107.6386 | 193.831 | 193.2374 | 196.0472 | 196.3883 | 212.3971 | 214.8407 | 210.6771 | 373.8894 | 377.7656 | 374.6856 | 411.6951 | 413.7926 | 416.4415 | 414.2729 | 415.6543 | 413.9488 | 400.2747 | 409.3585 | 412.4362 | 198.6702 | 199.0956 | 198.8477 | 213.0151 | 212.7122 | 212.6876 | 106.8506 | 108.5871 | 108.1186 | 100.6098 | 100.3306 | 101.1104 | 100.4599 | 101.196 | 100.4843 | 40.4575 | 41.5605 | 41.8341 | 43.2225 | 42.1086 | 44.0294 | 96.7844 | 97.7352 | 97.8312 | 103.5112 | 103.1312 | 104.5794 | 106.6256 | 107.0409 | 106.6489 | 203.3994 | 200.8406 | 203.0793 | 218.5591 | 212.8844 | 218.5082 | 213.8986 | 376.0741 | 374.7724 | 374.1692 | 374.5448 | 375.9294 | 378.0917 | 373.1916 | 373.0183 | 417.7165 | 418.0971 | 415.3696 | 408.9479 | 414.5864 | 415.5608 | 407.6325 | 408.5392 | 404.5109 | 402.5404 | 407.6571 | 398.3239 | 193.5027 | 194.1531 | 193.5975 | 195.0374 | 194.955 | 196.6561 | 95.6895 | 94.2544 | 95.2375 | 40.6576 | 40.0611 | 40.6095 | 42.6161 | 42.5085 | 212.0752 | 214.1322 | 211.9313 | 102.4169 | 103.498 | 104.5391 | 103.5562 | 106.6613 | 106.6509 | 106.4423 | 108.6787 | 109.6532 | 109.6073 | 42.2657 | 42.6891 | 42.9878 | 42.0057 | 360.675 | 362.6841 | 361.0677 | 361.5934 | 401.3242 | 401.2519 | 404.2058 | 400.6199 | 403.5039 | 406.406 | 405.4187 | 402.1727 | 400.6845 | 405.5304 | 399.7079 | 400.6594 | 397.746 | 397.3638 | 409.7689 | 408.4648 | 408.2861 | 408.4448 | 412.7133 | 411.8164 | 408.4937 | 407.3052 | 406.1302 | 373.5324 | 373.2789 | 373.7141 | 109.3896 | 110.8564 | 110.6567 | 408.3448 | 407.8336 | 408.4459 | 403.2173 | 404.5591 | 402.7563 | 409.642 | 410.0972 | 405.764 | 368.2458 | 366.5143 | 367.0172 | 107.0224 | 107.3984 | 107.3946 | 104.5636 | 103.2648 | 103.713 | 97.6098 | 97.4012 | 97.9645 | 41.9747 | 41.1678 | 41.5665 | 43.634 | 44.1199 | 43.9461 | 196.3658 | 201.0224 | 198.5457 | 216.4825 | 214.8778 | 212.9872 | 408.5803 | 401.9716 | 405.7374 | 409.0298 | 404.5637 | 407.0818 | 408.4728 | 406.1868 | 407.5453 | 362.8136 | 364.6181 | 360.7411 | 109.0842 | 108.8817 | 107.3377 | 408.0427 | 413.5165 | 406.282 | 414.4395 | 413.8753 | 411.3238
387 | Motor ID |  | 479.598 | 476.627 | 480.4009 | 451.6568 | 452.8101 | 448.6098 | 428.2346 | 426.3165 | 430.6196 | 416.5557 | 414.7835 | 414.9971 | 400.4448 | 399.7036 | 399.485 | 46.9588 | 44.8174 | 46.3839 | 47.7854 | 47.6115 | 47.7711 | 45.8222 | 44.7294 | 46.1016 | 47.5227 | 48.0086 | 47.6129 | 101.5233 | 102.0923 | 101.6451 | 105.7403 | 107.4222 | 106.453 | 113.5903 | 115.5237 | 115.5291 | 109.0844 | 109.8393 | 111.8412 | 115.0265 | 115.4759 | 115.5088 | 192.9976 | 193.2785 | 193.145 | 193.1752 | 210.3529 | 203.8685 | 207.9169 | 377.7567 | 380.9294 | 380.1367 | 417.1368 | 420.1509 | 418.0718 | 418.5641 | 420.6229 | 419.9131 | 406.0162 | 416.5298 | 417.374 | 198.6858 | 196.5078 | 198.3565 | 208.2475 | 207.9318 | 205.3157 | 114.8394 | 115.4956 | 115.3265 | 105.4149 | 105.8118 | 105.7619 | 106.5637 | 105.523 | 106.4277 | 43.0202 | 43.9333 | 43.7925 | 46.3432 | 45.8141 | 46.4298 | 103.444 | 103.2821 | 103.8839 | 112.8296 | 109.581 | 111.4662 | 115.7532 | 115.2437 | 115.8268 | 202.926 | 197.9886 | 197.1766 | 210.2579 | 211.3018 | 210.9482 | 207.2708 | 382.1381 | 382.3322 | 382.2426 | 380.3893 | 381.0325 | 379.596 | 377.4726 | 382.7531 | 419.7683 | 419.9897 | 419.3864 | 415.2794 | 419.1771 | 421.2502 | 412.9662 | 415.6606 | 411.067 | 409.0878 | 413.2569 | 409.0923 | 194.5562 | 194.0718 | 192.1757 | 193.1728 | 194.2406 | 193.6759 | 101.5948 | 101.4753 | 101.95 | 45.1977 | 44.2658 | 44.9619 | 47.2288 | 45.6918 | 206.4048 | 208.3821 | 207.6377 | 109.7312 | 108.5938 | 111.418 | 111.6057 | 117.0289 | 117.0718 | 117.5792 | 118.2015 | 117.4265 | 118.7652 | 46.6779 | 46.9874 | 46.6503 | 45.8407 | 370.4674 | 371.1904 | 369.545 | 367.5979 | 409.0742 | 411.7742 | 413.4091 | 410.0592 | 409.8034 | 408.9916 | 412.9295 | 410.6845 | 411.023 | 411.1498 | 410.317 | 412.18 | 409.9423 | 411.1288 | 411.7937 | 409.6749 | 413.5101 | 412.5161 | 417.0324 | 417.5754 | 414.3751 | 408.7112 | 410.6759 | 376.8148 | 375.249 | 375.9045 | 114.9691 | 113.116 | 112.1962 | 411.8212 | 412.9598 | 410.2328 | 407.0776 | 405.5102 | 408.1494 | 414.9767 | 414.1667 | 412.1024 | 373.7148 | 373.1971 | 371.5716 | 112.1357 | 113.7607 | 112.0673 | 109.5875 | 108.6506 | 109.4506 | 102.3868 | 102.0043 | 102.3327 | 45.3689 | 44.4895 | 44.5868 | 46.2517 | 46.259 | 46.4724 | 194.1053 | 198.2338 | 197.0615 | 211.5869 | 208.4117 | 209.7799 | 411.5932 | 404.3425 | 409.9918 | 415.2467 | 409.9733 | 407.3631 | 413.3945 | 412.0783 | 412.8414 | 368.4577 | 369.1425 | 368.5876 | 115.024 | 115.579 | 114.4309 | 413.1285 | 416.0854 | 408.6791 | 417.7939 | 419.5932 | 416.514
388 | Test Operator |  | 292.3456 | 291.0933 | 291.2538 | 274.3867 | 275.0303 | 272.963 | 261.06 | 260.4595 | 261.7583 | 253.0442 | 250.3067 | 250.7951 | 243.1942 | 242.2472 | 240.992 | 19.6327 | 19.0735 | 19.5051 | 20.5655 | 20.4138 | 20.5025 | 19.815 | 19.0676 | 19.5561 | 19.969 | 20.2063 | 20.7082 | 52.0438 | 52.4021 | 51.8934 | 54.6473 | 54.988 | 54.5901 | 58.7237 | 58.8791 | 59.0996 | 56.3391 | 56.2233 | 57.0856 | 59.3721 | 59.2069 | 59.4785 | 115.547 | 115.4643 | 116.2837 | 116.8157 | 126.4314 | 126.0191 | 125.7056 | 228.5681 | 230.489 | 229.3761 | 253.8824 | 254.116 | 255.0061 | 254.3421 | 254.149 | 253.995 | 251.2872 | 251.4931 | 253.7185 | 119.4992 | 118.79 | 119.4309 | 127.5683 | 128.006 | 127.5888 | 59.1581 | 59.7945 | 59.2685 | 54.1841 | 53.9606 | 54.4708 | 54.5679 | 54.1843 | 54.205 | 19.3043 | 19.9726 | 19.6288 | 20.6619 | 20.0945 | 21.2378 | 52.6734 | 52.8096 | 52.7737 | 57.2978 | 56.5406 | 57.2907 | 59.5372 | 59.1441 | 59.3426 | 122.3535 | 121.1635 | 121.5595 | 128.6453 | 128.3336 | 128.7511 | 126.3583 | 229.86 | 229.8192 | 229.788 | 229.7588 | 230.2063 | 230.3415 | 228.8473 | 230.1678 | 255.5948 | 256.0513 | 254.6313 | 252.0243 | 254.8569 | 257.0034 | 251.7677 | 252.3911 | 249.7002 | 248.1303 | 253.0356 | 250.7873 | 116.0362 | 116.253 | 116.5996 | 117.7818 | 117.9755 | 117.775 | 52.2129 | 51.8846 | 51.9135 | 19.3076 | 18.9079 | 19.4552 | 20.8503 | 19.9527 | 126.2066 | 126.4329 | 126.5345 | 55.8506 | 56.3042 | 57.0558 | 56.9312 | 59.386 | 59.4363 | 59.0296 | 59.8121 | 60.4708 | 60.3824 | 20.7578 | 20.9116 | 20.5648 | 20.537 | 226.7017 | 227.1654 | 226.3685 | 225.8979 | 250.1444 | 250.5474 | 251.8222 | 247.958 | 248.6345 | 248.3697 | 253.0415 | 251.1063 | 250.9324 | 251.6663 | 249.521 | 250.653 | 248.8685 | 248.8877 | 249.8527 | 250.2379 | 250.1678 | 250.0491 | 252.4685 | 253.5992 | 250.4028 | 249.5629 | 249.7189 | 227.605 | 226.5059 | 227.0164 | 59.1048 | 58.9568 | 58.5944 | 251.6153 | 252.1751 | 250.4415 | 250.3699 | 250.0738 | 249.3838 | 252.2843 | 252.7251 | 250.7308 | 226.7294 | 225.7125 | 226.1696 | 58.7229 | 58.9279 | 58.1343 | 56.0385 | 55.5897 | 56.3449 | 51.8491 | 52.0769 | 51.9873 | 19.7068 | 19.8131 | 19.7217 | 20.5707 | 21.0419 | 20.5815 | 117.4799 | 118.1851 | 117.2627 | 127.4955 | 126.3336 | 126.6961 | 249.9693 | 246.878 | 248.761 | 251.2586 | 249.6893 | 248.3999 | 248.9689 | 247.7815 | 249.3591 | 225.4875 | 225.4563 | 223.8227 | 58.3426 | 59.0402 | 58.3082 | 250.4776 | 253.801 | 249.7197 | 254.0856 | 254.7866 | 252.6337
389 | Text |  | 297.4002 | 295.9688 | 296.2024 | 278.8816 | 279.7215 | 277.4669 | 265.2827 | 264.7047 | 266.0056 | 257.1008 | 254.2769 | 254.6969 | 246.8727 | 246.0883 | 244.8459 | 19.6327 | 19.0735 | 19.5051 | 20.5655 | 20.4138 | 20.5025 | 19.815 | 19.0676 | 19.5561 | 19.969 | 20.2063 | 20.7082 | 52.7541 | 53.0711 | 52.599 | 55.3682 | 55.6972 | 55.334 | 59.5149 | 59.6074 | 59.7857 | 57.0882 | 56.9964 | 57.7809 | 60.0533 | 59.9164 | 60.1891 | 116.9815 | 116.8214 | 117.6491 | 118.1612 | 127.9838 | 127.5924 | 127.308 | 231.8969 | 233.9584 | 232.8021 | 257.68 | 257.8798 | 258.9923 | 258.2899 | 258.1311 | 257.9915 | 255.3382 | 255.6266 | 257.7859 | 121.0052 | 120.3011 | 121.0052 | 129.2498 | 129.6764 | 129.3082 | 59.896 | 60.5904 | 59.9891 | 54.8808 | 54.6528 | 55.1598 | 55.2447 | 54.8844 | 54.9074 | 19.3043 | 19.9726 | 19.6288 | 20.6619 | 20.0945 | 21.2378 | 53.3917 | 53.5965 | 53.4939 | 58.0551 | 57.343 | 58.0521 | 60.2698 | 59.5153 | 60.0978 | 123.8604 | 122.6675 | 123.1013 | 130.2757 | 130.0259 | 130.4278 | 128.0659 | 233.3126 | 233.1979 | 233.3763 | 233.2087 | 233.7648 | 233.7109 | 232.3788 | 233.665 | 259.8334 | 260.2949 | 258.7534 | 256.1062 | 258.9574 | 261.2513 | 255.8256 | 256.6155 | 253.7489 | 252.1496 | 257.1688 | 254.8527 | 117.4686 | 117.7043 | 117.9701 | 119.1463 | 119.4082 | 119.2404 | 52.8883 | 52.5699 | 52.6022 | 19.3076 | 18.9079 | 19.4552 | 20.8503 | 19.9527 | 127.9084 | 128.1674 | 128.222 | 56.6457 | 57.1396 | 57.8228 | 57.7325 | 60.1257 | 60.1361 | 59.7488 | 60.5038 | 61.2534 | 61.1388 | 20.7578 | 20.9116 | 20.5648 | 20.537 | 230.0805 | 230.7365 | 229.9608 | 229.4551 | 254.0111 | 254.6045 | 256.0167 | 251.9009 | 252.7801 | 252.3068 | 256.9721 | 255.2648 | 254.8903 | 255.6355 | 253.5096 | 254.5253 | 252.7785 | 252.8513 | 253.6246 | 254.2038 | 254.2623 | 253.9183 | 256.7501 | 257.7773 | 254.4604 | 253.5835 | 253.7932 | 230.9585 | 230.0722 | 230.391 | 59.794 | 59.6766 | 59.3078 | 255.791 | 256.2965 | 254.5574 | 254.4336 | 254.1602 | 253.5396 | 256.361 | 256.8544 | 254.819 | 230.0892 | 229.2124 | 229.5441 | 59.4338 | 59.6337 | 58.9141 | 56.8184 | 56.3691 | 57.0827 | 52.5802 | 52.7512 | 52.6716 | 19.7068 | 19.8131 | 19.7217 | 20.5707 | 21.0419 | 20.5815 | 118.9043 | 119.7305 | 118.8477 | 129.1187 | 127.9567 | 128.3392 | 253.8509 | 250.6833 | 252.5093 | 255.214 | 253.5668 | 252.1986 | 252.9578 | 251.668 | 253.2047 | 228.8341 | 228.8026 | 227.0325 | 59.0824 | 59.7982 | 59.0778 | 254.5256 | 257.9491 | 253.7417 | 258.0413 | 258.8129 | 256.5197
390 | Test Purpose |  | 54.5984 | 53.4998 | 53.9177 | 49.8688 | 51.0141 | 49.7902 | 47.1441 | 47.2166 | 47.3454 | 45.4913 | 44.7582 | 44.4105 | 42.458 | 43.3095 | 43.2709 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.6277 | 8.4005 | 8.5867 | 8.9056 | 8.8596 | 9.0424 | 9.672 | 9.2895 | 9.0317 | 9.2175 | 9.3556 | 8.9364 | 9.0197 | 9.1933 | 9.2216 | 18.2641 | 17.7547 | 17.872 | 17.7807 | 19.873 | 19.9754 | 20.1352 | 39.1514 | 40.1416 | 39.7926 | 44.0763 | 43.8982 | 45.2649 | 44.9859 | 45.1657 | 45.2348 | 45.3027 | 45.7837 | 45.6128 | 19.032 | 19.0082 | 19.4554 | 20.7812 | 20.7471 | 21.0164 | 9.373 | 9.7882 | 9.2703 | 8.7169 | 8.6712 | 8.6908 | 8.621 | 8.7384 | 8.7546 | 0 | 0 | 0 | 0 | 0 | 0 | 8.7283 | 9.1502 | 8.7481 | 9.3462 | 9.5597 | 9.3716 | 9.3689 | 9.3576 | 9.4977 | 19.262 | 19.1504 | 19.422 | 20.5461 | 20.9097 | 20.8459 | 20.8441 | 39.989 | 39.5525 | 40.7667 | 39.965 | 40.633 | 39.5423 | 40.3588 | 40.2756 | 46.741 | 46.8097 | 46.0019 | 45.543 | 45.9009 | 46.9203 | 45.3846 | 46.3708 | 45.1479 | 44.8417 | 45.9216 | 45.3388 | 18.289 | 18.4269 | 17.9298 | 17.98 | 18.4419 | 18.6363 | 8.4253 | 8.4605 | 8.4842 | 0 | 0 | 0 | 0 | 0 | 20.7955 | 21.0143 | 20.7339 | 9.4574 | 9.7351 | 9.3871 | 9.5857 | 9.4023 | 9.1477 | 9.2421 | 9.1221 | 9.7599 | 9.5876 | 0 | 0 | 0 | 0 | 39.2855 | 40.4378 | 40.4877 | 40.2466 | 44.1523 | 45.271 | 46.1537 | 44.3946 | 45.5925 | 44.3982 | 44.7737 | 45.8883 | 44.7436 | 44.8728 | 44.7922 | 44.2288 | 44.288 | 44.5947 | 43.5784 | 44.7273 | 45.4465 | 44.1584 | 46.6933 | 46.2236 | 45.2605 | 44.9771 | 45.2928 | 39.215 | 40.3518 | 39.2882 | 9.052 | 9.2405 | 9.1707 | 46.0303 | 45.7782 | 45.591 | 45.2921 | 45.3932 | 45.7169 | 45.5365 | 45.8717 | 45.4621 | 39.1769 | 39.9022 | 39.2148 | 9.1655 | 9.1474 | 9.5534 | 9.3823 | 9.3415 | 9.1479 | 8.738 | 8.4077 | 8.4628 | 0 | 0 | 0 | 0 | 0 | 0 | 18.3492 | 19.1747 | 19.3451 | 20.4093 | 20.3158 | 20.4708 | 44.2223 | 43.5126 | 43.3465 | 44.7584 | 44.1745 | 43.6071 | 44.7455 | 44.0581 | 43.9624 | 38.9926 | 38.9886 | 38.0414 | 9.3208 | 9.4915 | 9.5044 | 45.2133 | 46.0739 | 44.9993 | 45.0093 | 45.4746 | 44.481
391 | Refrigerant |  | 0.983 | 0.98353 | 0.98329 | 0.98388 | 0.98323 | 0.98377 | 0.98408 | 0.98396 | 0.98403 | 0.98422 | 0.98439 | 0.98468 | 0.9851 | 0.98439 | 0.98426 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.98654 | 0.98739 | 0.98659 | 0.98698 | 0.98727 | 0.98656 | 0.98671 | 0.98778 | 0.98852 | 0.98688 | 0.98644 | 0.98797 | 0.98866 | 0.98816 | 0.98819 | 0.98774 | 0.98838 | 0.98839 | 0.98861 | 0.98787 | 0.98767 | 0.98741 | 0.98564 | 0.98517 | 0.98528 | 0.98526 | 0.9854 | 0.98461 | 0.98472 | 0.98457 | 0.98451 | 0.98413 | 0.98383 | 0.98422 | 0.98755 | 0.98744 | 0.98699 | 0.98699 | 0.98712 | 0.9867 | 0.98768 | 0.98686 | 0.98799 | 0.9873 | 0.98733 | 0.98751 | 0.98775 | 0.98724 | 0.98721 | 1 | 1 | 1 | 1 | 1 | 1 | 0.98655 | 0.98532 | 0.98654 | 0.98696 | 0.98601 | 0.98688 | 0.98784 | 0.98756 | 0.98743 | 0.98783 | 0.98774 | 0.98748 | 0.98748 | 0.98699 | 0.98715 | 0.98667 | 0.9852 | 0.98551 | 0.98462 | 0.98521 | 0.98478 | 0.98558 | 0.9848 | 0.98503 | 0.98369 | 0.9837 | 0.98407 | 0.98406 | 0.98416 | 0.98374 | 0.98414 | 0.98354 | 0.98404 | 0.98406 | 0.98393 | 0.98405 | 0.98781 | 0.98767 | 0.98838 | 0.98855 | 0.988 | 0.98771 | 0.98723 | 0.98696 | 0.98691 | 1 | 1 | 1 | 1 | 1 | 0.98669 | 0.98647 | 0.98684 | 0.98596 | 0.98538 | 0.98673 | 0.98612 | 0.9877 | 0.98836 | 0.98796 | 0.98857 | 0.98722 | 0.98763 | 1 | 1 | 1 | 1 | 0.98532 | 0.98452 | 0.98438 | 0.9845 | 0.98478 | 0.98406 | 0.98362 | 0.98435 | 0.9836 | 0.9844 | 0.9847 | 0.98371 | 0.98447 | 0.98447 | 0.98427 | 0.98479 | 0.98453 | 0.98432 | 0.98513 | 0.9844 | 0.9839 | 0.98476 | 0.98332 | 0.98379 | 0.98405 | 0.98415 | 0.98395 | 0.98548 | 0.9845 | 0.98535 | 0.98847 | 0.98794 | 0.98797 | 0.98367 | 0.98392 | 0.98383 | 0.98403 | 0.98392 | 0.98361 | 0.9841 | 0.98392 | 0.98396 | 0.9854 | 0.98473 | 0.9853 | 0.98804 | 0.98816 | 0.98677 | 0.98627 | 0.98617 | 0.98708 | 0.9861 | 0.98722 | 0.98701 | 1 | 1 | 1 | 1 | 1 | 1 | 0.98802 | 0.98709 | 0.98666 | 0.98743 | 0.98732 | 0.9872 | 0.98471 | 0.98482 | 0.98516 | 0.9845 | 0.98471 | 0.98494 | 0.98423 | 0.98456 | 0.98481 | 0.98538 | 0.98537 | 0.98586 | 0.98748 | 0.98732 | 0.98697 | 0.9841 | 0.98392 | 0.98415 | 0.98467 | 0.98444 | 0.98485
392 | Flowmeter Choice |  | 162756 | 162744 | 162729 | 162584 | 162571 | 162541 | 162455 | 162434 | 162420 | 162313 | 162298 | 162285 | 162185 | 162182 | 162179 | 161945 | 161944 | 161942 | 161937 | 161936 | 161935 | 161776 | 161774 | 161773 | 161770 | 161769 | 161768 | 161724 | 161721 | 161717 | 161714 | 161711 | 161708 | 161692 | 161688 | 161686 | 161666 | 161661 | 161649 | 161636 | 161632 | 161629 | 161573 | 161569 | 161560 | 161546 | 161509 | 161501 | 161493 | 161366 | 161354 | 161318 | 161184 | 161164 | 161123 | 161035 | 161022 | 161008 | 160967 | 160945 | 160932 | 160727 | 160713 | 160705 | 160664 | 160657 | 160651 | 160567 | 160565 | 160561 | 160551 | 160549 | 160546 | 160541 | 160537 | 160535 | 160495 | 160494 | 160493 | 160479 | 160476 | 160472 | 160442 | 160439 | 160436 | 160416 | 160410 | 160407 | 160392 | 160389 | 160386 | 160315 | 160309 | 160304 | 160230 | 160223 | 160216 | 160105 | 160058 | 160054 | 160049 | 160012 | 160009 | 159997 | 159981 | 159948 | 159701 | 159688 | 159671 | 159574 | 159562 | 159549 | 159520 | 159502 | 159489 | 159281 | 159264 | 159251 | 159039 | 159035 | 159028 | 158982 | 158977 | 158972 | 158846 | 158843 | 158841 | 158774 | 158773 | 158772 | 158768 | 158766 | 158734 | 158727 | 158719 | 158603 | 158601 | 158599 | 158548 | 158527 | 158524 | 158521 | 158441 | 158437 | 158434 | 158369 | 158365 | 158364 | 158363 | 158325 | 158306 | 158295 | 158286 | 158108 | 158077 | 158062 | 157926 | 157906 | 157845 | 157122 | 157116 | 157091 | 157075 | 157040 | 157015 | 156992 | 156964 | 155590 | 155576 | 155564 | 155471 | 155458 | 155444 | 155425 | 155413 | 155401 | 155343 | 155322 | 155309 | 155111 | 155108 | 155104 | 154995 | 154972 | 154952 | 154859 | 154843 | 154831 | 154544 | 154528 | 154515 | 154480 | 154463 | 154448 | 154143 | 154141 | 154136 | 154045 | 154041 | 154034 | 154005 | 154001 | 153997 | 153953 | 153951 | 153950 | 153948 | 153945 | 153944 | 153876 | 153868 | 153860 | 153803 | 153796 | 153789 | 153498 | 153461 | 153439 | 153386 | 153374 | 153357 | 153320 | 153303 | 153283 | 152914 | 152907 | 152895 | 152678 | 152673 | 152670 | 152510 | 152493 | 152474 | 152425 | 152407 | 152388
393 | Logging Interval T1 |  | 53865 | 53863 | 53860 | 53833 | 53831 | 53825 | 53809 | 53806 | 53803 | 53784 | 53781 | 53779 | 53761 | 53760 | 53760 | 53721 | 53721 | 53721 | 53721 | 53721 | 53721 | 53705 | 53705 | 53705 | 53705 | 53705 | 53705 | 53705 | 53704 | 53704 | 53703 | 53703 | 53702 | 53700 | 53699 | 53699 | 53695 | 53695 | 53693 | 53691 | 53690 | 53690 | 53681 | 53681 | 53679 | 53677 | 53671 | 53670 | 53669 | 53648 | 53646 | 53640 | 53617 | 53613 | 53606 | 53590 | 53588 | 53585 | 53578 | 53574 | 53572 | 53537 | 53535 | 53534 | 53527 | 53526 | 53525 | 53512 | 53511 | 53511 | 53509 | 53509 | 53508 | 53507 | 53507 | 53506 | 53502 | 53502 | 53502 | 53502 | 53502 | 53502 | 53502 | 53501 | 53501 | 53497 | 53497 | 53496 | 53493 | 53493 | 53493 | 53482 | 53481 | 53480 | 53468 | 53467 | 53466 | 53448 | 53440 | 53440 | 53439 | 53432 | 53432 | 53430 | 53427 | 53421 | 53378 | 53376 | 53373 | 53355 | 53353 | 53351 | 53346 | 53342 | 53340 | 53305 | 53302 | 53299 | 53262 | 53261 | 53260 | 53253 | 53252 | 53251 | 53232 | 53231 | 53231 | 53222 | 53222 | 53222 | 53222 | 53222 | 53221 | 53220 | 53219 | 53200 | 53200 | 53199 | 53191 | 53187 | 53187 | 53186 | 53173 | 53173 | 53172 | 53162 | 53162 | 53162 | 53162 | 53161 | 53157 | 53155 | 53154 | 53123 | 53117 | 53114 | 53090 | 53086 | 53075 | 52950 | 52949 | 52945 | 52942 | 52936 | 52931 | 52927 | 52922 | 52683 | 52681 | 52678 | 52662 | 52660 | 52657 | 52654 | 52651 | 52649 | 52639 | 52635 | 52633 | 52599 | 52599 | 52598 | 52582 | 52577 | 52574 | 52557 | 52554 | 52552 | 52501 | 52498 | 52496 | 52490 | 52487 | 52484 | 52432 | 52431 | 52431 | 52417 | 52416 | 52415 | 52410 | 52409 | 52409 | 52402 | 52402 | 52402 | 52402 | 52402 | 52402 | 52396 | 52394 | 52393 | 52384 | 52383 | 52382 | 52336 | 52330 | 52326 | 52317 | 52314 | 52312 | 52305 | 52302 | 52298 | 52235 | 52234 | 52232 | 52196 | 52195 | 52194 | 52170 | 52167 | 52164 | 52155 | 52152 | 52148
394 | Logging Interval T2 |  | 50.0885 | 50.0689 | 49.9778 | 50.0532 | 50.0655 | 50.1449 | 50.0653 | 50.0799 | 50.1477 | 50.132 | 50.1583 | 50.0952 | 50.069 | 50.0577 | 50.048 | 50.0014 | 49.982 | 49.9151 | 49.9474 | 49.9128 | 49.9202 | 49.9227 | 49.9126 | 49.9881 | 49.9227 | 50.0179 | 50.0688 | 50.1475 | 50.0862 | 49.9509 | 49.9418 | 49.9821 | 50.0176 | 50.061 | 50.0892 | 50.068 | 49.958 | 50.0565 | 49.9117 | 49.9975 | 49.9761 | 50.0889 | 50.0163 | 49.9434 | 50.0869 | 50.0936 | 50.0265 | 50.0185 | 50.0407 | 49.865 | 49.9038 | 49.9625 | 50.0907 | 50.0122 | 49.8577 | 50.0182 | 50.0274 | 49.9475 | 50.0417 | 50.1261 | 50.1284 | 49.945 | 49.9392 | 49.9397 | 49.9102 | 50.0631 | 50.0327 | 50.0306 | 49.9723 | 49.9556 | 50.0876 | 49.9798 | 50.1305 | 50.0809 | 50.0327 | 49.9785 | 49.9705 | 49.9765 | 49.955 | 49.9433 | 49.9928 | 50.0868 | 49.926 | 49.9431 | 49.9604 | 49.8776 | 49.9252 | 49.9871 | 50.0405 | 50.0211 | 50.0631 | 50.0717 | 50.0511 | 50.0466 | 49.9605 | 49.9962 | 49.9993 | 50.0326 | 50.125 | 50.1317 | 50.0952 | 50.0735 | 50.0325 | 50.029 | 49.9764 | 50.0032 | 50.0087 | 50.0111 | 50.0476 | 49.9611 | 50.0178 | 50.0507 | 50.0536 | 49.9935 | 50.004 | 49.9297 | 50.0601 | 50.024 | 50.0575 | 50.0123 | 50.1775 | 50.108 | 50.0719 | 50.073 | 49.9657 | 49.961 | 50.0151 | 49.9395 | 49.9556 | 49.9676 | 49.948 | 49.8984 | 49.8999 | 49.8783 | 49.8943 | 50.0758 | 50.0657 | 50.0702 | 49.9924 | 50.0805 | 50.0579 | 50.0693 | 49.9713 | 49.9505 | 49.915 | 49.9437 | 49.9621 | 49.98 | 49.9866 | 50.112 | 50.1316 | 50.1773 | 50.1568 | 50.1493 | 50.1049 | 49.9818 | 49.9969 | 49.998 | 50.0716 | 49.9889 | 49.9143 | 49.9113 | 49.9202 | 49.942 | 49.9816 | 49.9231 | 50.0247 | 49.9589 | 50.0579 | 49.9014 | 50.1222 | 50.0678 | 50.1 | 50.087 | 50.0778 | 50.1147 | 49.9431 | 49.9257 | 49.9474 | 50.0748 | 50.0952 | 50.0442 | 49.9403 | 49.9936 | 49.981 | 50.0087 | 49.9202 | 49.926 | 50.0725 | 50.0518 | 50.0421 | 50.041 | 50.0088 | 50.0214 | 50.1845 | 50.1506 | 50.0839 | 50.0539 | 50.0693 | 50.0828 | 50.0186 | 50.1223 | 49.985 | 50.0648 | 50.0385 | 50.0368 | 49.9596 | 49.9304 | 49.9603 | 49.9857 | 49.9625 | 49.9219 | 49.9219 | 49.9521 | 49.8836 | 49.9773 | 50.0042 | 50.0267 | 49.9339 | 50.0298 | 49.9564 | 49.9121 | 49.9334 | 50.0116 | 49.9703 | 49.982 | 49.9802 | 49.948 | 50.0155 | 49.9794 | 50.0346 | 50.0662 | 50.0362 | 49.9878 | 50.0324 | 50.0491
395 | V L1-2 |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
396 | V L2-3 |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
397 | V L3-1 |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
398 | V1 |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
399 | V2 |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
400 | V3 |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
401 | A1 |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
402 | A2 |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
403 | A3 |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
404 | kW Sum |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
405 | kVA Sum |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
406 | kVAR Sum |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
407 | PF Average |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
408 | kWHr |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
409 | kVAHr |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
410 | Hz |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
411 | T1 |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
412 | T2 |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
413 | T3 |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
414 | T4 |  | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1
415 | T5 |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
416 | T6 |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
417 | T7 |  | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2
418 | T8 |  | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2
419 | T9 |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
420 | T10 |  | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1 | 17.1
421 | T11 |  | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2
422 | T12 |  | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2
423 | T13 |  | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2 | 17.2
424 | T14 |  | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7 | -3276.7
425 | T15 |  | 120.01 | 120 | 120.02 | 120.01 | 120 | 120.01 | 120 | 120 | 120 | 119.99 | 120 | 120.01 | 120 | 120.04 | 120 | 19.006 | 18.999 | 19.005 | 20.004 | 19.999 | 20.01 | 19.001 | 18.996 | 19.003 | 20.005 | 20.001 | 20 | 39.997 | 40.002 | 40.004 | 40.008 | 40.001 | 40.004 | 43.005 | 43.007 | 43.001 | 43.001 | 43.001 | 43.002 | 44.998 | 45.002 | 45 | 68.991 | 69.01 | 69.002 | 69.997 | 74.998 | 75.002 | 75.007 | 110 | 110 | 109.99 | 119.99 | 120.01 | 119.99 | 120 | 120 | 120 | 120 | 119.99 | 120 | 69.993 | 69.994 | 70.005 | 74.997 | 74.996 | 75.004 | 45.003 | 45.005 | 44.995 | 40.006 | 39.997 | 40.002 | 40.001 | 40.006 | 39.999 | 18.997 | 18.997 | 19.005 | 19.992 | 19.993 | 20.009 | 40.004 | 39.998 | 39.999 | 42.993 | 43.003 | 43.004 | 43.007 | 42.997 | 42.998 | 70.998 | 70.993 | 70.998 | 74.999 | 74.999 | 74.998 | 74 | 110 | 110 | 110 | 110 | 109.99 | 110 | 110 | 110.01 | 120 | 120 | 120.01 | 120.01 | 120 | 120.02 | 120 | 120 | 119.99 | 120.01 | 120 | 120 | 69.002 | 68.984 | 68.991 | 69.999 | 69.989 | 70 | 40.004 | 40.002 | 40.001 | 18.997 | 19 | 18.995 | 20.01 | 20 | 75 | 75.002 | 74.99 | 43.004 | 43.001 | 43.003 | 42.992 | 45.002 | 44.999 | 45.005 | 45 | 44.99 | 44.995 | 20.008 | 20.006 | 19.997 | 19.996 | 110 | 110 | 110.02 | 110.02 | 120 | 120 | 120 | 119.99 | 120 | 120 | 119.99 | 120.01 | 119.98 | 119.99 | 119.99 | 120 | 120 | 120 | 120 | 119.99 | 120.01 | 120.01 | 120 | 120 | 120.01 | 119.99 | 119.99 | 109.98 | 110 | 110 | 45.005 | 45.001 | 44.994 | 119.99 | 120.01 | 120.01 | 120.01 | 120 | 120 | 120 | 120 | 120 | 110.01 | 110 | 110 | 44.998 | 45.006 | 45.002 | 43.001 | 43 | 43.001 | 40 | 40.003 | 39.993 | 18.996 | 18.999 | 19.004 | 19.996 | 19.998 | 20.01 | 71 | 70.999 | 71 | 76.007 | 75.996 | 76.004 | 119.99 | 120.01 | 120 | 120.01 | 120 | 120.01 | 120 | 120 | 119.99 | 110.01 | 110.01 | 110 | 44.999 | 45.002 | 44.998 | 119.99 | 120 | 119.98 | 119.99 | 120 | 119.99
426 | T16 |  | 418.1 | 418.01 | 416.78 | 417.58 | 417.31 | 417.6 | 419.97 | 418.69 | 419.93 | 419.32 | 418.69 | 418.09 | 417.76 | 417.57 | 417.97 | 362.64 | 362.9 | 362.88 | 363.88 | 363.98 | 363.43 | 363.11 | 364.02 | 364.28 | 364.71 | 365.89 | 365.85 | 378.47 | 379 | 378.05 | 377.47 | 377.47 | 377.16 | 380.08 | 379.59 | 379.65 | 378.86 | 378.87 | 377.85 | 379.13 | 378.69 | 379.61 | 394.19 | 393.62 | 394.26 | 394.08 | 396.93 | 397.78 | 397.37 | 414.32 | 414.91 | 414.39 | 417.4 | 416.85 | 417.89 | 416.55 | 416.9 | 416.3 | 425.87 | 416.04 | 416.34 | 397.07 | 396.68 | 395.72 | 399.43 | 402.02 | 402.04 | 380.08 | 380.06 | 379.53 | 375.37 | 375.14 | 375.2 | 375.34 | 374.29 | 374.84 | 366.73 | 366.64 | 366.36 | 366.48 | 367.47 | 368.28 | 375.57 | 375.42 | 375.81 | 380.71 | 380.98 | 380.91 | 380.24 | 380.24 | 380.39 | 398.54 | 398.69 | 397.98 | 399.55 | 399.79 | 399.18 | 395.85 | 415.28 | 415.6 | 415.22 | 416.74 | 416.63 | 415.52 | 415.83 | 415.04 | 416.94 | 417.68 | 418.1 | 418.5 | 418.55 | 419.62 | 420.09 | 419.13 | 418.15 | 417.29 | 421.52 | 424.77 | 395.03 | 393.65 | 396.71 | 398.4 | 397.09 | 396.85 | 375.47 | 376.16 | 376.4 | 366.38 | 365.6 | 365.15 | 366.46 | 366.47 | 401.36 | 401.08 | 401.12 | 376.8 | 377.11 | 377.5 | 376.75 | 377.54 | 377.97 | 377.59 | 375.59 | 374.73 | 374.75 | 366.14 | 366.12 | 366.03 | 366.07 | 421.89 | 421.88 | 421.83 | 421.51 | 422.29 | 421.1 | 420.51 | 418.92 | 418.82 | 417.74 | 422.34 | 422.44 | 423.18 | 422.41 | 422.82 | 422.76 | 421.91 | 422.92 | 418 | 419.15 | 417.2 | 416.53 | 416.21 | 416.94 | 417.33 | 416.71 | 416.35 | 416.12 | 413.41 | 415.12 | 379.43 | 380.31 | 379.95 | 419.52 | 420.04 | 416.83 | 422.87 | 421.94 | 421.77 | 419.56 | 419.21 | 418.83 | 417.78 | 417.92 | 417.91 | 382.22 | 381.59 | 381.71 | 378.83 | 378.27 | 378.63 | 375.5 | 376.01 | 376.75 | 373.47 | 372.14 | 373.17 | 374.04 | 373.48 | 373.59 | 399.19 | 397.74 | 398.02 | 400 | 399.62 | 399.92 | 417.86 | 419.37 | 418.5 | 417.91 | 418.99 | 418.64 | 414.64 | 414.85 | 414.87 | 422.5 | 422.98 | 421.71 | 382.83 | 383.44 | 383.11 | 417.99 | 418.84 | 419.4 | 418.92 | 418.72 | 419.58
427 | T17 |  | 418.46 | 418.46 | 417.23 | 418.02 | 417.76 | 418.03 | 420.3 | 419.14 | 420.4 | 419.68 | 419.11 | 418.43 | 418.03 | 417.93 | 418.26 | 362.37 | 362.52 | 362.62 | 363.62 | 363.78 | 363.14 | 362.95 | 363.67 | 364.1 | 364.39 | 365.77 | 365.69 | 378.81 | 379.3 | 378.35 | 377.86 | 377.81 | 377.52 | 380.42 | 379.89 | 380.05 | 379.15 | 379.15 | 378.19 | 379.46 | 379.02 | 379.89 | 394.71 | 394.15 | 394.74 | 394.6 | 397.26 | 398.15 | 397.73 | 414.49 | 415.09 | 414.6 | 417.84 | 417.19 | 418.27 | 416.86 | 417.25 | 416.7 | 426.25 | 416.4 | 416.73 | 397.6 | 397.21 | 396.3 | 399.92 | 402.44 | 402.51 | 380.42 | 380.44 | 379.93 | 375.65 | 375.42 | 375.46 | 375.66 | 374.57 | 375.15 | 366.47 | 366.45 | 366.09 | 366.34 | 367.21 | 367.95 | 375.79 | 375.69 | 376.2 | 381.05 | 381.33 | 381.23 | 380.65 | 380.55 | 380.9 | 399.05 | 399.19 | 398.49 | 399.99 | 400.33 | 399.65 | 396.35 | 415.5 | 415.82 | 415.41 | 416.94 | 416.84 | 415.71 | 416.02 | 415.25 | 417.43 | 417.96 | 418.53 | 418.86 | 418.95 | 420.09 | 420.51 | 419.43 | 418.45 | 417.75 | 421.92 | 425.17 | 395.63 | 394.22 | 397.32 | 398.98 | 397.66 | 397.48 | 375.86 | 376.42 | 376.77 | 366.13 | 365.46 | 364.91 | 366.28 | 366.26 | 401.84 | 401.62 | 401.54 | 377.17 | 377.52 | 377.88 | 377.11 | 378 | 378.4 | 378.03 | 376.02 | 375.14 | 375.18 | 365.94 | 365.93 | 365.85 | 365.9 | 422.09 | 422.11 | 422.07 | 421.69 | 422.61 | 421.52 | 420.99 | 419.41 | 419.26 | 418.13 | 422.81 | 422.86 | 423.64 | 422.8 | 423.32 | 423.14 | 422.32 | 423.29 | 418.41 | 419.61 | 417.65 | 416.89 | 416.63 | 417.38 | 417.72 | 417.17 | 416.77 | 416.42 | 413.68 | 415.39 | 379.83 | 380.74 | 380.4 | 419.92 | 420.46 | 417.29 | 423.31 | 422.25 | 422.26 | 420.03 | 419.59 | 419.18 | 417.97 | 418.1 | 418.11 | 382.66 | 381.98 | 382.12 | 379.26 | 378.68 | 379 | 375.8 | 376.31 | 377.14 | 373.14 | 372.03 | 373.06 | 373.88 | 373.22 | 373.38 | 399.79 | 398.31 | 398.54 | 400.45 | 400.13 | 400.45 | 418.21 | 419.76 | 418.8 | 418.31 | 419.38 | 419.02 | 415.04 | 415.14 | 415.19 | 422.63 | 423.08 | 421.86 | 383.21 | 383.77 | 383.47 | 418.36 | 419.19 | 419.74 | 419.29 | 418.99 | 419.81
428 | T18 |  | 418.25 | 418.21 | 416.99 | 417.77 | 417.46 | 417.8 | 420.11 | 418.83 | 420.09 | 419.44 | 418.86 | 418.19 | 417.82 | 417.68 | 418.07 | 363.05 | 363.39 | 363.45 | 364.42 | 364.36 | 363.78 | 363.63 | 364.44 | 364.66 | 365.18 | 366.45 | 366.4 | 379.18 | 379.6 | 378.57 | 378.1 | 378.04 | 377.76 | 380.59 | 380.1 | 380.16 | 379.36 | 379.41 | 378.46 | 379.57 | 379.21 | 380.09 | 394.17 | 393.63 | 394.25 | 394.1 | 396.82 | 397.69 | 397.26 | 414.26 | 414.82 | 414.3 | 417.61 | 416.98 | 418.08 | 416.67 | 417.05 | 416.45 | 426.03 | 416.17 | 416.5 | 397.04 | 396.69 | 395.73 | 399.34 | 401.91 | 401.94 | 380.51 | 380.62 | 380.09 | 375.9 | 375.73 | 375.81 | 375.89 | 374.88 | 375.4 | 367.22 | 367.14 | 366.8 | 367.1 | 367.96 | 368.6 | 376.17 | 376 | 376.47 | 381.27 | 381.47 | 381.47 | 380.86 | 380.87 | 381.03 | 398.52 | 398.66 | 397.94 | 399.46 | 399.83 | 399.11 | 395.71 | 415.22 | 415.6 | 415.15 | 416.76 | 416.58 | 415.48 | 415.76 | 415 | 417.17 | 417.84 | 418.31 | 418.63 | 418.62 | 419.78 | 420.23 | 419.29 | 418.26 | 417.48 | 421.71 | 424.98 | 395.06 | 393.77 | 396.78 | 398.4 | 397.13 | 396.88 | 376.13 | 376.76 | 377.03 | 366.82 | 366.12 | 365.6 | 367 | 366.94 | 401.37 | 401.07 | 401.09 | 377.27 | 377.57 | 378.04 | 377.21 | 378.11 | 378.52 | 378.13 | 376.17 | 375.36 | 375.29 | 366.65 | 366.6 | 366.5 | 366.61 | 421.88 | 421.93 | 421.88 | 421.51 | 422.42 | 421.33 | 420.69 | 419.18 | 419.01 | 417.89 | 422.52 | 422.61 | 423.31 | 422.61 | 423.02 | 422.93 | 422.13 | 423.06 | 418.18 | 419.39 | 417.37 | 416.67 | 416.34 | 417.06 | 417.51 | 416.93 | 416.6 | 416.15 | 413.42 | 415.11 | 380.02 | 380.81 | 380.45 | 419.61 | 420.22 | 416.96 | 422.98 | 422.04 | 421.93 | 419.7 | 419.32 | 418.89 | 417.7 | 417.82 | 417.85 | 382.67 | 382.11 | 382.1 | 379.36 | 378.86 | 379.06 | 376.04 | 376.59 | 377.35 | 373.93 | 372.64 | 373.77 | 374.48 | 373.86 | 374.03 | 399.16 | 397.68 | 397.94 | 399.82 | 399.54 | 399.84 | 417.96 | 419.48 | 418.61 | 418.08 | 419.1 | 418.84 | 414.81 | 414.97 | 415.07 | 422.51 | 422.97 | 421.69 | 383.28 | 383.89 | 383.56 | 418.22 | 418.94 | 419.47 | 419.07 | 418.89 | 419.65
429 | T19 |  | 241.49 | 241.46 | 240.75 | 241.21 | 241.05 | 241.22 | 242.56 | 241.85 | 242.57 | 242.19 | 241.84 | 241.47 | 241.26 | 241.18 | 241.39 | 209.4 | 209.54 | 209.57 | 210.14 | 210.18 | 209.84 | 209.71 | 210.18 | 210.35 | 210.59 | 211.33 | 211.3 | 218.71 | 218.99 | 218.42 | 218.13 | 218.11 | 217.94 | 219.6 | 219.31 | 219.37 | 218.89 | 218.9 | 218.34 | 219.04 | 218.8 | 219.31 | 227.68 | 227.36 | 227.72 | 227.63 | 229.21 | 229.71 | 229.47 | 239.23 | 239.57 | 239.27 | 241.11 | 240.76 | 241.38 | 240.58 | 240.79 | 240.45 | 245.98 | 240.3 | 240.48 | 229.35 | 229.13 | 228.58 | 230.69 | 232.17 | 232.19 | 219.59 | 219.61 | 219.31 | 216.88 | 216.76 | 216.79 | 216.87 | 216.26 | 216.58 | 211.78 | 211.74 | 211.55 | 211.68 | 212.2 | 212.62 | 216.99 | 216.91 | 217.18 | 219.98 | 220.12 | 220.09 | 219.73 | 219.71 | 219.84 | 230.19 | 230.27 | 229.86 | 230.75 | 230.93 | 230.54 | 228.61 | 239.79 | 239.99 | 239.75 | 240.65 | 240.57 | 239.93 | 240.1 | 239.66 | 240.86 | 241.23 | 241.51 | 241.72 | 241.74 | 242.39 | 242.65 | 242.07 | 241.5 | 241.05 | 243.48 | 245.36 | 228.19 | 227.41 | 229.17 | 230.13 | 229.38 | 229.25 | 216.98 | 217.34 | 217.51 | 211.57 | 211.15 | 210.86 | 211.64 | 211.63 | 231.82 | 231.66 | 231.66 | 217.71 | 217.89 | 218.13 | 217.67 | 218.17 | 218.41 | 218.19 | 217.04 | 216.55 | 216.55 | 211.45 | 211.43 | 211.38 | 211.42 | 243.61 | 243.63 | 243.6 | 243.39 | 243.9 | 243.25 | 242.91 | 242.01 | 241.93 | 241.29 | 243.96 | 244.01 | 244.44 | 243.99 | 244.25 | 244.19 | 243.71 | 244.27 | 241.44 | 242.13 | 240.99 | 240.58 | 240.4 | 240.83 | 241.06 | 240.72 | 240.51 | 240.31 | 238.74 | 239.72 | 219.25 | 219.75 | 219.55 | 242.3 | 242.63 | 240.77 | 244.25 | 243.69 | 243.64 | 242.35 | 242.12 | 241.89 | 241.23 | 241.3 | 241.31 | 220.85 | 220.49 | 220.53 | 218.9 | 218.59 | 218.76 | 216.96 | 217.26 | 217.71 | 215.65 | 214.93 | 215.54 | 216.01 | 215.65 | 215.74 | 230.58 | 229.73 | 229.88 | 230.99 | 230.8 | 230.98 | 241.34 | 242.22 | 241.7 | 241.39 | 242 | 241.81 | 239.5 | 239.59 | 239.63 | 243.96 | 244.23 | 243.5 | 221.19 | 221.53 | 221.34 | 241.44 | 241.9 | 242.22 | 241.97 | 241.83 | 242.3
430 | T20 |  | 495.45 | 494.4 | 493.9 | 468.36 | 468.92 | 468.01 | 445.81 | 446.1 | 444.95 | 429.15 | 428.56 | 430.1 | 415.39 | 414.85 | 414.68 | 204.84 | 205.02 | 205.25 | 206.31 | 205.63 | 204.34 | 205.39 | 205.22 | 205.12 | 206.44 | 205.6 | 205.03 | 256.39 | 256.26 | 256.49 | 266.35 | 266.66 | 266.79 | 267.59 | 268.71 | 267.66 | 259.2 | 259.38 | 259.5 | 259.48 | 261.69 | 260.8 | 333.18 | 332.14 | 332.79 | 332.41 | 336.67 | 336.68 | 336.05 | 424.18 | 423.61 | 424.65 | 435.74 | 435.3 | 434.16 | 436.52 | 435.4 | 435.83 | 429.04 | 431.31 | 432.27 | 337.85 | 336.88 | 337.2 | 340.71 | 341.66 | 340.97 | 260.48 | 261.61 | 260.84 | 265.1 | 266.05 | 266.21 | 266.33 | 265.73 | 265.05 | 205.05 | 205.08 | 203.97 | 205.12 | 206.19 | 205.71 | 259.37 | 259.47 | 259.07 | 260.82 | 259.68 | 260.89 | 271.05 | 270.26 | 270.55 | 341.17 | 340.56 | 340.12 | 343.2 | 343.04 | 342.72 | 341.91 | 424.11 | 424.16 | 424.25 | 423.92 | 424.15 | 424.09 | 424.32 | 424.2 | 434.26 | 433.94 | 432.75 | 434.42 | 433.78 | 432.61 | 429.64 | 429.29 | 429.28 | 428.58 | 427.98 | 426.52 | 334.85 | 334.79 | 335.29 | 335.56 | 335.52 | 334.95 | 256.21 | 257.08 | 256.29 | 203.18 | 203.79 | 204.36 | 205.94 | 204.46 | 338.9 | 338.45 | 339.27 | 258.45 | 258.37 | 258.23 | 259.1 | 260.93 | 260.71 | 260.62 | 264.22 | 264.57 | 264.2 | 205.97 | 206.24 | 204.94 | 204.52 | 417.5 | 418.76 | 419.13 | 418.87 | 428.51 | 428.57 | 428.39 | 424.21 | 424.67 | 425.67 | 427.7 | 428.5 | 427.34 | 427.38 | 424.87 | 425.77 | 425.16 | 424.05 | 428.55 | 428.17 | 428.79 | 432.89 | 431.71 | 431.26 | 426.76 | 425.87 | 426.58 | 422.14 | 419.32 | 420.45 | 261.03 | 260.58 | 259.01 | 429.05 | 428.58 | 429.19 | 426.03 | 426.09 | 425.37 | 428.91 | 430.06 | 430.47 | 418.54 | 417.9 | 418.1 | 257.66 | 258.34 | 256.3 | 257.56 | 256.88 | 257.13 | 255.45 | 254.78 | 255.31 | 203.87 | 204.08 | 203.94 | 205.94 | 204.9 | 204.53 | 332.28 | 331.41 | 331.01 | 334.89 | 334.7 | 333.93 | 427.55 | 425.88 | 427.66 | 429.23 | 428.52 | 427.86 | 426.52 | 426.04 | 425.68 | 418.32 | 416.62 | 416.23 | 257.27 | 259.74 | 257.14 | 428.32 | 428.29 | 427.72 | 431.62 | 433.17 | 433.79
431 | T21 |  | 510.36 | 510.65 | 510.21 | 483.06 | 483.68 | 483.06 | 459.23 | 460.25 | 459.47 | 441.97 | 442.36 | 442.91 | 427.32 | 427.36 | 426.7 | 203.54 | 203.77 | 203.91 | 205.21 | 204.48 | 204.09 | 204.36 | 204.18 | 204.23 | 205.42 | 204.46 | 203.99 | 267.23 | 267.41 | 267.64 | 277.59 | 277.76 | 277.89 | 281.27 | 281.87 | 281.61 | 269.97 | 270.63 | 270.39 | 271.54 | 273.11 | 272.89 | 351.39 | 350.34 | 350.62 | 350.87 | 353.54 | 353.17 | 352.63 | 436.27 | 435.89 | 437.03 | 449.56 | 448.33 | 447.34 | 448.98 | 448.57 | 449.42 | 442.31 | 444.55 | 445.6 | 355.99 | 355.28 | 355.53 | 358.2 | 357.75 | 357.82 | 273.22 | 273.27 | 272.46 | 275.93 | 276.87 | 277.18 | 277.1 | 276.52 | 276.29 | 204.21 | 203.97 | 202.92 | 204.1 | 205.21 | 204.71 | 269.37 | 270.33 | 269.46 | 271.41 | 272.59 | 271.97 | 282.46 | 282.44 | 282.52 | 359.09 | 358.35 | 358.02 | 359.82 | 360.22 | 358.84 | 359.88 | 436.56 | 436.19 | 436.54 | 436.29 | 436.77 | 436.25 | 436.69 | 436.51 | 448.17 | 446.47 | 446.1 | 447.96 | 447.28 | 446.8 | 443.56 | 441.76 | 441.3 | 442.44 | 441.3 | 439.5 | 352.83 | 352.52 | 353.37 | 353.3 | 353.18 | 353.18 | 266.3 | 267.27 | 266.76 | 202.44 | 202.58 | 203.55 | 204.79 | 203.24 | 355.07 | 355.22 | 355.14 | 270.63 | 270.72 | 270.52 | 270.76 | 272.36 | 272.06 | 272.26 | 275.76 | 274.95 | 275.59 | 205.69 | 204.98 | 204.8 | 203.47 | 429.75 | 430.91 | 431.43 | 430.91 | 441.35 | 441.46 | 442.64 | 437.79 | 438.35 | 438.43 | 440.89 | 441.3 | 440.32 | 440.28 | 438.48 | 438.85 | 438.04 | 436.74 | 441.66 | 441.84 | 442.25 | 445.67 | 444.36 | 445.13 | 439.95 | 439.67 | 439.88 | 434.17 | 431.74 | 432.62 | 271.95 | 272.25 | 270.94 | 442.23 | 441.98 | 443.5 | 439.79 | 438.66 | 439.07 | 442.47 | 443.14 | 443.31 | 430.37 | 429.77 | 430 | 269.27 | 269.1 | 268.19 | 270.31 | 267.84 | 269.82 | 265.68 | 265.08 | 265.5 | 203.13 | 203.08 | 202.79 | 205.05 | 204.3 | 203.87 | 349.63 | 348.75 | 348.13 | 350.88 | 350.64 | 349.89 | 440.28 | 439.13 | 439.72 | 442.42 | 442.08 | 440.62 | 440.24 | 437.94 | 437.79 | 430.1 | 428.09 | 428.28 | 270.03 | 272 | 269.93 | 441.61 | 441.52 | 440.95 | 445.16 | 445.86 | 446.23
432 | T22 |  | 499.64 | 499.42 | 498.72 | 472.79 | 473.08 | 472.7 | 449.79 | 449.86 | 449.37 | 432.39 | 432.92 | 433.55 | 418.27 | 418.26 | 418.08 | 210.99 | 211.57 | 211.63 | 213.07 | 212.69 | 211.26 | 211.78 | 211.69 | 211.5 | 212.83 | 212.35 | 212.32 | 271.65 | 271.59 | 271.68 | 282.32 | 282.36 | 282.51 | 283.11 | 283.88 | 283.54 | 272.41 | 273.73 | 273.07 | 274.23 | 275.67 | 274.74 | 340.84 | 340.1 | 340.32 | 340.22 | 342.24 | 343.05 | 341.59 | 426.05 | 425.74 | 426.49 | 439.94 | 439.05 | 438.56 | 439.77 | 439.08 | 439.32 | 433.38 | 435.7 | 436.52 | 345.05 | 344.43 | 345 | 346.95 | 347.36 | 346.59 | 275.23 | 275.64 | 274.96 | 280.37 | 281.37 | 281.3 | 281.31 | 280.77 | 280.52 | 211.73 | 211.61 | 210.64 | 211.89 | 213.17 | 212.17 | 274.04 | 274.84 | 274.35 | 274.89 | 274.9 | 274.58 | 284.88 | 285.22 | 286.49 | 348.2 | 347.42 | 347.2 | 348.29 | 348.91 | 348.03 | 347.93 | 426.33 | 426.64 | 426.36 | 426.56 | 426.7 | 426.29 | 426.37 | 426.44 | 438.68 | 437.78 | 437.38 | 438.31 | 437.12 | 436.87 | 433.57 | 433.19 | 432.69 | 432.8 | 432.04 | 430.83 | 342.3 | 341.99 | 343.01 | 342.62 | 342.68 | 342.09 | 271.1 | 271.65 | 271.26 | 209.89 | 210.16 | 210.5 | 212.7 | 211.22 | 344.74 | 343.6 | 344.59 | 272.59 | 273.19 | 272.7 | 274.15 | 274.55 | 274.19 | 273.98 | 278.87 | 279.02 | 278.94 | 213.32 | 212.62 | 211.58 | 211.17 | 419.99 | 421.62 | 421.85 | 421.33 | 432.21 | 432.59 | 432.48 | 428.8 | 428.54 | 429.55 | 431.31 | 432.13 | 431.12 | 431.3 | 428.75 | 429.44 | 429.29 | 427.83 | 432.3 | 432.41 | 432.13 | 436.23 | 434.84 | 434.84 | 430.54 | 430.26 | 430.91 | 424.35 | 421.51 | 422.26 | 274.62 | 275.07 | 273.47 | 432.22 | 432.78 | 433.25 | 430.24 | 429.68 | 429.26 | 432.44 | 433.69 | 433.66 | 420.47 | 420 | 420.26 | 271.84 | 271.85 | 269.82 | 272.55 | 271.37 | 271.71 | 269.75 | 268.75 | 269.63 | 209.83 | 210.01 | 210.17 | 212.82 | 212 | 211.33 | 338.96 | 337.81 | 337.36 | 339.56 | 339.77 | 339.06 | 430.53 | 429.25 | 430.68 | 432.72 | 432.05 | 431.48 | 430.51 | 428.85 | 429.64 | 420.68 | 419.1 | 418.81 | 271.05 | 272.66 | 270.76 | 432.62 | 431.54 | 431.19 | 435.33 | 436.85 | 436.39
433 | T23 |  | 501.82 | 501.49 | 500.94 | 474.74 | 475.23 | 474.59 | 451.61 | 452.07 | 451.26 | 434.5 | 434.61 | 435.52 | 420.33 | 420.16 | 419.82 | 206.45 | 206.79 | 206.93 | 208.2 | 207.6 | 206.56 | 207.18 | 207.03 | 206.95 | 208.23 | 207.47 | 207.11 | 265.09 | 265.09 | 265.27 | 275.42 | 275.59 | 275.73 | 277.32 | 278.16 | 277.61 | 267.19 | 267.91 | 267.65 | 268.42 | 270.16 | 269.48 | 341.8 | 340.86 | 341.24 | 341.17 | 344.15 | 344.3 | 343.42 | 428.83 | 428.42 | 429.39 | 441.75 | 440.89 | 440.02 | 441.76 | 441.02 | 441.52 | 434.91 | 437.18 | 438.13 | 346.3 | 345.53 | 345.91 | 348.62 | 348.93 | 348.46 | 269.64 | 270.17 | 269.42 | 273.8 | 274.77 | 274.9 | 274.91 | 274.34 | 273.95 | 207 | 206.89 | 205.84 | 207.04 | 208.19 | 207.53 | 267.59 | 268.21 | 267.63 | 269.04 | 269.06 | 269.15 | 279.46 | 279.31 | 279.86 | 349.49 | 348.77 | 348.45 | 350.43 | 350.72 | 349.87 | 349.9 | 429 | 429 | 429.05 | 428.92 | 429.21 | 428.88 | 429.13 | 429.05 | 440.37 | 439.4 | 438.75 | 440.23 | 439.39 | 438.76 | 435.59 | 434.75 | 434.42 | 434.61 | 433.77 | 432.28 | 343.33 | 343.1 | 343.89 | 343.83 | 343.8 | 343.41 | 264.54 | 265.33 | 264.77 | 205.17 | 205.51 | 206.14 | 207.81 | 206.31 | 346.23 | 345.75 | 346.33 | 267.22 | 267.43 | 267.15 | 268 | 269.28 | 268.99 | 268.95 | 272.95 | 272.85 | 272.91 | 208.33 | 207.95 | 207.11 | 206.39 | 422.41 | 423.77 | 424.14 | 423.7 | 434.03 | 434.21 | 434.5 | 430.26 | 430.52 | 431.22 | 433.3 | 433.97 | 432.93 | 432.99 | 430.7 | 431.35 | 430.83 | 429.54 | 434.17 | 434.14 | 434.39 | 438.26 | 436.97 | 437.08 | 432.42 | 431.93 | 432.46 | 426.88 | 424.19 | 425.11 | 269.2 | 269.3 | 267.81 | 434.5 | 434.45 | 435.31 | 432.02 | 431.48 | 431.23 | 434.61 | 435.63 | 435.81 | 423.13 | 422.55 | 422.79 | 266.25 | 266.43 | 264.77 | 266.8 | 265.36 | 266.22 | 263.62 | 262.87 | 263.48 | 205.61 | 205.72 | 205.63 | 207.93 | 207.07 | 206.57 | 340.29 | 339.32 | 338.83 | 341.78 | 341.7 | 340.96 | 432.79 | 431.42 | 432.69 | 434.79 | 434.22 | 433.32 | 432.42 | 430.94 | 431.04 | 423.04 | 421.27 | 421.11 | 266.12 | 268.13 | 265.95 | 434.18 | 433.78 | 433.29 | 437.37 | 438.63 | 438.8
434 | T24 |  | 0.91984 | 0.91983 | 0.92005 | 0.91897 | 0.91904 | 0.91897 | 0.91711 | 0.91747 | 0.91706 | 0.91609 | 0.91624 | 0.91661 | 0.91539 | 0.91539 | 0.9153 | 0.84918 | 0.8496 | 0.8498 | 0.84842 | 0.84769 | 0.84603 | 0.84949 | 0.84935 | 0.84933 | 0.84807 | 0.84701 | 0.84646 | 0.87156 | 0.8717 | 0.87172 | 0.87821 | 0.8783 | 0.87828 | 0.87736 | 0.87766 | 0.87738 | 0.87078 | 0.87145 | 0.87101 | 0.87039 | 0.87141 | 0.87102 | 0.89744 | 0.8971 | 0.89734 | 0.89729 | 0.89802 | 0.89805 | 0.89779 | 0.91325 | 0.91315 | 0.91325 | 0.91713 | 0.91728 | 0.91686 | 0.91732 | 0.91711 | 0.91728 | 0.91398 | 0.91698 | 0.91697 | 0.89893 | 0.89871 | 0.89888 | 0.89943 | 0.89949 | 0.89937 | 0.87144 | 0.87174 | 0.87128 | 0.87733 | 0.87786 | 0.87793 | 0.87801 | 0.87763 | 0.87745 | 0.84896 | 0.8488 | 0.84754 | 0.84611 | 0.8473 | 0.84673 | 0.87335 | 0.87375 | 0.87336 | 0.87227 | 0.87226 | 0.87237 | 0.87865 | 0.87879 | 0.87891 | 0.8999 | 0.89966 | 0.89961 | 0.89984 | 0.89999 | 0.89982 | 0.89986 | 0.91353 | 0.91349 | 0.91351 | 0.91355 | 0.91359 | 0.91347 | 0.91349 | 0.91358 | 0.91736 | 0.91706 | 0.91695 | 0.91679 | 0.91662 | 0.91628 | 0.91582 | 0.91606 | 0.91629 | 0.91677 | 0.91543 | 0.91436 | 0.89819 | 0.89821 | 0.89846 | 0.89846 | 0.89845 | 0.89835 | 0.87177 | 0.8723 | 0.8718 | 0.8466 | 0.84703 | 0.848 | 0.84714 | 0.84494 | 0.89883 | 0.89873 | 0.89891 | 0.87121 | 0.87139 | 0.87122 | 0.87178 | 0.87128 | 0.87116 | 0.87109 | 0.8737 | 0.8738 | 0.87381 | 0.84753 | 0.84695 | 0.84575 | 0.84533 | 0.9128 | 0.91301 | 0.91309 | 0.91297 | 0.91508 | 0.91539 | 0.91555 | 0.91549 | 0.91561 | 0.91606 | 0.91496 | 0.91496 | 0.91467 | 0.91484 | 0.91449 | 0.91458 | 0.91483 | 0.91432 | 0.91631 | 0.916 | 0.91662 | 0.91701 | 0.91702 | 0.91678 | 0.91624 | 0.91646 | 0.91652 | 0.91309 | 0.91268 | 0.91274 | 0.87143 | 0.87129 | 0.87031 | 0.91604 | 0.91584 | 0.91687 | 0.91465 | 0.91485 | 0.91487 | 0.91586 | 0.91604 | 0.91617 | 0.91271 | 0.91267 | 0.91269 | 0.86953 | 0.86962 | 0.86864 | 0.87111 | 0.87023 | 0.87066 | 0.87106 | 0.87046 | 0.87079 | 0.84762 | 0.84738 | 0.84747 | 0.84714 | 0.84589 | 0.8457 | 0.89721 | 0.89685 | 0.89678 | 0.8975 | 0.89758 | 0.89737 | 0.91628 | 0.91563 | 0.91598 | 0.91631 | 0.916 | 0.91595 | 0.91708 | 0.91689 | 0.91693 | 0.91274 | 0.9125 | 0.91247 | 0.86921 | 0.87062 | 0.8691 | 0.91614 | 0.91594 | 0.91565 | 0.9162 | 0.91644 | 0.91614
435 | T25 |  | 0.91984 | 0.91983 | 0.92005 | 0.91897 | 0.91904 | 0.91897 | 0.91711 | 0.91747 | 0.91706 | 0.91609 | 0.91624 | 0.91661 | 0.91539 | 0.91539 | 0.9153 | 0.84918 | 0.8496 | 0.8498 | 0.84842 | 0.84769 | 0.84603 | 0.84949 | 0.84935 | 0.84933 | 0.84807 | 0.84701 | 0.84646 | 0.87156 | 0.8717 | 0.87172 | 0.87821 | 0.8783 | 0.87828 | 0.87736 | 0.87766 | 0.87738 | 0.87078 | 0.87145 | 0.87101 | 0.87039 | 0.87141 | 0.87102 | 0.89744 | 0.8971 | 0.89734 | 0.89729 | 0.89802 | 0.89805 | 0.89779 | 0.91325 | 0.91315 | 0.91325 | 0.91713 | 0.91728 | 0.91686 | 0.91732 | 0.91711 | 0.91728 | 0.91398 | 0.91698 | 0.91697 | 0.89893 | 0.89871 | 0.89888 | 0.89943 | 0.89949 | 0.89937 | 0.87144 | 0.87174 | 0.87128 | 0.87733 | 0.87786 | 0.87793 | 0.87801 | 0.87763 | 0.87745 | 0.84896 | 0.8488 | 0.84754 | 0.84611 | 0.8473 | 0.84673 | 0.87335 | 0.87375 | 0.87336 | 0.87227 | 0.87226 | 0.87237 | 0.87865 | 0.87879 | 0.87891 | 0.8999 | 0.89966 | 0.89961 | 0.89984 | 0.89999 | 0.89982 | 0.89986 | 0.91353 | 0.91349 | 0.91351 | 0.91355 | 0.91359 | 0.91347 | 0.91349 | 0.91358 | 0.91736 | 0.91706 | 0.91695 | 0.91679 | 0.91662 | 0.91628 | 0.91582 | 0.91606 | 0.91629 | 0.91677 | 0.91543 | 0.91436 | 0.89819 | 0.89821 | 0.89846 | 0.89846 | 0.89845 | 0.89835 | 0.87177 | 0.8723 | 0.8718 | 0.8466 | 0.84703 | 0.848 | 0.84714 | 0.84494 | 0.89883 | 0.89873 | 0.89891 | 0.87121 | 0.87139 | 0.87122 | 0.87178 | 0.87128 | 0.87116 | 0.87109 | 0.8737 | 0.8738 | 0.87381 | 0.84753 | 0.84695 | 0.84575 | 0.84533 | 0.9128 | 0.91301 | 0.91309 | 0.91297 | 0.91508 | 0.91539 | 0.91555 | 0.91549 | 0.91561 | 0.91606 | 0.91496 | 0.91496 | 0.91467 | 0.91484 | 0.91449 | 0.91458 | 0.91476 | 0.91432 | 0.91631 | 0.916 | 0.91662 | 0.91701 | 0.91702 | 0.91678 | 0.91624 | 0.91646 | 0.91652 | 0.91309 | 0.91268 | 0.91274 | 0.87143 | 0.87129 | 0.87031 | 0.91604 | 0.91584 | 0.91687 | 0.91465 | 0.91485 | 0.91487 | 0.91586 | 0.91604 | 0.91617 | 0.91271 | 0.91267 | 0.91269 | 0.86953 | 0.86962 | 0.86864 | 0.87111 | 0.87023 | 0.87066 | 0.87106 | 0.87046 | 0.87079 | 0.84762 | 0.84738 | 0.84747 | 0.84714 | 0.84589 | 0.8457 | 0.89721 | 0.89685 | 0.89678 | 0.8975 | 0.89758 | 0.89737 | 0.91628 | 0.91563 | 0.91598 | 0.91631 | 0.916 | 0.91595 | 0.91708 | 0.91689 | 0.91693 | 0.91274 | 0.9125 | 0.91247 | 0.86921 | 0.87062 | 0.8691 | 0.91614 | 0.91594 | 0.91565 | 0.9162 | 0.91644 | 0.91614
436 | T26 |  | 0.79013 | 0.79017 | 0.79144 | 0.78885 | 0.78913 | 0.78889 | 0.78417 | 0.78564 | 0.78398 | 0.78302 | 0.78366 | 0.78458 | 0.78313 | 0.78324 | 0.78274 | 0.14034 | 0.1403 | 0.14031 | 0.14723 | 0.14711 | 0.14708 | 0.14019 | 0.13986 | 0.13974 | 0.14688 | 0.14625 | 0.14619 | 0.2892 | 0.28894 | 0.28968 | 0.29208 | 0.29215 | 0.29238 | 0.31122 | 0.31166 | 0.31151 | 0.30995 | 0.31013 | 0.31078 | 0.32355 | 0.32434 | 0.32343 | 0.48412 | 0.48474 | 0.48432 | 0.49099 | 0.52102 | 0.51978 | 0.51993 | 0.73201 | 0.73095 | 0.73182 | 0.78602 | 0.78663 | 0.78531 | 0.787 | 0.78637 | 0.78706 | 0.77513 | 0.78684 | 0.78657 | 0.48813 | 0.48881 | 0.49001 | 0.51873 | 0.51559 | 0.51502 | 0.32316 | 0.32325 | 0.32357 | 0.29348 | 0.29384 | 0.29381 | 0.2937 | 0.2944 | 0.29391 | 0.13891 | 0.1389 | 0.13885 | 0.14596 | 0.14579 | 0.14542 | 0.2919 | 0.29212 | 0.29164 | 0.30873 | 0.30851 | 0.30859 | 0.31123 | 0.31129 | 0.31116 | 0.49307 | 0.49293 | 0.49378 | 0.5177 | 0.51747 | 0.51871 | 0.51619 | 0.73012 | 0.72937 | 0.73024 | 0.72754 | 0.72794 | 0.72966 | 0.72916 | 0.73062 | 0.78624 | 0.78552 | 0.78489 | 0.78451 | 0.78428 | 0.78298 | 0.78204 | 0.78307 | 0.78416 | 0.78541 | 0.78051 | 0.77635 | 0.48308 | 0.4849 | 0.4813 | 0.48615 | 0.48761 | 0.48765 | 0.29145 | 0.29114 | 0.29075 | 0.13862 | 0.13892 | 0.13923 | 0.14607 | 0.14577 | 0.51505 | 0.51539 | 0.51535 | 0.31152 | 0.31134 | 0.31096 | 0.31174 | 0.32495 | 0.32458 | 0.3248 | 0.32743 | 0.32824 | 0.32822 | 0.14625 | 0.14617 | 0.14603 | 0.14595 | 0.71841 | 0.71865 | 0.71882 | 0.71923 | 0.77973 | 0.78106 | 0.78171 | 0.7828 | 0.78298 | 0.78441 | 0.77932 | 0.77932 | 0.77823 | 0.77917 | 0.77824 | 0.77847 | 0.77937 | 0.77796 | 0.78398 | 0.78283 | 0.78491 | 0.78608 | 0.7863 | 0.78543 | 0.78442 | 0.78513 | 0.78552 | 0.72823 | 0.73249 | 0.72943 | 0.32343 | 0.32265 | 0.3226 | 0.78259 | 0.7818 | 0.78546 | 0.77803 | 0.77915 | 0.77922 | 0.78217 | 0.78272 | 0.78322 | 0.72498 | 0.72465 | 0.72472 | 0.32042 | 0.32094 | 0.32049 | 0.30982 | 0.30998 | 0.3099 | 0.29123 | 0.29068 | 0.29021 | 0.13628 | 0.13668 | 0.13635 | 0.14329 | 0.14333 | 0.14329 | 0.49122 | 0.49274 | 0.4923 | 0.52287 | 0.5235 | 0.5229 | 0.78418 | 0.78225 | 0.78338 | 0.78421 | 0.78295 | 0.78316 | 0.78729 | 0.78689 | 0.78693 | 0.71707 | 0.71601 | 0.7181 | 0.32007 | 0.3201 | 0.3198 | 0.78384 | 0.7829 | 0.78227 | 0.78322 | 0.78368 | 0.7826
437 | T27 |  | 284370 | 284160 | 283500 | 268170 | 268360 | 268110 | 254840 | 254850 | 254610 | 244360 | 244300 | 244740 | 235470 | 235320 | 235190 | 17209 | 17245 | 17262 | 18261 | 18193 | 18064 | 17280 | 17264 | 17255 | 18259 | 18170 | 18127 | 47872 | 47886 | 47925 | 50207 | 50249 | 50274 | 54250 | 54434 | 54306 | 51802 | 51980 | 51907 | 54394 | 54840 | 54661 | 109570 | 109260 | 109450 | 110950 | 119850 | 119870 | 119470 | 222290 | 222060 | 222570 | 248370 | 247730 | 247440 | 248140 | 247740 | 247930 | 245790 | 245240 | 245860 | 112800 | 112610 | 112760 | 121660 | 121760 | 121460 | 54722 | 54858 | 54684 | 49866 | 50086 | 50114 | 50116 | 49991 | 49902 | 17263 | 17249 | 17136 | 18116 | 18245 | 18173 | 48450 | 48588 | 48451 | 52225 | 52223 | 52252 | 54734 | 54710 | 54830 | 115480 | 115250 | 115140 | 122080 | 122230 | 122030 | 120440 | 222320 | 222270 | 222340 | 222260 | 222470 | 222250 | 222370 | 222360 | 247410 | 247000 | 246710 | 247630 | 247110 | 246970 | 245130 | 244430 | 244010 | 244060 | 244430 | 244080 | 110070 | 110060 | 110300 | 111870 | 111860 | 111670 | 47780 | 47956 | 47821 | 17043 | 17080 | 17150 | 18194 | 18016 | 120480 | 120310 | 120500 | 51803 | 51858 | 51790 | 51990 | 54611 | 54542 | 54522 | 55546 | 55541 | 55551 | 18255 | 18208 | 18109 | 18034 | 218670 | 219470 | 219690 | 219410 | 244720 | 244610 | 244670 | 241720 | 241850 | 242070 | 244260 | 244690 | 244150 | 244050 | 242710 | 243090 | 242580 | 241980 | 243770 | 244060 | 243740 | 245890 | 245060 | 245270 | 242530 | 242150 | 242360 | 221070 | 219570 | 220000 | 54614 | 54620 | 54245 | 244360 | 244390 | 244210 | 243410 | 242910 | 242730 | 244320 | 244840 | 244890 | 218970 | 218630 | 218780 | 53852 | 53893 | 53477 | 51709 | 51373 | 51572 | 47569 | 47398 | 47529 | 17107 | 17111 | 17106 | 18214 | 18109 | 18063 | 112130 | 111760 | 111560 | 120380 | 120400 | 120080 | 242910 | 242400 | 242980 | 244100 | 244010 | 243370 | 241890 | 241020 | 241110 | 218860 | 217850 | 217770 | 53806 | 54319 | 53757 | 243700 | 243640 | 243470 | 245850 | 246570 | 246780
438 | T28 |  | 287250 | 287040 | 286350 | 270990 | 271190 | 270940 | 257690 | 257680 | 257450 | 247190 | 247100 | 247530 | 238240 | 238100 | 237970 | 18201 | 18237 | 18254 | 19324 | 19256 | 19124 | 18273 | 18258 | 18250 | 19323 | 19237 | 19193 | 50302 | 50319 | 50352 | 52640 | 52682 | 52708 | 56859 | 57035 | 56908 | 54381 | 54562 | 54483 | 57068 | 57515 | 57343 | 113030 | 112700 | 112900 | 114390 | 123300 | 123330 | 122920 | 225280 | 225060 | 225560 | 251150 | 250490 | 250220 | 250920 | 250520 | 250670 | 248760 | 247980 | 248620 | 116300 | 116100 | 116230 | 125150 | 125300 | 125010 | 57401 | 57537 | 57354 | 52279 | 52499 | 52527 | 52530 | 52400 | 52315 | 18268 | 18253 | 18139 | 19190 | 19322 | 19250 | 50848 | 50985 | 50851 | 54814 | 54813 | 54839 | 57333 | 57308 | 57429 | 119000 | 118770 | 118650 | 125590 | 125730 | 125520 | 123870 | 225320 | 225270 | 225350 | 225290 | 225490 | 225240 | 225380 | 225370 | 250180 | 249780 | 249500 | 250440 | 249910 | 249810 | 247960 | 247230 | 246800 | 246840 | 247290 | 247020 | 113540 | 113500 | 113790 | 115400 | 115360 | 115170 | 50186 | 50368 | 50231 | 18052 | 18085 | 18155 | 19272 | 19094 | 124020 | 123840 | 124040 | 54369 | 54425 | 54360 | 54556 | 57271 | 57206 | 57180 | 58192 | 58181 | 58192 | 19328 | 19280 | 19179 | 19105 | 221780 | 222580 | 222800 | 222510 | 247610 | 247480 | 247510 | 244530 | 244650 | 244840 | 247140 | 247570 | 247060 | 246940 | 245600 | 245980 | 245470 | 244880 | 246550 | 246870 | 246500 | 248640 | 247800 | 248020 | 245290 | 244890 | 245100 | 224110 | 222530 | 223000 | 57269 | 57281 | 56903 | 247170 | 247220 | 246970 | 246290 | 245770 | 245600 | 247150 | 247670 | 247700 | 221990 | 221660 | 221810 | 56523 | 56558 | 56140 | 54283 | 53940 | 54142 | 49970 | 49803 | 49940 | 18127 | 18130 | 18130 | 19307 | 19201 | 19157 | 115630 | 115230 | 115040 | 123840 | 123860 | 123540 | 245710 | 245230 | 245770 | 246910 | 246810 | 246180 | 244600 | 243740 | 243840 | 222010 | 221000 | 220900 | 56519 | 57040 | 56475 | 246500 | 246450 | 246300 | 248660 | 249380 | 249620
439 | T29 |  | 362.54 | 362.43 | 361.87 | 362.33 | 362.24 | 362.36 | 363.49 | 362.92 | 363.44 | 363.26 | 362.94 | 362.66 | 362.63 | 362.5 | 362.7 | 57.504 | 57.498 | 57.5 | 60.621 | 60.62 | 60.625 | 57.507 | 57.506 | 57.508 | 60.631 | 60.635 | 60.633 | 122.84 | 122.86 | 122.87 | 122.8 | 122.82 | 122.83 | 132.2 | 132.2 | 132.19 | 132.29 | 132.26 | 132.28 | 138.51 | 138.54 | 138.52 | 212.41 | 212.41 | 212.42 | 215.42 | 230.63 | 230.59 | 230.62 | 336.23 | 336.2 | 336.2 | 362.41 | 362.18 | 362.63 | 362.03 | 362.15 | 361.91 | 366 | 361.76 | 361.87 | 215.38 | 215.41 | 215.4 | 230.59 | 230.6 | 230.59 | 138.48 | 138.51 | 138.53 | 122.84 | 122.84 | 122.85 | 122.83 | 122.84 | 122.83 | 57.542 | 57.541 | 57.542 | 60.665 | 60.664 | 60.673 | 122.84 | 122.81 | 122.81 | 132.19 | 132.15 | 132.2 | 132.16 | 132.12 | 132.12 | 218.31 | 218.3 | 218.32 | 230.47 | 230.46 | 230.48 | 227.42 | 335.97 | 335.96 | 336.02 | 335.89 | 335.92 | 335.97 | 335.99 | 335.98 | 362.09 | 362.48 | 362.61 | 362.78 | 362.86 | 363.28 | 363.52 | 363.11 | 362.7 | 362.31 | 364.23 | 365.57 | 212.26 | 212.27 | 212.24 | 215.28 | 215.27 | 215.26 | 122.8 | 122.81 | 122.79 | 57.504 | 57.51 | 57.501 | 60.629 | 60.635 | 230.48 | 230.48 | 230.49 | 132.16 | 132.15 | 132.16 | 132.13 | 138.43 | 138.43 | 138.42 | 138.38 | 138.4 | 138.38 | 60.615 | 60.622 | 60.63 | 60.622 | 335.97 | 335.94 | 335.93 | 335.98 | 364.63 | 364.12 | 363.83 | 363.16 | 363.1 | 362.61 | 364.66 | 364.71 | 364.99 | 364.7 | 364.86 | 364.84 | 364.54 | 364.9 | 362.54 | 363.02 | 362.15 | 361.87 | 361.7 | 361.98 | 362.18 | 361.89 | 361.72 | 335.97 | 336.06 | 336.03 | 138.43 | 138.41 | 138.42 | 363.16 | 363.36 | 361.86 | 364.56 | 364.21 | 364.14 | 363.14 | 362.97 | 362.82 | 335.94 | 335.93 | 335.93 | 138.38 | 138.4 | 138.4 | 132.11 | 132.14 | 132.14 | 122.79 | 122.8 | 122.8 | 57.509 | 57.511 | 57.501 | 60.634 | 60.629 | 60.64 | 218.34 | 218.36 | 218.36 | 233.49 | 233.48 | 233.47 | 362.48 | 363.19 | 362.84 | 362.49 | 362.96 | 362.85 | 360.91 | 361.08 | 361.03 | 335.84 | 335.85 | 335.87 | 138.43 | 138.44 | 138.43 | 362.46 | 362.85 | 363.09 | 362.88 | 362.78 | 363.21
440 | T30 |  | 363.14 | 363.17 | 362.62 | 363.02 | 362.91 | 363.06 | 364.08 | 363.59 | 364.17 | 363.85 | 363.62 | 363.27 | 363.14 | 363.1 | 363.23 | 57.535 | 57.533 | 57.534 | 60.663 | 60.672 | 60.68 | 57.549 | 57.543 | 57.541 | 60.666 | 60.681 | 60.685 | 123.28 | 123.31 | 123.32 | 123.26 | 123.27 | 123.28 | 132.74 | 132.71 | 132.73 | 132.71 | 132.72 | 132.72 | 139.01 | 139.01 | 139.02 | 213.15 | 213.16 | 213.14 | 216.19 | 231.32 | 231.27 | 231.3 | 336.66 | 336.65 | 336.67 | 363.08 | 362.77 | 363.25 | 362.56 | 362.76 | 362.56 | 366.64 | 362.38 | 362.51 | 216.13 | 216.17 | 216.16 | 231.32 | 231.26 | 231.29 | 139.02 | 138.98 | 139 | 123.27 | 123.28 | 123.27 | 123.26 | 123.27 | 123.28 | 57.584 | 57.574 | 57.582 | 60.707 | 60.712 | 60.709 | 123.23 | 123.25 | 123.24 | 132.62 | 132.68 | 132.64 | 132.59 | 132.61 | 132.6 | 219.03 | 219.03 | 219.05 | 231.14 | 231.18 | 231.12 | 228.17 | 336.44 | 336.4 | 336.46 | 336.36 | 336.4 | 336.41 | 336.44 | 336.43 | 362.78 | 363.02 | 363.25 | 363.43 | 363.49 | 364 | 364.2 | 363.67 | 363.21 | 363 | 364.88 | 366.19 | 213 | 213 | 212.99 | 216 | 216 | 216.02 | 123.22 | 123.22 | 123.23 | 57.553 | 57.543 | 57.54 | 60.667 | 60.683 | 231.14 | 231.19 | 231.13 | 132.65 | 132.66 | 132.66 | 132.62 | 138.9 | 138.9 | 138.89 | 138.88 | 138.84 | 138.88 | 60.675 | 60.662 | 60.684 | 60.669 | 336.42 | 336.39 | 336.4 | 336.41 | 365.2 | 364.72 | 364.55 | 363.83 | 363.76 | 363.2 | 365.28 | 365.29 | 365.59 | 365.28 | 365.52 | 365.45 | 365.07 | 365.49 | 363.16 | 363.7 | 362.79 | 362.41 | 362.26 | 362.65 | 362.8 | 362.59 | 362.35 | 336.45 | 336.55 | 336.48 | 138.9 | 138.9 | 138.93 | 363.78 | 364.01 | 362.6 | 365.25 | 364.77 | 364.82 | 363.81 | 363.57 | 363.39 | 336.38 | 336.37 | 336.37 | 138.89 | 138.86 | 138.9 | 132.64 | 132.61 | 132.65 | 123.21 | 123.22 | 123.22 | 57.552 | 57.545 | 57.548 | 60.683 | 60.684 | 60.696 | 219.06 | 219.07 | 219.07 | 234.16 | 234.15 | 234.15 | 363.06 | 363.81 | 363.34 | 363.11 | 363.62 | 363.44 | 361.59 | 361.59 | 361.57 | 336.26 | 336.25 | 336.33 | 138.95 | 138.93 | 138.94 | 363.11 | 363.51 | 363.75 | 363.54 | 363.35 | 363.74
441 | Frequency |  | 362.95 | 362.93 | 362.36 | 362.81 | 362.66 | 362.86 | 363.91 | 363.3 | 363.88 | 363.6 | 363.38 | 363.04 | 362.93 | 362.86 | 363.06 | 57.694 | 57.699 | 57.708 | 60.836 | 60.846 | 60.829 | 57.708 | 57.705 | 57.697 | 60.835 | 60.855 | 60.868 | 123.38 | 123.38 | 123.38 | 123.36 | 123.37 | 123.37 | 132.73 | 132.72 | 132.73 | 132.75 | 132.77 | 132.76 | 139.05 | 139.06 | 139.03 | 212.64 | 212.65 | 212.65 | 215.67 | 230.78 | 230.81 | 230.77 | 336.4 | 336.37 | 336.36 | 362.86 | 362.58 | 363.1 | 362.39 | 362.56 | 362.3 | 366.46 | 362.22 | 362.34 | 215.59 | 215.63 | 215.64 | 230.76 | 230.76 | 230.73 | 139.01 | 139.02 | 139.05 | 123.37 | 123.38 | 123.37 | 123.35 | 123.36 | 123.36 | 57.742 | 57.736 | 57.746 | 60.878 | 60.88 | 60.878 | 123.35 | 123.34 | 123.35 | 132.69 | 132.68 | 132.68 | 132.64 | 132.65 | 132.69 | 218.51 | 218.49 | 218.52 | 230.59 | 230.63 | 230.63 | 227.58 | 336.14 | 336.18 | 336.18 | 336.14 | 336.13 | 336.16 | 336.16 | 336.17 | 362.55 | 362.89 | 363.11 | 363.18 | 363.2 | 363.72 | 363.92 | 363.53 | 363.07 | 362.75 | 364.66 | 366.02 | 212.48 | 212.49 | 212.46 | 215.47 | 215.48 | 215.47 | 123.33 | 123.32 | 123.32 | 57.708 | 57.704 | 57.69 | 60.844 | 60.855 | 230.65 | 230.6 | 230.64 | 132.66 | 132.67 | 132.67 | 132.68 | 138.93 | 138.93 | 138.91 | 138.94 | 138.96 | 138.95 | 60.838 | 60.834 | 60.83 | 60.843 | 336.19 | 336.18 | 336.17 | 336.19 | 365.01 | 364.57 | 364.25 | 363.65 | 363.51 | 363.03 | 365.05 | 365.1 | 365.38 | 365.1 | 365.27 | 365.22 | 364.88 | 365.3 | 362.95 | 363.49 | 362.51 | 362.21 | 362.05 | 362.35 | 362.6 | 362.34 | 362.2 | 336.17 | 336.26 | 336.2 | 138.95 | 138.95 | 138.96 | 363.51 | 363.81 | 362.3 | 365 | 364.6 | 364.55 | 363.52 | 363.36 | 363.16 | 336.12 | 336.12 | 336.12 | 138.93 | 138.92 | 138.9 | 132.65 | 132.68 | 132.65 | 123.3 | 123.31 | 123.31 | 57.695 | 57.695 | 57.723 | 60.853 | 60.854 | 60.853 | 218.55 | 218.53 | 218.55 | 233.61 | 233.63 | 233.63 | 362.81 | 363.54 | 363.17 | 362.86 | 363.33 | 363.24 | 361.33 | 361.41 | 361.49 | 336.06 | 336.07 | 336.09 | 138.93 | 138.9 | 138.92 | 362.93 | 363.21 | 363.48 | 363.28 | 363.19 | 363.5
442
443 | COP - BASED ON POWER METER (Takes into account econ) - FUND |  | 4.1995 | 4.2034 | 4.2054 | 3.7188 | 3.7143 | 3.7056 | 3.1973 | 3.228 | 3.2293 | 2.7325 | 2.7381 | 2.722 | 2.3119 | 2.3115 | 2.3095 | 8.8993 | 8.9035 | 8.9953 | 9.1276 | 9.1611 | 9.0655 | 9.0238 | 9.3422 | 9.1211 | 9.1549 | 9.4474 | 9.3935 | 7.2518 | 7.2554 | 7.2568 | 6.931 | 6.9215 | 6.8915 | 6.908 | 6.8821 | 6.9498 | 7.3009 | 7.2498 | 7.2378 | 7.2799 | 7.1838 | 7.2121 | 4.9343 | 4.9472 | 4.9245 | 4.9634 | 4.8729 | 4.8767 | 4.8978 | 3.2999 | 3.3028 | 3.2977 | 2.8737 | 2.883 | 2.892 | 3.2102 | 3.2071 | 3.2042 | 3.2449 | 3.2745 | 3.2672 | 4.795 | 4.7927 | 4.7849 | 4.7643 | 4.7562 | 4.7601 | 7.1986 | 7.1878 | 7.1993 | 6.9027 | 6.9011 | 6.9407 | 6.9414 | 6.9254 | 6.9508 | 9.4029 | 9.4012 | 9.4766 | 9.6068 | 9.5628 | 9.7335 | 7.1198 | 7.1053 | 7.1397 | 7.0834 | 7.0983 | 7.1108 | 6.7654 | 6.7874 | 6.7693 | 4.7494 | 4.7466 | 4.7461 | 4.7166 | 4.7038 | 4.6977 | 4.7347 | 3.257 | 3.2653 | 3.2611 | 3.2629 | 3.2563 | 3.2594 | 3.5299 | 3.535 | 2.8434 | 2.8506 | 2.8487 | 3.1513 | 3.1668 | 3.1603 | 3.2175 | 3.2259 | 3.2312 | 2.827 | 2.8238 | 2.8283 | 4.74 | 4.7199 | 4.7044 | 4.7616 | 4.7773 | 4.7704 | 7.0139 | 6.9929 | 6.9989 | 8.629 | 8.7885 | 8.1704 | 8.8946 | 9.0394 | 4.6898 | 4.6916 | 4.6963 | 6.9936 | 6.9812 | 7.0086 | 6.984 | 7.0084 | 7.0546 | 7.0384 | 6.5098 | 6.5138 | 6.5327 | 8.6171 | 8.9369 | 8.7807 | 9.0985 | 3.3934 | 3.3947 | 3.4051 | 3.3997 | 3.131 | 3.1526 | 3.1544 | 3.2208 | 3.2289 | 3.2403 | 3.2911 | 3.2949 | 3.2986 | 3.2992 | 3.3335 | 3.3281 | 3.3338 | 3.3573 | 2.9682 | 2.9667 | 2.9707 | 3.2626 | 3.2676 | 3.273 | 3.3367 | 3.3428 | 3.3456 | 3.6436 | 3.6653 | 3.6728 | 7.1768 | 7.182 | 7.2335 | 2.9434 | 2.9397 | 2.9466 | 3.3183 | 3.3047 | 3.3052 | 3.2865 | 3.2777 | 3.2994 | 3.6874 | 3.6907 | 3.691 | 7.2787 | 7.3 | 7.3772 | 7.1657 | 7.2253 | 7.1859 | 7.2591 | 7.2616 | 7.2467 | 8.704 | 8.7702 | 9.2724 | 9.3217 | 9.1718 | 9.2698 | 4.9061 | 4.946 | 4.952 | 4.8799 | 4.8825 | 4.8958 | 2.9448 | 2.9468 | 2.9209 | 3.2418 | 3.2451 | 3.2523 | 3.294 | 3.3091 | 3.3003 | 3.6568 | 3.6892 | 3.674 | 7.2558 | 7.1488 | 7.274 | 3.297 | 3.2941 | 3.291 | 3.2499 | 3.2445 | 3.2332
444 | IE POWER - BASED ON POWER METER (FUND) |  | 63.1335 | 63.2693 | 63.2663 | 66.1631 | 66.2063 | 66.0962 | 66.8625 | 67.0575 | 67.0244 | 65.8977 | 66.0071 | 65.7333 | 63.5682 | 63.5366 | 63.4753 | 68.2907 | 68.4212 | 69.3125 | 70.3938 | 70.2655 | 69.139 | 69.5993 | 72.0025 | 70.0758 | 70.7487 | 72.413 | 71.9119 | 73.1297 | 73.2594 | 73.2052 | 69.8995 | 69.8035 | 69.6928 | 70.1148 | 70.0052 | 70.3689 | 73.6701 | 73.3748 | 73.2711 | 73.3555 | 73.1891 | 73.1407 | 74.407 | 74.2521 | 74.292 | 74.4367 | 73.7885 | 73.5098 | 73.5764 | 68.5765 | 68.76 | 68.6629 | 66.2287 | 66.2496 | 66.3559 | 66.6826 | 66.7094 | 66.5436 | 66.5123 | 66.8207 | 66.9076 | 72.2986 | 72.2402 | 72.3194 | 71.3078 | 71.5054 | 71.4501 | 73.1857 | 73.1704 | 73.0871 | 69.8429 | 69.802 | 70.2584 | 70.2458 | 70.2158 | 70.1503 | 72.4945 | 72.5901 | 72.7926 | 73.5479 | 73.5341 | 74.5974 | 71.9992 | 71.9539 | 72.1602 | 71.701 | 71.7563 | 71.7667 | 68.3969 | 68.7337 | 68.4714 | 71.5593 | 71.5749 | 71.5473 | 71.0031 | 70.8501 | 70.7857 | 71.2236 | 67.7684 | 67.9178 | 67.9343 | 67.891 | 67.7025 | 67.7401 | 67.8981 | 67.8721 | 65.1032 | 65.2168 | 65.2939 | 65.7435 | 65.8016 | 65.6566 | 65.9179 | 65.8944 | 65.8266 | 64.7561 | 64.801 | 64.8016 | 71.2308 | 71.0176 | 71.1218 | 71.5327 | 71.768 | 71.6527 | 70.6291 | 70.6725 | 70.6551 | 66.3373 | 67.6988 | 62.9357 | 69.0056 | 69.5628 | 70.5406 | 70.4879 | 70.6274 | 70.6383 | 70.4493 | 70.8481 | 70.7075 | 70.9212 | 71.182 | 70.9994 | 70.3543 | 70.6167 | 70.6107 | 67.8687 | 69.6948 | 68.0992 | 70.1978 | 67.1868 | 67.2252 | 67.3349 | 67.2979 | 65.4111 | 65.4702 | 65.3205 | 65.7072 | 65.8729 | 65.8972 | 67.779 | 67.8664 | 67.9455 | 67.9798 | 67.8773 | 67.9244 | 67.9664 | 67.9551 | 67.958 | 67.8101 | 68.0918 | 67.8938 | 67.806 | 67.9055 | 68.2527 | 68.2228 | 68.2765 | 69.6534 | 69.8588 | 69.9508 | 72.9891 | 73.0301 | 73.1751 | 67.6545 | 67.5848 | 67.6242 | 68.0147 | 67.7141 | 67.766 | 68.3757 | 68.0996 | 68.5147 | 70.1726 | 70.1617 | 70.1192 | 74.2344 | 74.388 | 74.6801 | 72.9008 | 73.0406 | 73.081 | 73.2307 | 73.0589 | 73.1397 | 66.8532 | 67.3622 | 70.7057 | 72.0637 | 70.7423 | 71.3913 | 74.0948 | 74.1684 | 74.3085 | 73.1635 | 73.3096 | 73.2676 | 67.6578 | 67.7008 | 67.4117 | 67.6734 | 67.8304 | 67.884 | 67.7472 | 67.7096 | 67.7784 | 70.3313 | 70.85 | 70.3421 | 73.2872 | 72.941 | 73.4042 | 67.5221 | 67.5713 | 67.5274 | 67.7359 | 67.7838 | 67.7569
445 | % of TABLE IE - BASED ON POWER METER |  | 88.9562 | 89.1274 | 89.1182 | 90.449 | 90.4955 | 90.348 | 90.4302 | 90.6995 | 90.6556 | 89.7881 | 89.9353 | 89.5717 | 88.7377 | 88.6941 | 88.6112 | 117.4488 | 117.5888 | 118.9643 | 120.7981 | 120.8893 | 119.2466 | 119.3968 | 123.5631 | 120.4537 | 121.2778 | 124.604 | 123.807 | 112.6989 | 112.8455 | 112.8109 | 107.7443 | 107.5959 | 107.321 | 107.7938 | 107.5717 | 108.3048 | 113.5121 | 112.961 | 112.7955 | 113.1128 | 112.4061 | 112.5233 | 103.3959 | 103.257 | 103.2238 | 103.5329 | 102.4676 | 102.1664 | 102.3105 | 92.7481 | 92.9956 | 92.8645 | 89.8521 | 89.8624 | 90.0048 | 90.187 | 90.2225 | 89.9989 | 89.9645 | 90.3851 | 90.4989 | 100.4652 | 100.3763 | 100.4454 | 99.1904 | 99.3866 | 99.3298 | 112.4351 | 112.3851 | 112.351 | 107.4782 | 107.471 | 108.1453 | 108.1457 | 108.0085 | 108.0745 | 124.4308 | 124.5029 | 125.1068 | 126.619 | 126.361 | 128.3617 | 110.8562 | 110.7552 | 111.1377 | 110.3496 | 110.4884 | 110.5841 | 105.328 | 105.7805 | 105.4382 | 99.4388 | 99.4399 | 99.4003 | 98.6711 | 98.4565 | 98.3548 | 98.9906 | 91.6544 | 91.8567 | 91.8785 | 91.8202 | 91.5657 | 91.6167 | 91.8311 | 91.7964 | 88.2917 | 88.4471 | 88.5583 | 88.9151 | 88.9949 | 88.7988 | 89.1606 | 89.1316 | 89.0432 | 87.8208 | 87.8897 | 87.8854 | 99.02 | 98.6996 | 98.7665 | 99.4424 | 99.7651 | 99.6042 | 108.9046 | 108.8372 | 108.8466 | 113.9663 | 116.2036 | 108.0667 | 118.1183 | 119.4699 | 98.0539 | 97.9996 | 98.188 | 108.8033 | 108.5557 | 109.1029 | 108.8497 | 109.1758 | 109.6922 | 109.4179 | 105.6362 | 105.9116 | 106.0234 | 115.3079 | 119.0089 | 116.5654 | 120.4426 | 90.8674 | 90.919 | 91.0676 | 91.0173 | 88.4654 | 88.5468 | 88.3457 | 88.8756 | 89.0995 | 89.1375 | 91.6702 | 91.7887 | 91.8951 | 91.9413 | 91.8114 | 91.8735 | 91.9307 | 91.9234 | 92.166 | 91.9572 | 92.3551 | 91.8244 | 91.7063 | 91.8408 | 92.3193 | 92.2804 | 92.3535 | 94.2034 | 94.4821 | 94.6062 | 112.1716 | 112.2446 | 112.6287 | 91.769 | 91.6739 | 91.7166 | 91.9983 | 91.5914 | 91.661 | 92.4755 | 92.1029 | 92.6645 | 94.9068 | 94.8922 | 94.8345 | 113.9564 | 114.249 | 114.9301 | 112.015 | 112.4677 | 112.2861 | 112.8426 | 112.673 | 112.678 | 114.9292 | 115.8046 | 121.99 | 123.5139 | 121.3725 | 122.5599 | 102.9208 | 103.1472 | 103.3264 | 101.7529 | 101.9328 | 101.9311 | 91.7765 | 91.8326 | 91.4569 | 91.5254 | 91.7375 | 91.8101 | 91.6329 | 91.5868 | 91.6759 | 95.1201 | 95.8218 | 95.1364 | 112.8603 | 111.9463 | 113.0938 | 91.3306 | 91.3954 | 91.3351 | 91.6097 | 91.6742 | 91.6377
446 | Frequency Based on POWER METER |  | 120.01 | 120 | 120.02 | 120.01 | 120 | 120.01 | 120 | 120 | 120 | 119.99 | 120 | 120.01 | 120 | 120.04 | 120 | 19.006 | 18.999 | 19.005 | 20.004 | 19.999 | 20.01 | 19.001 | 18.996 | 19.003 | 20.005 | 20.001 | 20 | 39.997 | 40.002 | 40.004 | 40.008 | 40.001 | 40.004 | 43.005 | 43.007 | 43.001 | 43.001 | 43.001 | 43.002 | 44.998 | 45.002 | 45 | 68.991 | 69.01 | 69.002 | 69.997 | 74.998 | 75.002 | 75.007 | 110 | 110 | 109.99 | 119.99 | 120.01 | 119.99 | 120 | 120 | 120 | 120 | 119.99 | 120 | 69.993 | 69.994 | 70.005 | 74.997 | 74.996 | 75.004 | 45.003 | 45.005 | 44.995 | 40.006 | 39.997 | 40.002 | 40.001 | 40.006 | 39.999 | 18.997 | 18.997 | 19.005 | 19.992 | 19.993 | 20.009 | 40.004 | 39.998 | 39.999 | 42.993 | 43.003 | 43.004 | 43.007 | 42.997 | 42.998 | 70.998 | 70.993 | 70.998 | 74.999 | 74.999 | 74.998 | 74 | 110 | 110 | 110 | 110 | 109.99 | 110 | 110 | 110.01 | 120 | 120 | 120.01 | 120.01 | 120 | 120.02 | 120 | 120 | 119.99 | 120.01 | 120 | 120 | 69.002 | 68.984 | 68.991 | 69.999 | 69.989 | 70 | 40.004 | 40.002 | 40.001 | 18.997 | 19 | 18.995 | 20.01 | 20 | 75 | 75.002 | 74.99 | 43.004 | 43.001 | 43.003 | 42.992 | 45.002 | 44.999 | 45.005 | 45 | 44.99 | 44.995 | 20.008 | 20.006 | 19.997 | 19.996 | 110 | 110 | 110.02 | 110.02 | 120 | 120 | 120 | 119.99 | 120 | 120 | 119.99 | 120.01 | 119.98 | 119.99 | 119.99 | 120 | 120 | 120 | 120 | 119.99 | 120.01 | 120.01 | 120 | 120 | 120.01 | 119.99 | 119.99 | 109.98 | 110 | 110 | 45.005 | 45.001 | 44.994 | 119.99 | 120.01 | 120.01 | 120.01 | 120 | 120 | 120 | 120 | 120 | 110.01 | 110 | 110 | 44.998 | 45.006 | 45.002 | 43.001 | 43 | 43.001 | 40 | 40.003 | 39.993 | 18.996 | 18.999 | 19.004 | 19.996 | 19.998 | 20.01 | 71 | 70.999 | 71 | 76.007 | 75.996 | 76.004 | 119.99 | 120.01 | 120 | 120.01 | 120 | 120.01 | 120 | 120 | 119.99 | 110.01 | 110.01 | 110 | 44.999 | 45.002 | 44.998 | 119.99 | 120 | 119.98 | 119.99 | 120 | 119.99
447 | Corrected Swept Vol for Hz |  | 1312.4774 | 1312.368 | 1312.5867 | 1312.4774 | 1312.368 | 1312.4774 | 1312.368 | 1312.368 | 1312.368 | 1312.2586 | 1312.368 | 1312.4774 | 1312.368 | 1312.8055 | 1312.368 | 207.8572 | 207.7807 | 207.8463 | 218.7717 | 218.7171 | 218.8374 | 207.8025 | 207.7479 | 207.8244 | 218.7827 | 218.7389 | 218.728 | 437.4232 | 437.4779 | 437.4997 | 437.5435 | 437.4669 | 437.4997 | 470.3199 | 470.3418 | 470.2761 | 470.2761 | 470.2761 | 470.2871 | 492.1161 | 492.1599 | 492.138 | 754.5132 | 754.721 | 754.6335 | 765.5152 | 820.2081 | 820.2519 | 820.3066 | 1203.004 | 1203.004 | 1202.8946 | 1312.2586 | 1312.4774 | 1312.2586 | 1312.368 | 1312.368 | 1312.368 | 1312.368 | 1312.2586 | 1312.368 | 765.4714 | 765.4824 | 765.6027 | 820.1972 | 820.1863 | 820.2737 | 492.1708 | 492.1927 | 492.0833 | 437.5216 | 437.4232 | 437.4779 | 437.4669 | 437.5216 | 437.4451 | 207.7588 | 207.7588 | 207.8463 | 218.6405 | 218.6514 | 218.8264 | 437.4997 | 437.4341 | 437.4451 | 470.1886 | 470.298 | 470.3089 | 470.3418 | 470.2324 | 470.2433 | 776.4625 | 776.4078 | 776.4625 | 820.2191 | 820.2191 | 820.2081 | 809.2936 | 1203.004 | 1203.004 | 1203.004 | 1203.004 | 1202.8946 | 1203.004 | 1203.004 | 1203.1134 | 1312.368 | 1312.368 | 1312.4774 | 1312.4774 | 1312.368 | 1312.5867 | 1312.368 | 1312.368 | 1312.2586 | 1312.4774 | 1312.368 | 1312.368 | 754.6335 | 754.4366 | 754.5132 | 765.5371 | 765.4277 | 765.548 | 437.4997 | 437.4779 | 437.4669 | 207.7588 | 207.7916 | 207.7369 | 218.8374 | 218.728 | 820.23 | 820.2519 | 820.1206 | 470.3089 | 470.2761 | 470.298 | 470.1777 | 492.1599 | 492.1271 | 492.1927 | 492.138 | 492.0286 | 492.0833 | 218.8155 | 218.7936 | 218.6952 | 218.6843 | 1203.004 | 1203.004 | 1203.2227 | 1203.2227 | 1312.368 | 1312.368 | 1312.368 | 1312.2586 | 1312.368 | 1312.368 | 1312.2586 | 1312.4774 | 1312.1493 | 1312.2586 | 1312.2586 | 1312.368 | 1312.368 | 1312.368 | 1312.368 | 1312.2586 | 1312.4774 | 1312.4774 | 1312.368 | 1312.368 | 1312.4774 | 1312.2586 | 1312.2586 | 1202.7853 | 1203.004 | 1203.004 | 492.1927 | 492.1489 | 492.0724 | 1312.2586 | 1312.4774 | 1312.4774 | 1312.4774 | 1312.368 | 1312.368 | 1312.368 | 1312.368 | 1312.368 | 1203.1134 | 1203.004 | 1203.004 | 492.1161 | 492.2036 | 492.1599 | 470.2761 | 470.2652 | 470.2761 | 437.456 | 437.4888 | 437.3794 | 207.7479 | 207.7807 | 207.8353 | 218.6843 | 218.7061 | 218.8374 | 776.4844 | 776.4735 | 776.4844 | 831.243 | 831.1227 | 831.2101 | 1312.2586 | 1312.4774 | 1312.368 | 1312.4774 | 1312.368 | 1312.4774 | 1312.368 | 1312.368 | 1312.2586 | 1203.1134 | 1203.1134 | 1203.004 | 492.1271 | 492.1599 | 492.1161 | 1312.2586 | 1312.368 | 1312.1493 | 1312.2586 | 1312.368 | 1312.2586
448 | Corrected VE% Based on Swept Hz above |  | 96.7046 | 96.7843 | 96.8354 | 96.5316 | 96.5982 | 96.4799 | 95.5027 | 95.8854 | 95.9349 | 94.724 | 94.764 | 94.5929 | 93.679 | 93.6814 | 93.6762 | 82.1187 | 82.4309 | 83.4384 | 84.9342 | 84.8024 | 83.2887 | 83.8886 | 86.7534 | 84.4116 | 85.3181 | 87.4439 | 86.7525 | 93.7636 | 93.8641 | 93.8106 | 93.6922 | 93.6699 | 93.414 | 94.3748 | 94.1389 | 94.7286 | 95.068 | 94.6192 | 94.2962 | 94.7958 | 94.769 | 94.5375 | 96.9633 | 96.7876 | 96.8123 | 97.1977 | 96.5204 | 96.2607 | 96.347 | 96.0652 | 96.2351 | 96.1448 | 94.917 | 94.9238 | 94.8769 | 95.5184 | 95.4168 | 95.3036 | 95.4328 | 95.707 | 95.671 | 95.6138 | 95.5759 | 95.5841 | 95.1706 | 95.3599 | 95.2629 | 94.6687 | 94.5708 | 94.5086 | 93.0692 | 93.0628 | 93.6619 | 93.6028 | 93.404 | 93.5311 | 87.0653 | 87.0511 | 87.3277 | 88.7089 | 88.8757 | 90.1312 | 93.0763 | 93.0323 | 93.2858 | 93.1204 | 93.2297 | 93.2317 | 92.9557 | 93.3423 | 93.078 | 95.3279 | 95.2846 | 95.3216 | 95.0044 | 94.7955 | 94.6975 | 95.2262 | 94.7324 | 94.8868 | 94.9415 | 94.8658 | 94.6885 | 94.6221 | 94.9078 | 94.8339 | 93.0018 | 93.1605 | 93.2593 | 93.6538 | 93.7235 | 93.5102 | 93.9455 | 93.8835 | 93.7546 | 91.4575 | 91.5305 | 91.5329 | 93.3393 | 93.1032 | 93.1911 | 93.9157 | 94.3062 | 94.0483 | 90.2491 | 90.3324 | 90.1362 | 79.1147 | 80.7385 | 75.1317 | 82.4048 | 83.1243 | 93.2508 | 93.1331 | 93.3341 | 90.9786 | 90.8152 | 91.1208 | 91.0485 | 91.8273 | 92.201 | 91.9572 | 91.7495 | 92.0616 | 92.018 | 80.8852 | 83.0009 | 81.1238 | 83.6378 | 92.8795 | 92.894 | 92.976 | 92.974 | 92.3383 | 92.2948 | 92.1274 | 92.3788 | 92.5992 | 92.5817 | 95.1821 | 95.294 | 95.5025 | 95.5004 | 95.4101 | 95.3973 | 95.4721 | 95.5802 | 95.772 | 95.6607 | 95.9082 | 96.1706 | 96.1108 | 96.159 | 96.437 | 96.4757 | 96.4977 | 96.6747 | 96.7502 | 96.8656 | 94.0195 | 94.0829 | 94.3488 | 95.436 | 95.313 | 95.3545 | 96.2325 | 95.8601 | 95.9635 | 96.4336 | 96.1592 | 96.7221 | 96.8044 | 96.7931 | 96.8775 | 94.3812 | 94.4654 | 94.8659 | 93.0313 | 93.0994 | 93.1 | 92.9725 | 92.7447 | 92.9139 | 79.9064 | 80.5134 | 84.7357 | 86.7045 | 84.8064 | 85.4846 | 96.1085 | 96.2286 | 96.2804 | 95.3313 | 95.4848 | 95.4423 | 94.7408 | 94.8839 | 94.6602 | 95.0519 | 95.2797 | 95.3688 | 95.3185 | 95.3008 | 95.3035 | 96.327 | 96.8995 | 96.3799 | 93.7126 | 93.375 | 93.7167 | 95.7342 | 95.7837 | 95.7527 | 95.8601 | 95.9113 | 95.9675
449 | IE% based on total power | % | 62.5005 | 62.6344 | 62.6366 | 65.4746 | 65.5154 | 65.4058 | 66.123 | 66.321 | 66.285 | 65.1432 | 65.2592 | 64.9924 | 62.8291 | 62.7948 | 62.7338 | 64.5687 | 64.6994 | 65.5457 | 66.5215 | 66.3866 | 65.3068 | 65.8171 | 68.0825 | 66.2552 | 66.853 | 68.3965 | 67.9178 | 69.597 | 69.7172 | 69.6766 | 66.6688 | 66.5798 | 66.4744 | 66.8975 | 66.8127 | 67.1514 | 70.1763 | 69.9025 | 69.8068 | 69.9183 | 69.7851 | 69.7199 | 72.1293 | 71.9856 | 72.0218 | 72.1982 | 71.7239 | 71.4475 | 71.5113 | 67.6663 | 67.8435 | 67.7527 | 65.4956 | 65.5196 | 65.6187 | 65.9439 | 65.9691 | 65.8163 | 65.7182 | 66.0824 | 66.1648 | 70.1228 | 70.0686 | 70.1604 | 69.3193 | 69.4852 | 69.4211 | 69.77 | 69.7634 | 69.6846 | 66.6192 | 66.5937 | 67.0309 | 67.0176 | 66.9878 | 66.9147 | 68.5063 | 68.5973 | 68.7675 | 69.4316 | 69.4353 | 70.4238 | 68.6037 | 68.5711 | 68.7545 | 68.3144 | 68.3657 | 68.3812 | 65.2963 | 65.6178 | 65.3727 | 69.4426 | 69.4536 | 69.4307 | 69.0187 | 68.8778 | 68.8175 | 69.2514 | 66.8661 | 67.0133 | 67.0269 | 66.9779 | 66.7957 | 66.8409 | 66.9913 | 66.9656 | 64.3824 | 64.4909 | 64.5638 | 65.0058 | 65.0644 | 64.9102 | 65.1656 | 65.1481 | 65.0824 | 64.0268 | 64.0516 | 64.0304 | 69.0539 | 68.8651 | 68.9405 | 69.3446 | 69.5906 | 69.4751 | 67.243 | 67.2882 | 67.2652 | 62.6294 | 63.9367 | 59.4518 | 65.1457 | 65.6354 | 68.5271 | 68.4787 | 68.6117 | 67.3044 | 67.1265 | 67.4986 | 67.3818 | 67.6272 | 67.8672 | 67.699 | 67.1552 | 67.4125 | 67.4061 | 64.101 | 65.8197 | 64.3 | 66.2626 | 66.2446 | 66.2859 | 66.395 | 66.3603 | 64.6477 | 64.7109 | 64.5709 | 64.9521 | 65.119 | 65.1517 | 66.9892 | 67.0769 | 67.1452 | 67.1842 | 67.0786 | 67.1264 | 67.1662 | 67.1503 | 67.1918 | 67.0382 | 67.3294 | 67.1429 | 67.0563 | 67.1525 | 67.4847 | 67.4594 | 67.5133 | 68.7086 | 68.9296 | 69.0098 | 69.6053 | 69.6375 | 69.757 | 66.8854 | 66.8111 | 66.8684 | 67.2194 | 66.9261 | 66.9741 | 67.5928 | 67.3215 | 67.7374 | 69.218 | 69.2026 | 69.1613 | 70.7265 | 70.8829 | 71.1376 | 69.4439 | 69.5646 | 69.612 | 69.712 | 69.5309 | 69.6086 | 63.0914 | 63.5761 | 66.7122 | 67.984 | 66.719 | 67.3143 | 71.852 | 71.9349 | 72.0606 | 71.1194 | 71.2617 | 71.2156 | 66.8868 | 66.9195 | 66.6465 | 66.9032 | 67.0609 | 67.1092 | 66.9966 | 66.954 | 67.0195 | 69.3334 | 69.8402 | 69.3454 | 69.7693 | 69.4615 | 69.8714 | 66.7551 | 66.8009 | 66.7515 | 66.9705 | 67.02 | 66.986
450 | Oil Flowmeter (m3/hr) | m3/hr | 0.8232 | 1.2957 | 0.58466 | 2.5652 | 2.2198 | 3.585 | 3.2995 | 3.4562 | 3.4459 | 3.0125 | 3.3249 | 3.3453 | 2.6173 | 2.5554 | 2.548 | 1.7097 | 1.548 | 2.0649 | 2.4146 | 1.9063 | 2.8224 | 1.0809 | 3.3334 | 1.7294 | 2.1767 | 2.3383 | 2.6578 | 1.6925 | 1.7112 | 1.5511 | 1.7967 | 1.7283 | 1.7522 | 1.727 | 1.7675 | 1.7125 | 1.7026 | 1.7455 | 1.7419 | 1.6737 | 1.5884 | 1.6711 | 2.7545 | 2.391 | 2.5158 | 2.7106 | 2.8878 | 2.6815 | 3.077 | 3.449 | 3.4526 | 3.5135 | 3.3598 | 3.3923 | 3.2014 | 3.4012 | 3.2829 | 3.4435 | 3.1465 | 3.3399 | 3.4754 | 3.3203 | 3.1158 | 2.9665 | 3.3055 | 3.3343 | 3.4 | 1.2898 | -0.087323 | -0.087149 | -0.08721 | -0.087407 | -0.087445 | -0.087371 | -0.087287 | -0.087356 | -0.087435 | -0.08743 | -0.087407 | 1.1153 | 1.3586 | 0.95133 | 1.7877 | 1.7826 | 1.7745 | 1.8736 | 1.8327 | 1.798 | 1.7297 | 1.7758 | 1.8303 | 3.2635 | 2.9657 | 2.9667 | 3.4473 | 3.4487 | 3.4911 | 3.1709 | 3.5254 | 3.4988 | 3.4647 | 3.4244 | 3.5817 | 3.4874 | 3.396 | 3.5166 | 3.3631 | 3.4401 | 3.409 | 3.3709 | 3.4555 | 3.4289 | 3.3061 | 3.3695 | 3.2814 | 3.1415 | 3.227 | 3.4368 | 2.4513 | 2.8303 | 2.3925 | 2.7399 | 2.8007 | 2.6863 | 1.7121 | 1.6289 | 1.7105 | 0.95405 | 0.96186 | 0.9611 | 0.95635 | 0.94654 | 3.3347 | 3.225 | 2.9106 | 1.7246 | 1.6962 | 1.815 | 1.7036 | 1.7167 | 1.6121 | 1.6906 | 1.0886 | 0.97593 | 0.76148 | -0.087224 | 1.2108 | 1.632 | 1.2297 | 3.438 | 3.3868 | 3.4775 | 3.4096 | 3.4376 | 3.3661 | 3.1758 | 3.3718 | 3.434 | 3.3974 | 3.0165 | 3.2518 | 3.4668 | 3.1946 | 3.0268 | 3.0704 | 3.4377 | 2.8544 | 2.4486 | 2.4486 | 2.4395 | 2.2385 | 2.3954 | 2.4339 | 2.3551 | 2.33 | 2.3509 | 2.3829 | 2.6506 | 2.1368 | 1.0563 | 1.0465 | 1.0489 | 2.4192 | 2.4118 | 2.4414 | 2.8753 | 3.1463 | 2.9777 | 2.8234 | 2.9772 | 2.7899 | 2.4674 | 2.4217 | 2.4947 | 1.6339 | 1.7331 | 1.6461 | 1.087 | 1.0489 | 1.0594 | 1.0384 | 1.1851 | 0.99594 | -0.087317 | 0.63614 | -0.087444 | 0.64103 | -0.087417 | 1.1103 | 2.1786 | 2.1492 | 1.986 | 2.4165 | 2.3444 | 2.5862 | 2.5215 | 2.5056 | 2.6371 | 2.8738 | 3.0474 | 3.0115 | 2.8429 | 3.0321 | 3.1359 | 2.8283 | 3.2098 | 2.9735 | 1.668 | 1.7092 | 1.7219 | 3.1612 | 3.2919 | 3.3233 | 3.0149 | 3.2999 | 3.008
451 | Pressure Differential meter NRV (AI6) | bar | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.000872 | 0.00049 | 0.000292 | 0.000411 | 0.000514 | 0.000865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.001686 | 0.001747 | 0.001749 | 0.004556 | 0.004408 | 0.004838 | 0.033904 | 0.033879 | 0.033606 | 0.033046 | 0.032879 | 0.032334
452 | COP - based on total (not incl. econ) |  | 4.1574 | 4.1612 | 4.1635 | 3.6801 | 3.6755 | 3.6669 | 3.1619 | 3.1925 | 3.1937 | 2.7012 | 2.7071 | 2.6913 | 2.285 | 2.2845 | 2.2825 | 8.4142 | 8.4192 | 8.5064 | 8.6255 | 8.6554 | 8.5631 | 8.5334 | 8.8336 | 8.6238 | 8.6508 | 8.9234 | 8.8718 | 6.9015 | 6.9046 | 6.907 | 6.6107 | 6.6018 | 6.5733 | 6.591 | 6.5683 | 6.632 | 6.9547 | 6.9067 | 6.8956 | 6.9388 | 6.8497 | 6.8748 | 4.7832 | 4.7962 | 4.774 | 4.8142 | 4.7365 | 4.7399 | 4.7603 | 3.2561 | 3.2588 | 3.2539 | 2.8419 | 2.8513 | 2.8599 | 3.1746 | 3.1715 | 3.1692 | 3.2061 | 3.2383 | 3.2309 | 4.6507 | 4.6486 | 4.6421 | 4.6314 | 4.6218 | 4.6249 | 6.8626 | 6.8531 | 6.8641 | 6.5841 | 6.5839 | 6.6218 | 6.6224 | 6.607 | 6.6302 | 8.8856 | 8.8841 | 8.9526 | 9.0691 | 9.0298 | 9.1889 | 6.784 | 6.7712 | 6.8027 | 6.7489 | 6.7629 | 6.7754 | 6.4587 | 6.4797 | 6.463 | 4.609 | 4.6059 | 4.6057 | 4.5848 | 4.5729 | 4.5671 | 4.6036 | 3.2137 | 3.2218 | 3.2175 | 3.219 | 3.2127 | 3.2161 | 3.2287 | 3.2304 | 2.8119 | 2.8188 | 2.8169 | 3.1159 | 3.1313 | 3.1244 | 3.1808 | 3.1893 | 3.1947 | 2.7952 | 2.7912 | 2.7946 | 4.5952 | 4.5768 | 4.5601 | 4.616 | 4.6324 | 4.6255 | 6.6777 | 6.658 | 6.6631 | 8.1467 | 8.3001 | 7.7181 | 8.3971 | 8.529 | 4.5559 | 4.5579 | 4.5622 | 6.6636 | 6.6519 | 6.6773 | 6.6555 | 6.6829 | 6.7261 | 6.7112 | 6.2138 | 6.2182 | 6.2362 | 8.1388 | 8.44 | 8.2908 | 8.5884 | 3.1836 | 3.1779 | 3.1856 | 3.1826 | 3.0945 | 3.116 | 3.1182 | 3.1838 | 3.1919 | 3.2036 | 3.2527 | 3.2566 | 3.2597 | 3.2606 | 3.2942 | 3.289 | 3.2945 | 3.3176 | 2.9347 | 2.9329 | 2.9375 | 3.2265 | 3.2315 | 3.2367 | 3.2992 | 3.3054 | 3.3082 | 3.2923 | 3.3176 | 3.315 | 6.8441 | 6.8484 | 6.8956 | 2.9099 | 2.9061 | 2.9137 | 3.2795 | 3.2662 | 3.2666 | 3.2488 | 3.2402 | 3.2619 | 3.3306 | 3.3333 | 3.3309 | 6.9348 | 6.956 | 7.0273 | 6.8259 | 6.8815 | 6.8448 | 6.9103 | 6.9109 | 6.8968 | 8.2142 | 8.2773 | 8.7487 | 8.794 | 8.6502 | 8.7404 | 4.7576 | 4.7971 | 4.8022 | 4.7436 | 4.7461 | 4.7587 | 2.9112 | 2.9128 | 2.8877 | 3.2049 | 3.2083 | 3.2152 | 3.2575 | 3.2722 | 3.2633 | 3.3226 | 3.3578 | 3.3443 | 6.9075 | 6.8077 | 6.924 | 3.2595 | 3.2565 | 3.2532 | 3.2132 | 3.2079 | 3.1964
453 | Pressure at Top cover | bar | 4.7358 | 4.7391 | 4.7219 | 4.036 | 4.04 | 4.0367 | 3.3919 | 3.4164 | 3.4089 | 2.8564 | 2.8597 | 2.8551 | 2.3824 | 2.3797 | 2.3726 | 3.8791 | 3.8755 | 3.8697 | 3.8796 | 3.8832 | 3.8807 | 3.8716 | 3.8708 | 3.8785 | 3.8757 | 3.8823 | 3.8812 | 3.8123 | 3.8081 | 3.8161 | 3.8222 | 3.8256 | 3.8201 | 3.7975 | 3.8109 | 3.8161 | 3.8056 | 3.8218 | 3.8123 | 3.8201 | 3.8073 | 3.818 | 3.5835 | 3.5843 | 3.5804 | 3.5855 | 3.578 | 3.5833 | 3.5797 | 3.2995 | 3.2957 | 3.3064 | 3.0226 | 3.0241 | 3.027 | 3.2851 | 3.2816 | 3.2836 | 3.2746 | 3.2773 | 3.2861 | 3.5798 | 3.567 | 3.575 | 3.5759 | 3.5734 | 3.5665 | 3.8059 | 3.8116 | 3.81 | 3.8056 | 3.827 | 3.8273 | 3.8268 | 3.8206 | 3.813 | 3.8961 | 3.8905 | 3.8809 | 3.8893 | 3.8891 | 3.8912 | 3.8148 | 3.8216 | 3.8204 | 3.7982 | 3.8022 | 3.8117 | 3.8091 | 3.8085 | 3.8143 | 3.5859 | 3.5774 | 3.5644 | 3.5645 | 3.563 | 3.5632 | 3.5722 | 3.2969 | 3.2947 | 3.2965 | 3.2945 | 3.298 | 3.2999 | 3.302 | 3.2996 | 3.0253 | 3.0155 | 3.0169 | 3.2761 | 3.2791 | 3.2746 | 3.2772 | 3.2738 | 3.2787 | 3.0509 | 3.0612 | 3.0566 | 3.615 | 3.6165 | 3.6147 | 3.6195 | 3.6167 | 3.6139 | 3.857 | 3.8573 | 3.8551 | 3.9037 | 3.9039 | 3.9191 | 3.9232 | 3.9108 | 3.6102 | 3.6055 | 3.612 | 3.8473 | 3.8507 | 3.8489 | 3.8593 | 3.848 | 3.8529 | 3.8478 | 3.6488 | 3.6403 | 3.6508 | 3.9001 | 3.9299 | 3.9273 | 3.9264 | 3.3013 | 3.3117 | 3.3208 | 3.3101 | 3.2948 | 3.3079 | 3.3151 | 3.3108 | 3.3044 | 3.323 | 3.3086 | 3.3161 | 3.3031 | 3.3001 | 3.3069 | 3.3158 | 3.3023 | 3.3106 | 3.0252 | 3.0297 | 3.022 | 3.2826 | 3.2704 | 3.2766 | 3.2753 | 3.2706 | 3.2747 | 3.2952 | 3.2884 | 3.2974 | 3.8214 | 3.8161 | 3.8061 | 3.0326 | 3.0296 | 3.0293 | 3.2909 | 3.2824 | 3.2766 | 3.2771 | 3.2836 | 3.2825 | 3.308 | 3.2994 | 3.299 | 3.8098 | 3.8165 | 3.812 | 3.8222 | 3.8266 | 3.8157 | 3.8278 | 3.821 | 3.8192 | 3.8866 | 3.8834 | 3.9027 | 3.8822 | 3.8821 | 3.8775 | 3.5885 | 3.5935 | 3.5907 | 3.5868 | 3.5886 | 3.5929 | 3.0255 | 3.0168 | 3.0161 | 3.2754 | 3.2728 | 3.2658 | 3.2744 | 3.2737 | 3.2674 | 3.3097 | 3.2977 | 3.3042 | 3.8025 | 3.799 | 3.8026 | 3.2695 | 3.2732 | 3.266 | 3.267 | 3.276 | 3.2666
454 | Gauge at Top cover | ºC | 14.0457 | 14.0671 | 13.9549 | 9.1971 | 9.2262 | 9.2018 | 4.129 | 4.3346 | 4.2718 | -0.68124 | -0.65032 | -0.69426 | -5.5595 | -5.5886 | -5.6682 | 8.0224 | 7.9956 | 7.9511 | 8.0264 | 8.0536 | 8.035 | 7.966 | 7.9599 | 8.0183 | 7.9965 | 8.0469 | 8.0389 | 7.5118 | 7.4795 | 7.5407 | 7.5883 | 7.6139 | 7.5714 | 7.3976 | 7.5007 | 7.5408 | 7.4601 | 7.5847 | 7.5118 | 7.5719 | 7.4733 | 7.5558 | 5.7082 | 5.7147 | 5.6828 | 5.7244 | 5.6641 | 5.707 | 5.6773 | 3.3423 | 3.31 | 3.4017 | 0.88076 | 0.89429 | 0.92088 | 3.2188 | 3.1885 | 3.206 | 3.128 | 3.1509 | 3.2269 | 5.678 | 5.5744 | 5.6397 | 5.6466 | 5.6264 | 5.5711 | 7.4625 | 7.5062 | 7.4941 | 7.4598 | 7.6245 | 7.6271 | 7.6236 | 7.5758 | 7.5173 | 8.1519 | 8.1091 | 8.0366 | 8.0999 | 8.0989 | 8.1143 | 7.5309 | 7.5837 | 7.5741 | 7.4032 | 7.4343 | 7.5071 | 7.4871 | 7.4827 | 7.5274 | 5.7274 | 5.659 | 5.554 | 5.5549 | 5.5424 | 5.5441 | 5.6172 | 3.3202 | 3.3013 | 3.3168 | 3.2997 | 3.3297 | 3.3457 | 3.3639 | 3.3433 | 0.90512 | 0.8148 | 0.82843 | 3.1407 | 3.1663 | 3.1278 | 3.1499 | 3.1205 | 3.163 | 1.14 | 1.2341 | 1.1915 | 5.9616 | 5.9733 | 5.9596 | 5.9975 | 5.9749 | 5.9531 | 7.8542 | 7.8568 | 7.8399 | 8.2089 | 8.2106 | 8.3253 | 8.3561 | 8.2626 | 5.9229 | 5.8853 | 5.9374 | 7.7804 | 7.8067 | 7.7928 | 7.8723 | 7.7858 | 7.8233 | 7.7843 | 6.2319 | 6.164 | 6.2475 | 8.1819 | 8.4066 | 8.3875 | 8.3808 | 3.3583 | 3.4474 | 3.5254 | 3.4335 | 3.302 | 3.4145 | 3.4765 | 3.4398 | 3.3844 | 3.5445 | 3.4208 | 3.4847 | 3.3735 | 3.3473 | 3.4066 | 3.4822 | 3.3669 | 3.438 | 0.90454 | 0.94593 | 0.87548 | 3.1966 | 3.0913 | 3.1452 | 3.1338 | 3.0931 | 3.129 | 3.3053 | 3.2472 | 3.3247 | 7.5821 | 7.5413 | 7.4644 | 0.97224 | 0.94497 | 0.94239 | 3.2687 | 3.1955 | 3.145 | 3.149 | 3.2054 | 3.1957 | 3.4153 | 3.3421 | 3.3384 | 7.4922 | 7.5443 | 7.5095 | 7.5882 | 7.622 | 7.5378 | 7.6312 | 7.579 | 7.5652 | 8.0797 | 8.0554 | 8.2013 | 8.0466 | 8.0454 | 8.0105 | 5.7488 | 5.789 | 5.7664 | 5.735 | 5.7495 | 5.7842 | 0.90676 | 0.82742 | 0.82048 | 3.1347 | 3.1122 | 3.0518 | 3.1262 | 3.1198 | 3.0655 | 3.4305 | 3.3272 | 3.3833 | 7.4363 | 7.4093 | 7.437 | 3.0834 | 3.1159 | 3.053 | 3.0616 | 3.1399 | 3.0585
455 | Temp after motor | ºC | 22.7776 | 22.7296 | 22.7056 | 22.3947 | 22.3519 | 22.2101 | 21.7072 | 21.603 | 21.5399 | 20.8922 | 20.7709 | 20.6787 | 20.6079 | 20.6004 | 20.5981 | 17.9771 | 17.9956 | 17.8833 | 17.7385 | 17.6792 | 17.6379 | 18.6242 | 18.5443 | 18.4993 | 18.4114 | 18.3591 | 18.3201 | 22.8264 | 22.8483 | 22.8683 | 22.8926 | 22.9215 | 22.9062 | 22.9182 | 22.9483 | 22.9339 | 23.0018 | 22.9914 | 23.0139 | 23.0127 | 23.0337 | 23.0286 | 22.8327 | 22.8259 | 22.7699 | 22.7464 | 22.6381 | 22.6055 | 22.5855 | 22.2827 | 22.183 | 22.0311 | 21.2121 | 21.0633 | 20.6967 | 19.929 | 19.8278 | 19.6724 | 19.1605 | 18.8852 | 18.7036 | 23.1507 | 23.0822 | 23.0314 | 22.6296 | 22.5849 | 22.537 | 21.5798 | 21.5382 | 21.4427 | 21.2781 | 21.225 | 21.1688 | 21.0591 | 20.9891 | 20.9295 | 20.0619 | 20.0102 | 19.9554 | 19.0473 | 18.7823 | 18.5746 | 22.5989 | 22.592 | 22.5856 | 22.5851 | 22.5704 | 22.5848 | 22.6203 | 22.6256 | 22.6394 | 22.9762 | 22.9477 | 22.9516 | 22.8491 | 22.8037 | 22.8399 | 22.9652 | 22.8799 | 22.8507 | 22.8429 | 22.7172 | 22.6382 | 22.5915 | 22.5228 | 22.4003 | 21.0526 | 20.9714 | 20.8422 | 20.0663 | 19.939 | 19.8323 | 19.5084 | 19.2777 | 19.1276 | 21.8241 | 21.7414 | 21.6717 | 20.7673 | 20.7147 | 20.6736 | 20.5433 | 20.5384 | 20.5088 | 19.4722 | 19.3873 | 19.3536 | 17.6604 | 17.5894 | 17.5609 | 17.3494 | 17.2473 | 21.2418 | 21.231 | 21.199 | 19.9991 | 19.9789 | 19.937 | 19.643 | 19.5493 | 19.5242 | 19.5208 | 19.0131 | 18.9861 | 18.9567 | 17.6915 | 17.5855 | 17.5831 | 17.5389 | 24.9401 | 24.8996 | 24.9012 | 24.8546 | 24.6722 | 24.6053 | 24.5658 | 24.0188 | 23.912 | 23.5293 | 23.4345 | 23.3864 | 23.3561 | 23.3411 | 23.2462 | 23.1835 | 23.1491 | 23.0527 | 21.7648 | 21.674 | 21.6298 | 21.111 | 21.0415 | 20.9985 | 20.8925 | 20.8325 | 20.7531 | 20.3791 | 20.2051 | 20.0522 | 18.3873 | 18.2884 | 18.2317 | 21.7326 | 21.6181 | 21.5173 | 21.0421 | 20.9607 | 20.882 | 19.942 | 19.887 | 19.8199 | 19.6187 | 19.536 | 19.4589 | 16.7604 | 16.6981 | 16.6225 | 18.2066 | 18.0843 | 18.0152 | 17.3168 | 17.2251 | 17.104 | 19.3907 | 19.3829 | 19.4077 | 19.353 | 19.3431 | 19.3408 | 20.2704 | 20.2346 | 20.2482 | 19.8033 | 19.7573 | 19.7239 | 21.517 | 21.3045 | 21.12 | 20.798 | 20.6835 | 20.5372 | 20.2806 | 20.1086 | 19.9581 | 21.5806 | 21.4833 | 21.4326 | 19.787 | 19.6938 | 19.6292 | 21.7639 | 21.6537 | 21.5465 | 21.1886 | 21.0316 | 20.9139
456 | Pressure after strainer | barA | 4.8908 | 4.8901 | 4.8736 | 4.1496 | 4.1497 | 4.1475 | 3.4835 | 3.5021 | 3.4986 | 2.9254 | 2.9281 | 2.9249 | 2.4361 | 2.4323 | 2.4294 | 3.8522 | 3.849 | 3.8449 | 3.8544 | 3.8588 | 3.8543 | 3.8415 | 3.8428 | 3.8523 | 3.8478 | 3.8524 | 3.8511 | 3.794 | 3.7928 | 3.7991 | 3.8074 | 3.807 | 3.8043 | 3.7863 | 3.7985 | 3.8009 | 3.7934 | 3.802 | 3.8037 | 3.8084 | 3.7946 | 3.8045 | 3.5977 | 3.5977 | 3.5913 | 3.5993 | 3.5952 | 3.6062 | 3.6023 | 3.3771 | 3.3717 | 3.3812 | 3.1083 | 3.1091 | 3.1114 | 3.3808 | 3.3763 | 3.378 | 3.3679 | 3.3725 | 3.377 | 3.5968 | 3.5873 | 3.5884 | 3.6017 | 3.5943 | 3.5891 | 3.7889 | 3.7995 | 3.794 | 3.7862 | 3.8072 | 3.807 | 3.811 | 3.7996 | 3.7987 | 3.8575 | 3.8547 | 3.8411 | 3.8506 | 3.8567 | 3.8494 | 3.799 | 3.8079 | 3.8029 | 3.7896 | 3.7916 | 3.8008 | 3.7998 | 3.7963 | 3.8064 | 3.6017 | 3.5936 | 3.5869 | 3.5897 | 3.5944 | 3.587 | 3.594 | 3.3789 | 3.3815 | 3.3771 | 3.3791 | 3.3818 | 3.3835 | 3.3868 | 3.3888 | 3.1203 | 3.1137 | 3.1083 | 3.3788 | 3.3818 | 3.3794 | 3.38 | 3.378 | 3.3809 | 3.1144 | 3.1155 | 3.1128 | 3.5974 | 3.5923 | 3.5883 | 3.5973 | 3.5935 | 3.5906 | 3.8027 | 3.8042 | 3.8035 | 3.8404 | 3.8418 | 3.8577 | 3.8611 | 3.8468 | 3.5918 | 3.5918 | 3.5974 | 3.7965 | 3.8012 | 3.7992 | 3.8079 | 3.7993 | 3.8028 | 3.8017 | 3.6002 | 3.591 | 3.6037 | 3.8266 | 3.857 | 3.8543 | 3.8554 | 3.3572 | 3.3671 | 3.3747 | 3.365 | 3.3672 | 3.383 | 3.3887 | 3.3732 | 3.3736 | 3.3916 | 3.3847 | 3.3921 | 3.3787 | 3.3781 | 3.3858 | 3.3898 | 3.3829 | 3.3872 | 3.1149 | 3.1188 | 3.1122 | 3.384 | 3.3732 | 3.3782 | 3.3736 | 3.369 | 3.3743 | 3.3834 | 3.3709 | 3.3776 | 3.803 | 3.8043 | 3.788 | 3.1147 | 3.116 | 3.1191 | 3.3869 | 3.3778 | 3.3733 | 3.37 | 3.3797 | 3.3825 | 3.3777 | 3.373 | 3.3691 | 3.79 | 3.8016 | 3.7897 | 3.8016 | 3.8004 | 3.7965 | 3.8041 | 3.7984 | 3.7979 | 3.852 | 3.8523 | 3.8661 | 3.8482 | 3.8472 | 3.844 | 3.5865 | 3.5939 | 3.5897 | 3.6003 | 3.5993 | 3.5985 | 3.1162 | 3.1087 | 3.1058 | 3.3819 | 3.3775 | 3.3687 | 3.3765 | 3.3746 | 3.3702 | 3.3889 | 3.3777 | 3.381 | 3.792 | 3.7928 | 3.7994 | 3.378 | 3.3731 | 3.3674 | 3.374 | 3.3809 | 3.3759
457 | Pressure before suction strainer (H30+Pressure differential) | barA | 4.8908 | 4.8901 | 4.8736 | 4.1496 | 4.1497 | 4.1475 | 3.4835 | 3.5021 | 3.4986 | 2.9254 | 2.9281 | 2.9249 | 2.4361 | 2.4323 | 2.4294 | 3.8522 | 3.849 | 3.8449 | 3.8544 | 3.8588 | 3.8543 | 3.8415 | 3.8428 | 3.8523 | 3.8478 | 3.8524 | 3.8511 | 3.794 | 3.7928 | 3.7991 | 3.8074 | 3.807 | 3.8043 | 3.7863 | 3.7985 | 3.8009 | 3.7934 | 3.802 | 3.8037 | 3.8084 | 3.7946 | 3.8045 | 3.5977 | 3.5977 | 3.5913 | 3.5993 | 3.5952 | 3.6062 | 3.6023 | 3.3771 | 3.3717 | 3.3812 | 3.1083 | 3.1091 | 3.1114 | 3.3808 | 3.3763 | 3.378 | 3.3679 | 3.3725 | 3.377 | 3.5968 | 3.5873 | 3.5884 | 3.6017 | 3.5943 | 3.5891 | 3.7889 | 3.7995 | 3.794 | 3.7862 | 3.8072 | 3.807 | 3.811 | 3.7996 | 3.7987 | 3.8575 | 3.8547 | 3.8411 | 3.8506 | 3.8567 | 3.8494 | 3.799 | 3.8079 | 3.8029 | 3.7896 | 3.7916 | 3.8008 | 3.7998 | 3.7963 | 3.8064 | 3.6017 | 3.5936 | 3.5869 | 3.5897 | 3.5944 | 3.587 | 3.594 | 3.3789 | 3.3815 | 3.3771 | 3.3791 | 3.3818 | 3.3835 | 3.3868 | 3.3888 | 3.1203 | 3.1137 | 3.1083 | 3.3788 | 3.3818 | 3.3794 | 3.38 | 3.378 | 3.3809 | 3.1144 | 3.1155 | 3.1128 | 3.5974 | 3.5923 | 3.5883 | 3.5973 | 3.5935 | 3.5906 | 3.8027 | 3.8042 | 3.8035 | 3.8404 | 3.8418 | 3.8577 | 3.8611 | 3.8468 | 3.5918 | 3.5918 | 3.5974 | 3.7965 | 3.8012 | 3.7992 | 3.8079 | 3.7993 | 3.8028 | 3.8017 | 3.6002 | 3.591 | 3.6037 | 3.8266 | 3.857 | 3.8543 | 3.8554 | 3.3572 | 3.3671 | 3.3747 | 3.365 | 3.3672 | 3.383 | 3.3887 | 3.3732 | 3.3736 | 3.3916 | 3.3847 | 3.3921 | 3.3787 | 3.3781 | 3.3858 | 3.3898 | 3.3829 | 3.3872 | 3.1149 | 3.1188 | 3.1122 | 3.384 | 3.3732 | 3.3782 | 3.3736 | 3.369 | 3.3743 | 3.3834 | 3.3709 | 3.3776 | 3.803 | 3.8043 | 3.788 | 3.1147 | 3.116 | 3.1191 | 3.3869 | 3.3778 | 3.3733 | 3.37 | 3.3797 | 3.3825 | 3.3777 | 3.373 | 3.3691 | 3.79 | 3.8016 | 3.7897 | 3.8016 | 3.8004 | 3.7965 | 3.8041 | 3.7984 | 3.7979 | 3.8529 | 3.8528 | 3.8664 | 3.8487 | 3.8477 | 3.8448 | 3.5865 | 3.5939 | 3.5897 | 3.6003 | 3.5993 | 3.5985 | 3.1162 | 3.1087 | 3.1058 | 3.3819 | 3.3775 | 3.3687 | 3.3765 | 3.3746 | 3.3702 | 3.3906 | 3.3795 | 3.3828 | 3.7966 | 3.7972 | 3.8042 | 3.4119 | 3.4069 | 3.401 | 3.407 | 3.4137 | 3.4083
458 | Gauge at suction before strainer | ºC | 15.045 | 15.0404 | 14.9352 | 10.0257 | 10.0264 | 10.0102 | 4.8919 | 5.045 | 5.0166 | -0.024873 | 0.0005201 | -0.029269 | -4.9711 | -5.0117 | -5.0443 | 7.8179 | 7.7937 | 7.7616 | 7.8346 | 7.8684 | 7.8341 | 7.7359 | 7.7456 | 7.8182 | 7.7844 | 7.8192 | 7.8091 | 7.3709 | 7.3616 | 7.4104 | 7.4741 | 7.471 | 7.4504 | 7.3107 | 7.4051 | 7.424 | 7.366 | 7.4322 | 7.4456 | 7.4819 | 7.3756 | 7.4516 | 5.8226 | 5.8226 | 5.7712 | 5.8355 | 5.8026 | 5.8914 | 5.8597 | 4.0038 | 3.9585 | 4.0387 | 1.6602 | 1.6676 | 1.6885 | 4.0355 | 3.9971 | 4.0115 | 3.9265 | 3.9654 | 4.003 | 5.8159 | 5.7387 | 5.7481 | 5.855 | 5.795 | 5.7536 | 7.3309 | 7.4129 | 7.3707 | 7.3106 | 7.4729 | 7.4713 | 7.5019 | 7.4136 | 7.4071 | 7.8581 | 7.8367 | 7.733 | 7.8054 | 7.8525 | 7.7967 | 7.4091 | 7.4779 | 7.4393 | 7.337 | 7.3518 | 7.4234 | 7.4157 | 7.3881 | 7.4661 | 5.8551 | 5.79 | 5.7359 | 5.7585 | 5.7962 | 5.7363 | 5.7931 | 4.0191 | 4.041 | 4.0037 | 4.0212 | 4.044 | 4.0581 | 4.0857 | 4.1028 | 1.7679 | 1.7087 | 1.6604 | 4.018 | 4.0439 | 4.0237 | 4.0281 | 4.0116 | 4.0364 | 1.7149 | 1.7248 | 1.7011 | 5.8199 | 5.7791 | 5.747 | 5.8193 | 5.7885 | 5.7659 | 7.4376 | 7.4492 | 7.4441 | 7.7278 | 7.7381 | 7.86 | 7.8858 | 7.7763 | 5.7751 | 5.7756 | 5.8203 | 7.3896 | 7.4265 | 7.411 | 7.4778 | 7.4116 | 7.4388 | 7.4301 | 5.8425 | 5.7689 | 5.8709 | 7.6214 | 7.8545 | 7.8336 | 7.8419 | 3.8356 | 3.9195 | 3.9838 | 3.9014 | 3.9206 | 4.0538 | 4.1016 | 3.971 | 3.9743 | 4.1267 | 4.068 | 4.1303 | 4.0176 | 4.0123 | 4.0773 | 4.1109 | 4.0527 | 4.0896 | 1.7195 | 1.7552 | 1.6955 | 4.0623 | 3.9712 | 4.013 | 3.9743 | 3.9357 | 3.9807 | 4.0571 | 3.9514 | 4.0081 | 7.4402 | 7.4504 | 7.3242 | 1.7182 | 1.7293 | 1.7573 | 4.0871 | 4.0095 | 3.9715 | 3.9439 | 4.0261 | 4.0498 | 4.0094 | 3.9691 | 3.9364 | 7.34 | 7.4291 | 7.3371 | 7.4293 | 7.4202 | 7.3903 | 7.4488 | 7.4048 | 7.4005 | 7.823 | 7.822 | 7.9264 | 7.7907 | 7.7835 | 7.7616 | 5.7321 | 5.7925 | 5.7584 | 5.844 | 5.8357 | 5.8295 | 1.7314 | 1.6637 | 1.6382 | 4.0446 | 4.0075 | 3.9326 | 3.9987 | 3.9832 | 3.9456 | 4.1175 | 4.024 | 4.0519 | 7.3907 | 7.3954 | 7.4493 | 4.2966 | 4.2551 | 4.2054 | 4.2559 | 4.3122 | 4.2664
459 | Gauge after strainer | ºC | 15.045 | 15.0404 | 14.9352 | 10.0257 | 10.0264 | 10.0102 | 4.8919 | 5.045 | 5.0166 | -0.024873 | 0.0005201 | -0.029269 | -4.9711 | -5.0117 | -5.0443 | 7.8179 | 7.7937 | 7.7616 | 7.8346 | 7.8684 | 7.8341 | 7.7359 | 7.7456 | 7.8182 | 7.7844 | 7.8192 | 7.8091 | 7.3709 | 7.3616 | 7.4104 | 7.4741 | 7.471 | 7.4504 | 7.3107 | 7.4051 | 7.424 | 7.366 | 7.4322 | 7.4456 | 7.4819 | 7.3756 | 7.4516 | 5.8226 | 5.8226 | 5.7712 | 5.8355 | 5.8026 | 5.8914 | 5.8597 | 4.0038 | 3.9585 | 4.0387 | 1.6602 | 1.6676 | 1.6885 | 4.0355 | 3.9971 | 4.0115 | 3.9265 | 3.9654 | 4.003 | 5.8159 | 5.7387 | 5.7481 | 5.855 | 5.795 | 5.7536 | 7.3309 | 7.4129 | 7.3707 | 7.3106 | 7.4729 | 7.4713 | 7.5019 | 7.4136 | 7.4071 | 7.8581 | 7.8367 | 7.733 | 7.8054 | 7.8525 | 7.7967 | 7.4091 | 7.4779 | 7.4393 | 7.337 | 7.3518 | 7.4234 | 7.4157 | 7.3881 | 7.4661 | 5.8551 | 5.79 | 5.7359 | 5.7585 | 5.7962 | 5.7363 | 5.7931 | 4.0191 | 4.041 | 4.0037 | 4.0212 | 4.044 | 4.0581 | 4.0857 | 4.1028 | 1.7679 | 1.7087 | 1.6604 | 4.018 | 4.0439 | 4.0237 | 4.0281 | 4.0116 | 4.0364 | 1.7149 | 1.7248 | 1.7011 | 5.8199 | 5.7791 | 5.747 | 5.8193 | 5.7885 | 5.7659 | 7.4376 | 7.4492 | 7.4441 | 7.7278 | 7.7381 | 7.86 | 7.8858 | 7.7763 | 5.7751 | 5.7756 | 5.8203 | 7.3896 | 7.4265 | 7.411 | 7.4778 | 7.4116 | 7.4388 | 7.4301 | 5.8425 | 5.7689 | 5.8709 | 7.6214 | 7.8545 | 7.8336 | 7.8419 | 3.8356 | 3.9195 | 3.9838 | 3.9014 | 3.9206 | 4.0538 | 4.1016 | 3.971 | 3.9743 | 4.1267 | 4.068 | 4.1303 | 4.0176 | 4.0123 | 4.0773 | 4.1109 | 4.0527 | 4.0896 | 1.7195 | 1.7552 | 1.6955 | 4.0623 | 3.9712 | 4.013 | 3.9743 | 3.9357 | 3.9807 | 4.0571 | 3.9514 | 4.0081 | 7.4402 | 7.4504 | 7.3242 | 1.7182 | 1.7293 | 1.7573 | 4.0871 | 4.0095 | 3.9715 | 3.9439 | 4.0261 | 4.0498 | 4.0094 | 3.9691 | 3.9364 | 7.34 | 7.4291 | 7.3371 | 7.4293 | 7.4202 | 7.3903 | 7.4488 | 7.4048 | 7.4005 | 7.8163 | 7.8183 | 7.9242 | 7.7876 | 7.7795 | 7.755 | 5.7321 | 5.7925 | 5.7584 | 5.844 | 5.8357 | 5.8295 | 1.7314 | 1.6637 | 1.6382 | 4.0446 | 4.0075 | 3.9326 | 3.9987 | 3.9832 | 3.9456 | 4.1033 | 4.0092 | 4.0372 | 7.3554 | 7.3613 | 7.412 | 4.0114 | 3.9698 | 3.9219 | 3.9776 | 4.0357 | 3.9942
460 | Differential pressure Suction [keller 1bar] | bar | 0.12494 | 0.13135 | 0.12624 | 0.10801 | 0.10773 | 0.11225 | 0.078395 | 0.083706 | 0.0814 | 0.052269 | 0.05624 | 0.060559 | 0.039958 | 0.039353 | 0.046264 | -0.027835 | -0.027778 | -0.027895 | -0.024655 | -0.02489 | -0.02546 | -0.039464 | -0.040668 | -0.038121 | -0.037519 | -0.037996 | -0.03777 | -0.042881 | -0.043335 | -0.044098 | -0.043432 | -0.043296 | -0.044384 | -0.041877 | -0.042591 | -0.039854 | -0.0409 | -0.041147 | -0.042255 | -0.040266 | -0.038397 | -0.039207 | -0.020506 | -0.020746 | -0.019085 | -0.018116 | -0.012873 | -0.013636 | -0.012836 | 0.042871 | 0.043758 | 0.041436 | 0.04399 | 0.041779 | 0.04982 | 0.074357 | 0.075196 | 0.077519 | 0.078238 | 0.086044 | 0.091375 | 0.011424 | 0.011271 | 0.011116 | 0.026736 | 0.026879 | 0.030243 | 0.02356 | 0.023876 | 0.023433 | 0.019441 | 0.019332 | 0.01955 | 0.019676 | 0.019435 | 0.019145 | -0.041105 | -0.039229 | -0.040285 | -0.033653 | -0.032236 | -0.031732 | -0.044268 | -0.044165 | -0.044208 | -0.041311 | -0.042226 | -0.040987 | -0.041779 | -0.041886 | -0.041437 | -0.011722 | -0.01326 | -0.012592 | -0.0074391 | -0.0085503 | -0.0078958 | -0.010759 | 0.04613 | 0.049175 | 0.051204 | 0.053992 | 0.054408 | 0.052598 | 0.050972 | 0.050516 | 0.053287 | 0.054379 | 0.055519 | 0.07417 | 0.075738 | 0.073887 | 0.075876 | 0.074013 | 0.074297 | 0.063156 | 0.056516 | 0.060244 | -0.012123 | -0.0091849 | -0.011245 | -0.0094513 | -0.0092282 | -0.009319 | -0.042132 | -0.042051 | -0.041508 | -0.051278 | -0.051217 | -0.050828 | -0.051235 | -0.051498 | -0.005309 | -0.0049317 | -0.006027 | -0.037466 | -0.037391 | -0.038116 | -0.0377 | -0.035203 | -0.035145 | -0.035172 | -0.037871 | -0.037969 | -0.03892 | -0.049294 | -0.051488 | -0.052001 | -0.052269 | 0.049699 | 0.050022 | 0.051557 | 0.047706 | 0.068098 | 0.066953 | 0.068172 | 0.06664 | 0.068436 | 0.068001 | 0.079025 | 0.080172 | 0.078024 | 0.07736 | 0.077534 | 0.079187 | 0.079776 | 0.078635 | 0.075592 | 0.077649 | 0.076962 | 0.10702 | 0.10494 | 0.10941 | 0.10827 | 0.10492 | 0.11045 | 0.087841 | 0.089428 | 0.089254 | 0.014405 | 0.01487 | 0.014473 | 0.073074 | 0.073338 | 0.072753 | 0.10212 | 0.099822 | 0.1014 | 0.08201 | 0.088667 | 0.095284 | 0.08453 | 0.08339 | 0.082702 | 0.021499 | 0.021084 | 0.019599 | 0.013034 | 0.012872 | 0.014285 | 0.017987 | 0.017652 | 0.016662 | -0.037548 | -0.036868 | -0.036811 | -0.037746 | -0.037722 | -0.036952 | 0.045826 | 0.04415 | 0.046213 | 0.053161 | 0.053688 | 0.052377 | 0.058628 | 0.063911 | 0.074017 | 0.055086 | 0.057583 | 0.060476 | 0.066768 | 0.067516 | 0.06301 | 0.10767 | 0.10781 | 0.10605 | -0.0072758 | -0.0098827 | -0.0073511 | 0.065007 | 0.068452 | 0.066994 | 0.074807 | 0.067693 | 0.06868
461 | Differential pressure Oil Separator [omega 2bar] | bar | 0.32328 | 0.32543 | 0.3221 | 0.2707 | 0.27353 | 0.27315 | 0.22438 | 0.22684 | 0.22921 | 0.18613 | 0.18818 | 0.18558 | 0.15179 | 0.15174 | 0.15066 | 0.0013097 | 0.001674 | 0.0015389 | 0.0022373 | 0.001982 | 0.0022151 | 0.0016721 | 0.0015708 | 0.0016275 | 0.0022243 | 0.0022516 | 0.0023649 | 0.023965 | 0.023875 | 0.024154 | 0.023995 | 0.024229 | 0.023978 | 0.028352 | 0.028721 | 0.028745 | 0.028587 | 0.028826 | 0.028966 | 0.032475 | 0.032498 | 0.032661 | 0.080968 | 0.08046 | 0.081131 | 0.082592 | 0.092764 | 0.092702 | 0.092607 | 0.18765 | 0.18699 | 0.18798 | 0.19941 | 0.1999 | 0.19912 | 0.21915 | 0.22084 | 0.21856 | 0.21753 | 0.21721 | 0.21858 | 0.079863 | 0.079262 | 0.079651 | 0.089567 | 0.08907 | 0.088998 | 0.031016 | 0.030582 | 0.030904 | 0.022918 | 0.022818 | 0.023015 | 0.023185 | 0.023005 | 0.022678 | 0.0016981 | 0.0016955 | 0.0018036 | 0.0027025 | 0.0026085 | 0.0027387 | 0.023398 | 0.023484 | 0.023436 | 0.027789 | 0.027768 | 0.028393 | 0.028208 | 0.027901 | 0.028014 | 0.081762 | 0.082045 | 0.081817 | 0.09126 | 0.089749 | 0.089825 | 0.086746 | 0.17904 | 0.17958 | 0.17966 | 0.18097 | 0.17921 | 0.17967 | 0.17922 | 0.18065 | 0.19176 | 0.19159 | 0.19111 | 0.20957 | 0.20968 | 0.21107 | 0.21054 | 0.21022 | 0.2115 | 0.18396 | 0.18493 | 0.18412 | 0.074105 | 0.074336 | 0.074255 | 0.07561 | 0.075639 | 0.076194 | 0.021554 | 0.021333 | 0.021153 | 0.0012244 | 0.0014253 | 0.0013989 | 0.0017453 | 0.0020865 | 0.086221 | 0.085483 | 0.085645 | 0.025934 | 0.026416 | 0.026411 | 0.026438 | 0.029858 | 0.029769 | 0.029679 | 0.027337 | 0.027139 | 0.027514 | 0.0019117 | 0.0018941 | 0.0018606 | 0.0018466 | 0.17038 | 0.1719 | 0.17107 | 0.1716 | 0.20131 | 0.20261 | 0.20184 | 0.20029 | 0.20097 | 0.20151 | 0.20079 | 0.20185 | 0.20004 | 0.20063 | 0.19994 | 0.20165 | 0.20022 | 0.20135 | 0.19257 | 0.19219 | 0.19262 | 0.21408 | 0.21142 | 0.21182 | 0.21075 | 0.21111 | 0.21014 | 0.17984 | 0.17894 | 0.18153 | 0.030596 | 0.030531 | 0.030928 | 0.19432 | 0.19486 | 0.19527 | 0.21522 | 0.2135 | 0.21448 | 0.21383 | 0.21327 | 0.21385 | 0.18204 | 0.18091 | 0.18098 | 0.031274 | 0.031083 | 0.031643 | 0.028206 | 0.027669 | 0.027566 | 0.023554 | 0.022908 | 0.02324 | 0.0012654 | 0.0012836 | 0.00155 | 0.0018736 | 0.0020917 | 0.0021546 | 0.082704 | 0.082116 | 0.081489 | 0.091912 | 0.092317 | 0.091985 | 0.19493 | 0.1956 | 0.19647 | 0.21511 | 0.21617 | 0.21435 | 0.21443 | 0.21521 | 0.21436 | 0.18122 | 0.18015 | 0.18176 | 0.031309 | 0.03091 | 0.031361 | 0.21342 | 0.21279 | 0.21132 | 0.21239 | 0.21243 | 0.21278
462 | Oil Sump pressure | bar | 14.3429 | 14.407 | 14.3632 | 14.2377 | 14.2554 | 14.2356 | 14.1253 | 14.0973 | 14.0754 | 14.0159 | 14.0146 | 14.0282 | 13.9525 | 13.9328 | 13.9229 | 7.3034 | 7.3127 | 7.3078 | 7.3291 | 7.3189 | 7.2838 | 7.3068 | 7.3087 | 7.3074 | 7.3223 | 7.3021 | 7.2899 | 8.5209 | 8.5256 | 8.5261 | 8.5339 | 8.5423 | 8.5531 | 8.5377 | 8.5769 | 8.5494 | 8.5225 | 8.5562 | 8.5474 | 8.5566 | 8.5953 | 8.5826 | 10.8948 | 10.8639 | 10.8874 | 10.8532 | 10.933 | 10.9281 | 10.8722 | 13.6738 | 13.6781 | 13.6875 | 14.0946 | 14.0536 | 14.0424 | 13.6929 | 13.7146 | 13.6904 | 13.4954 | 13.4744 | 13.5202 | 10.8801 | 10.8738 | 10.8964 | 10.8731 | 10.8853 | 10.8626 | 8.5692 | 8.5965 | 8.5772 | 8.5126 | 8.5586 | 8.5617 | 8.5665 | 8.5467 | 8.5287 | 7.3289 | 7.3305 | 7.287 | 7.2915 | 7.3183 | 7.2947 | 8.5406 | 8.5672 | 8.5365 | 8.5182 | 8.5203 | 8.5334 | 8.5412 | 8.542 | 8.5545 | 10.9645 | 10.9414 | 10.9327 | 10.9217 | 10.9291 | 10.9154 | 10.8961 | 13.7476 | 13.7561 | 13.7515 | 13.7525 | 13.7483 | 13.7416 | 13.7401 | 13.7381 | 14.1037 | 14.0787 | 14.0572 | 13.7728 | 13.7389 | 13.7222 | 13.5669 | 13.495 | 13.4872 | 13.9727 | 14.0051 | 14.0048 | 10.8588 | 10.8619 | 10.8836 | 10.8684 | 10.8587 | 10.8422 | 8.5148 | 8.5378 | 8.5269 | 7.2868 | 7.296 | 7.3226 | 7.3509 | 7.2995 | 10.8503 | 10.8239 | 10.8426 | 8.5272 | 8.5365 | 8.5307 | 8.5663 | 8.5572 | 8.5504 | 8.5481 | 8.5207 | 8.5199 | 8.525 | 7.3547 | 7.3694 | 7.3389 | 7.3258 | 13.5813 | 13.6297 | 13.651 | 13.638 | 13.6866 | 13.6796 | 13.6613 | 13.4842 | 13.4951 | 13.4864 | 13.6402 | 13.6635 | 13.6254 | 13.6329 | 13.5068 | 13.5369 | 13.4986 | 13.44 | 13.9733 | 14.0262 | 13.997 | 13.7762 | 13.7379 | 13.7303 | 13.513 | 13.5169 | 13.5334 | 13.7843 | 13.674 | 13.7188 | 8.5555 | 8.5596 | 8.4999 | 14.0165 | 14.0118 | 13.9882 | 13.512 | 13.4938 | 13.4706 | 13.6528 | 13.68 | 13.6575 | 13.6103 | 13.5785 | 13.5891 | 8.5403 | 8.5559 | 8.5039 | 8.5765 | 8.5417 | 8.5639 | 8.5333 | 8.5087 | 8.5188 | 7.2956 | 7.3009 | 7.2995 | 7.3229 | 7.3083 | 7.2952 | 10.8717 | 10.8204 | 10.8167 | 10.8627 | 10.8632 | 10.8306 | 14.0394 | 14.0159 | 14.0205 | 13.7144 | 13.6976 | 13.6893 | 13.5377 | 13.4648 | 13.4849 | 13.7127 | 13.6306 | 13.5994 | 8.5236 | 8.5925 | 8.5296 | 13.4781 | 13.5 | 13.4991 | 13.6896 | 13.7229 | 13.7414
463
464
465 | Economiser Calculations (Ignore if not running economised)
466 | Item
467 | Assumed Liq Approach @ Economiser | ºC | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
468 | Pressure @ Econ@Compressor | BarA | 8.6348 | 8.6285 | 8.6243 | 8.5484 | 8.5461 | 8.5221 | 8.4413 | 8.4223 | 8.4045 | 8.2906 | 8.2746 | 8.2558 | 8.1518 | 8.1516 | 8.1439 | 7.6883 | 7.6749 | 7.6756 | 7.6428 | 7.6336 | 7.6292 | 7.799 | 7.7922 | 7.7908 | 7.7675 | 7.7613 | 7.7582 | 8.455 | 8.4602 | 8.4635 | 8.4708 | 8.4702 | 8.4709 | 8.4768 | 8.4757 | 8.4799 | 8.4906 | 8.4938 | 8.5186 | 8.5293 | 8.5373 | 8.5389 | 8.5675 | 8.5767 | 8.5641 | 8.5601 | 8.544 | 8.5434 | 8.5276 | 8.4521 | 8.4365 | 8.3986 | 8.2005 | 8.1648 | 8.0863 | 7.9266 | 7.9036 | 7.8789 | 7.7947 | 7.7753 | 7.7435 | 8.4122 | 8.3863 | 8.3756 | 8.2964 | 8.2792 | 8.2753 | 8.102 | 8.0947 | 8.0819 | 8.0613 | 8.0515 | 8.0407 | 8.0219 | 8.0117 | 8.0032 | 7.8814 | 7.8635 | 7.8615 | 7.7608 | 7.7299 | 7.7267 | 8.3739 | 8.3785 | 8.3743 | 8.3887 | 8.3909 | 8.3951 | 8.4105 | 8.4154 | 8.4131 | 8.4665 | 8.4716 | 8.4632 | 8.4403 | 8.4471 | 8.4529 | 8.4622 | 8.437 | 8.4356 | 8.4334 | 8.4098 | 8.4042 | 8.3926 | 8.3812 | 8.3533 | 8.088 | 8.0736 | 8.0436 | 7.8913 | 7.8766 | 7.8545 | 7.7996 | 7.7697 | 7.7737 | 8.4721 | 8.4522 | 8.4436 | 8.234 | 8.2236 | 8.2227 | 8.1699 | 8.1704 | 8.1603 | 7.9611 | 7.9505 | 7.9479 | 7.7678 | 7.7624 | 7.7525 | 7.7264 | 7.718 | 8.3037 | 8.295 | 8.2789 | 8.0887 | 8.0956 | 8.0862 | 8.0374 | 8.024 | 8.0136 | 8.0114 | 7.8993 | 7.8961 | 7.8928 | 7.7666 | 7.7533 | 7.752 | 7.757 | 8.9966 | 8.9857 | 8.9795 | 8.9769 | 8.8824 | 8.8671 | 8.8562 | 8.7487 | 8.7354 | 8.6794 | 8.8807 | 8.8701 | 8.8601 | 8.8601 | 8.8366 | 8.8188 | 8.803 | 8.7805 | 8.4585 | 8.4446 | 8.4312 | 8.3059 | 8.2927 | 8.2723 | 8.2481 | 8.2316 | 8.2163 | 8.1345 | 8.0984 | 8.0683 | 7.744 | 7.7269 | 7.7258 | 8.4467 | 8.4234 | 8.4077 | 8.3 | 8.284 | 8.2754 | 8.1488 | 8.1331 | 8.1158 | 8.0749 | 8.0532 | 8.0264 | 7.5594 | 7.5504 | 7.5345 | 7.8341 | 7.8246 | 7.8102 | 7.7531 | 7.742 | 7.7261 | 8.0665 | 8.0632 | 8.0628 | 8.0669 | 8.0618 | 8.0629 | 8.1815 | 8.1701 | 8.1636 | 8.0727 | 8.0678 | 8.0516 | 8.4408 | 8.3876 | 8.3531 | 8.2698 | 8.2522 | 8.2204 | 8.1659 | 8.1342 | 8.0997 | 8.2913 | 8.2775 | 8.2599 | 7.9204 | 7.9024 | 7.8954 | 8.4482 | 8.4278 | 8.4046 | 8.3458 | 8.3168 | 8.2942
469 | Gauge @ Econ@ Compressor | ºC | 34.0352 | 34.0093 | 33.9918 | 33.6757 | 33.6662 | 33.566 | 33.2263 | 33.1462 | 33.071 | 32.5864 | 32.5181 | 32.4375 | 31.9893 | 31.9883 | 31.9553 | 29.9384 | 29.8774 | 29.8808 | 29.7318 | 29.6901 | 29.6699 | 30.4365 | 30.4059 | 30.3994 | 30.2954 | 30.2674 | 30.2532 | 33.2839 | 33.3062 | 33.3199 | 33.3505 | 33.3479 | 33.3512 | 33.3759 | 33.3713 | 33.3888 | 33.4338 | 33.4471 | 33.5513 | 33.596 | 33.6296 | 33.636 | 33.7555 | 33.7941 | 33.7416 | 33.7249 | 33.6576 | 33.6548 | 33.589 | 33.272 | 33.2061 | 33.0461 | 32.1997 | 32.0458 | 31.7048 | 31.0042 | 30.9021 | 30.7927 | 30.417 | 30.33 | 30.1873 | 33.1036 | 32.9939 | 32.9486 | 32.6113 | 32.5375 | 32.5212 | 31.773 | 31.7414 | 31.6856 | 31.5957 | 31.5529 | 31.5059 | 31.4236 | 31.3787 | 31.3413 | 30.8037 | 30.724 | 30.7152 | 30.2651 | 30.1259 | 30.1117 | 32.941 | 32.9605 | 32.943 | 33.0039 | 33.0134 | 33.0309 | 33.0964 | 33.1169 | 33.1072 | 33.3326 | 33.3538 | 33.3188 | 33.2222 | 33.2509 | 33.2754 | 33.3143 | 33.2082 | 33.2022 | 33.1929 | 33.0932 | 33.0697 | 33.0203 | 32.9723 | 32.8538 | 31.7125 | 31.6497 | 31.5184 | 30.8476 | 30.7822 | 30.6841 | 30.4392 | 30.3052 | 30.3232 | 33.3559 | 33.2723 | 33.2362 | 32.344 | 32.2993 | 32.2955 | 32.0675 | 32.0698 | 32.0259 | 31.1564 | 31.1095 | 31.0982 | 30.2964 | 30.2721 | 30.2276 | 30.1104 | 30.0725 | 32.6425 | 32.6054 | 32.5363 | 31.7152 | 31.7453 | 31.7046 | 31.4915 | 31.4329 | 31.387 | 31.3774 | 30.8831 | 30.8691 | 30.8544 | 30.2913 | 30.2314 | 30.2253 | 30.2481 | 35.5125 | 35.4688 | 35.4438 | 35.4332 | 35.0513 | 34.9891 | 34.9445 | 34.5054 | 34.4509 | 34.2201 | 35.0441 | 35.0012 | 34.9607 | 34.9607 | 34.8649 | 34.7922 | 34.7278 | 34.6358 | 33.2986 | 33.2404 | 33.1838 | 32.6518 | 32.5954 | 32.5083 | 32.4043 | 32.3334 | 32.2677 | 31.9142 | 31.7574 | 31.6262 | 30.1895 | 30.1124 | 30.1077 | 33.2493 | 33.1507 | 33.0846 | 32.6266 | 32.5584 | 32.5216 | 31.9763 | 31.9083 | 31.833 | 31.6552 | 31.5604 | 31.4431 | 29.3512 | 29.3101 | 29.237 | 30.5932 | 30.5508 | 30.4864 | 30.2306 | 30.1805 | 30.1087 | 31.6187 | 31.6043 | 31.6023 | 31.6202 | 31.598 | 31.6028 | 32.1179 | 32.0684 | 32.0402 | 31.6455 | 31.6244 | 31.5535 | 33.2244 | 32.9991 | 32.853 | 32.4976 | 32.4221 | 32.2856 | 32.0504 | 31.9129 | 31.7631 | 32.5895 | 32.5303 | 32.4551 | 30.9764 | 30.8971 | 30.8659 | 33.2555 | 33.1693 | 33.0714 | 32.8218 | 32.6984 | 32.6019
470 | Temp Subcooled Liq from Econ@comp | ºC | 39.0352 | 39.0093 | 38.9918 | 38.6757 | 38.6662 | 38.566 | 38.2263 | 38.1462 | 38.071 | 37.5864 | 37.5181 | 37.4375 | 36.9893 | 36.9883 | 36.9553 | 34.9384 | 34.8774 | 34.8808 | 34.7318 | 34.6901 | 34.6699 | 35.4365 | 35.4059 | 35.3994 | 35.2954 | 35.2674 | 35.2532 | 38.2839 | 38.3062 | 38.3199 | 38.3505 | 38.3479 | 38.3512 | 38.3759 | 38.3713 | 38.3888 | 38.4338 | 38.4471 | 38.5513 | 38.596 | 38.6296 | 38.636 | 38.7555 | 38.7941 | 38.7416 | 38.7249 | 38.6576 | 38.6548 | 38.589 | 38.272 | 38.2061 | 38.0461 | 37.1997 | 37.0458 | 36.7048 | 36.0042 | 35.9021 | 35.7927 | 35.417 | 35.33 | 35.1873 | 38.1036 | 37.9939 | 37.9486 | 37.6113 | 37.5375 | 37.5212 | 36.773 | 36.7414 | 36.6856 | 36.5957 | 36.5529 | 36.5059 | 36.4236 | 36.3787 | 36.3413 | 35.8037 | 35.724 | 35.7152 | 35.2651 | 35.1259 | 35.1117 | 37.941 | 37.9605 | 37.943 | 38.0039 | 38.0134 | 38.0309 | 38.0964 | 38.1169 | 38.1072 | 38.3326 | 38.3538 | 38.3188 | 38.2222 | 38.2509 | 38.2754 | 38.3143 | 38.2082 | 38.2022 | 38.1929 | 38.0932 | 38.0697 | 38.0203 | 37.9723 | 37.8538 | 36.7125 | 36.6497 | 36.5184 | 35.8476 | 35.7822 | 35.6841 | 35.4392 | 35.3052 | 35.3232 | 38.3559 | 38.2723 | 38.2362 | 37.344 | 37.2993 | 37.2955 | 37.0675 | 37.0698 | 37.0259 | 36.1564 | 36.1095 | 36.0982 | 35.2964 | 35.2721 | 35.2276 | 35.1104 | 35.0725 | 37.6425 | 37.6054 | 37.5363 | 36.7152 | 36.7453 | 36.7046 | 36.4915 | 36.4329 | 36.387 | 36.3774 | 35.8831 | 35.8691 | 35.8544 | 35.2913 | 35.2314 | 35.2253 | 35.2481 | 40.5125 | 40.4688 | 40.4438 | 40.4332 | 40.0513 | 39.9891 | 39.9445 | 39.5054 | 39.4509 | 39.2201 | 40.0441 | 40.0012 | 39.9607 | 39.9607 | 39.8649 | 39.7922 | 39.7278 | 39.6358 | 38.2986 | 38.2404 | 38.1838 | 37.6518 | 37.5954 | 37.5083 | 37.4043 | 37.3334 | 37.2677 | 36.9142 | 36.7574 | 36.6262 | 35.1895 | 35.1124 | 35.1077 | 38.2493 | 38.1507 | 38.0846 | 37.6266 | 37.5584 | 37.5216 | 36.9763 | 36.9083 | 36.833 | 36.6552 | 36.5604 | 36.4431 | 34.3512 | 34.3101 | 34.237 | 35.5932 | 35.5508 | 35.4864 | 35.2306 | 35.1805 | 35.1087 | 36.6187 | 36.6043 | 36.6023 | 36.6202 | 36.598 | 36.6028 | 37.1179 | 37.0684 | 37.0402 | 36.6455 | 36.6244 | 36.5535 | 38.2244 | 37.9991 | 37.853 | 37.4976 | 37.4221 | 37.2856 | 37.0504 | 36.9129 | 36.7631 | 37.5895 | 37.5303 | 37.4551 | 35.9764 | 35.8971 | 35.8659 | 38.2555 | 38.1693 | 38.0714 | 37.8218 | 37.6984 | 37.6019
471 | Enthalphy @ SubC Liq from Econ@comp | ºC | 254.9711 | 254.9326 | 254.9064 | 254.4364 | 254.4224 | 254.2735 | 253.769 | 253.6502 | 253.5385 | 252.8203 | 252.7192 | 252.5999 | 251.9371 | 251.9355 | 251.8868 | 248.9162 | 248.8267 | 248.8317 | 248.6131 | 248.5519 | 248.5222 | 249.648 | 249.603 | 249.5935 | 249.4406 | 249.3994 | 249.3787 | 253.8545 | 253.8875 | 253.9079 | 253.9534 | 253.9495 | 253.9543 | 253.991 | 253.9842 | 254.0102 | 254.0771 | 254.0968 | 254.2515 | 254.318 | 254.3679 | 254.3774 | 254.555 | 254.6124 | 254.5343 | 254.5095 | 254.4095 | 254.4054 | 254.3075 | 253.8368 | 253.7391 | 253.5016 | 252.248 | 252.0205 | 251.5168 | 250.4836 | 250.3331 | 250.172 | 249.6193 | 249.4915 | 249.2818 | 253.5869 | 253.4243 | 253.357 | 252.8573 | 252.7479 | 252.7238 | 251.6175 | 251.5709 | 251.4884 | 251.3557 | 251.2926 | 251.2231 | 251.1018 | 251.0355 | 250.9804 | 250.1883 | 250.071 | 250.058 | 249.3961 | 249.1916 | 249.1707 | 253.3458 | 253.3747 | 253.3488 | 253.439 | 253.4531 | 253.4791 | 253.5763 | 253.6067 | 253.5923 | 253.9267 | 253.9582 | 253.9062 | 253.7629 | 253.8054 | 253.8419 | 253.8996 | 253.7421 | 253.7332 | 253.7195 | 253.5715 | 253.5367 | 253.4634 | 253.3922 | 253.2165 | 251.5281 | 251.4354 | 251.2417 | 250.253 | 250.1567 | 250.0122 | 249.6521 | 249.455 | 249.4814 | 253.9613 | 253.8372 | 253.7836 | 252.4615 | 252.3954 | 252.3897 | 252.0526 | 252.056 | 251.9911 | 250.7077 | 250.6387 | 250.622 | 249.442 | 249.4063 | 249.3409 | 249.1687 | 249.1132 | 252.9034 | 252.8486 | 252.7462 | 251.5321 | 251.5766 | 251.5165 | 251.2019 | 251.1155 | 251.0478 | 251.0337 | 250.3052 | 250.2846 | 250.2628 | 249.4345 | 249.3466 | 249.3376 | 249.3712 | 257.1753 | 257.1098 | 257.0725 | 257.0565 | 256.4858 | 256.393 | 256.3265 | 255.6714 | 255.5901 | 255.2463 | 256.4752 | 256.4111 | 256.3506 | 256.3506 | 256.2076 | 256.0992 | 256.0029 | 255.8658 | 253.8763 | 253.7899 | 253.7059 | 252.9171 | 252.8336 | 252.7048 | 252.5508 | 252.4458 | 252.3487 | 251.8261 | 251.5944 | 251.4008 | 249.2851 | 249.1718 | 249.1649 | 253.8031 | 253.6568 | 253.5587 | 252.8799 | 252.7789 | 252.7243 | 251.9179 | 251.8174 | 251.7061 | 251.4436 | 251.3036 | 251.1306 | 248.055 | 247.9948 | 247.8878 | 249.8784 | 249.8161 | 249.7214 | 249.3454 | 249.2717 | 249.1663 | 251.3896 | 251.3685 | 251.3654 | 251.3919 | 251.3591 | 251.3662 | 252.1272 | 252.0539 | 252.0122 | 251.4291 | 251.398 | 251.2935 | 253.7661 | 253.4319 | 253.2153 | 252.6889 | 252.5772 | 252.3751 | 252.0274 | 251.8242 | 251.6028 | 252.8249 | 252.7373 | 252.6259 | 250.4426 | 250.3258 | 250.2798 | 253.8123 | 253.6844 | 253.5391 | 253.1691 | 252.9862 | 252.8432
472 | Measured Duty | kW | 1285.5318 | 1286.4971 | 1282.7741 | 1078.0834 | 1078.4003 | 1076.2238 | 886.7811 | 895.3896 | 895.0622 | 732.7356 | 734.5958 | 732.4974 | 600.9839 | 600.1606 | 599.2589 | 138.6053 | 139.0473 | 140.6519 | 151.2771 | 151.2444 | 148.4666 | 140.4935 | 145.3752 | 141.9025 | 150.9362 | 154.8974 | 153.6309 | 317.3516 | 317.6251 | 317.9896 | 318.2209 | 318.0264 | 316.869 | 342.7013 | 342.9795 | 345.1982 | 345.1002 | 344.1639 | 342.8328 | 361.0187 | 359.5342 | 359.7694 | 532.1033 | 531.102 | 530.3025 | 541.3298 | 575.8675 | 576.186 | 576.3699 | 788.8678 | 789.3832 | 791.9162 | 786.3352 | 787.2796 | 790.8702 | 875.2622 | 873.917 | 874.2928 | 875.7947 | 881.189 | 883.905 | 535.6112 | 534.5778 | 535.096 | 575.9332 | 576.1901 | 574.839 | 366.2443 | 367.0384 | 366.3025 | 320.0279 | 321.9014 | 324.0861 | 324.4098 | 322.8472 | 323.2661 | 145.8013 | 145.7599 | 145.7209 | 157.0245 | 157.7342 | 159.779 | 316.7466 | 317.1455 | 317.5865 | 339.1284 | 339.7522 | 340.5906 | 339.3372 | 340.2333 | 340.2514 | 542.2657 | 540.5213 | 539.7824 | 569.1504 | 568.4215 | 566.3223 | 563.2824 | 779.595 | 781.5283 | 780.9635 | 781.6478 | 780.9613 | 781.2955 | 784.9356 | 786.0378 | 777.4702 | 777.8107 | 777.6258 | 859.6757 | 861.5819 | 859.8804 | 866.3691 | 866.1682 | 865.4049 | 750.519 | 752.0208 | 751.7233 | 520.0429 | 517.9577 | 517.9259 | 532.2875 | 533.8217 | 532.2234 | 312.7819 | 313.4231 | 312.8162 | 132.6045 | 135.4322 | 126.5993 | 146.506 | 147.1696 | 561.359 | 560.7958 | 562.9523 | 336.2688 | 335.9721 | 337.0229 | 338.0377 | 356.3516 | 358.2896 | 357.336 | 338.108 | 338.3261 | 339.5198 | 142.168 | 147.2795 | 143.7895 | 148.2225 | 742.0331 | 745.0422 | 748.0737 | 745.925 | 810.8357 | 815.9196 | 816.5062 | 821.6113 | 824.5786 | 830.4121 | 847.8718 | 851.2695 | 849.69 | 849.5426 | 851.4302 | 852.9516 | 852.2854 | 855.078 | 787.2941 | 788.0393 | 788.8548 | 868.8031 | 865.8954 | 869.0182 | 871.9533 | 871.6753 | 874.0589 | 805.4831 | 804.8007 | 808.0095 | 369.6438 | 370.2102 | 369.5724 | 784.2278 | 784.2737 | 785.754 | 870.3541 | 864.7612 | 864.4495 | 873.7675 | 874.2148 | 880.8346 | 807.4213 | 806.9046 | 807.5146 | 372.2224 | 373.9627 | 374.4374 | 348.2479 | 348.5775 | 348.6336 | 325.236 | 323.9818 | 324.5566 | 132.6938 | 133.7693 | 141.3747 | 151.4369 | 148.0857 | 149.2094 | 549.6542 | 551.7842 | 551.5222 | 589.0355 | 589.7337 | 589.5587 | 780.0139 | 780.1013 | 777.5005 | 859.0997 | 860.3626 | 859.9811 | 863.5574 | 863.8011 | 863.823 | 800.3355 | 803.6893 | 800.0833 | 364.995 | 363.9877 | 366.0042 | 859.5716 | 859.4268 | 858.4508 | 863.3998 | 866.7674 | 865.9582
473 | COP (Based on Fund. Power) |  | 4.5206 | 4.5274 | 4.5248 | 4.0201 | 4.0185 | 4.0141 | 3.4798 | 3.5134 | 3.5154 | 2.9986 | 3.0069 | 2.993 | 2.5523 | 2.5504 | 2.548 | 8.0542 | 8.0631 | 8.1481 | 8.2842 | 8.3133 | 8.2189 | 8.1304 | 8.4207 | 8.2238 | 8.2664 | 8.5249 | 8.4753 | 6.6292 | 6.6329 | 6.6352 | 6.3382 | 6.329 | 6.3028 | 6.3171 | 6.3008 | 6.3565 | 6.6619 | 6.6211 | 6.6048 | 6.6371 | 6.5561 | 6.5818 | 4.8563 | 4.8609 | 4.8452 | 4.879 | 4.8049 | 4.8068 | 4.8244 | 3.5488 | 3.5548 | 3.5581 | 3.166 | 3.178 | 3.1962 | 3.5273 | 3.5276 | 3.5264 | 3.5632 | 3.5932 | 3.5952 | 4.7483 | 4.7472 | 4.7454 | 4.734 | 4.7322 | 4.7327 | 6.6928 | 6.6907 | 6.6985 | 6.4178 | 6.427 | 6.467 | 6.4732 | 6.4581 | 6.478 | 8.4459 | 8.4503 | 8.5038 | 8.6677 | 8.6453 | 8.7921 | 6.5376 | 6.5272 | 6.5548 | 6.4936 | 6.5058 | 6.5182 | 6.1998 | 6.2189 | 6.2056 | 4.6958 | 4.69 | 4.6881 | 4.6621 | 4.6504 | 4.6408 | 4.6769 | 3.5066 | 3.5161 | 3.5125 | 3.5168 | 3.5104 | 3.5154 | 3.5299 | 3.535 | 3.1424 | 3.149 | 3.152 | 3.4716 | 3.4866 | 3.4817 | 3.5343 | 3.5436 | 3.5466 | 3.0751 | 3.0766 | 3.0798 | 4.7247 | 4.7061 | 4.6956 | 4.7581 | 4.7722 | 4.766 | 6.5463 | 6.5356 | 6.5414 | 7.7806 | 7.9293 | 7.3819 | 8.0524 | 8.1688 | 4.6594 | 4.6613 | 4.6718 | 6.4913 | 6.4787 | 6.5075 | 6.502 | 6.5253 | 6.5691 | 6.554 | 6.087 | 6.0915 | 6.1119 | 7.7879 | 8.0887 | 7.9402 | 8.2191 | 3.3934 | 3.3947 | 3.4051 | 3.3997 | 3.3133 | 3.3356 | 3.3372 | 3.399 | 3.4095 | 3.4305 | 3.4712 | 3.479 | 3.4802 | 3.481 | 3.508 | 3.5088 | 3.5134 | 3.5337 | 3.2297 | 3.2289 | 3.2365 | 3.5333 | 3.5334 | 3.5431 | 3.5952 | 3.5997 | 3.6064 | 3.6436 | 3.6653 | 3.6728 | 6.7683 | 6.7779 | 6.813 | 3.2093 | 3.2091 | 3.2175 | 3.5757 | 3.56 | 3.5614 | 3.5763 | 3.5706 | 3.5969 | 3.6874 | 3.6907 | 3.691 | 6.912 | 6.939 | 7.0018 | 6.7348 | 6.7852 | 6.7601 | 6.8371 | 6.8353 | 6.8286 | 7.7567 | 7.8177 | 8.2646 | 8.3143 | 8.1775 | 8.2605 | 4.9019 | 4.9372 | 4.9437 | 4.8931 | 4.8981 | 4.9097 | 3.2111 | 3.2182 | 3.1999 | 3.5195 | 3.5259 | 3.5336 | 3.57 | 3.5839 | 3.5827 | 3.6568 | 3.6892 | 3.674 | 6.7835 | 6.7009 | 6.8085 | 3.5272 | 3.5274 | 3.5259 | 3.5119 | 3.5153 | 3.509
474
475 | Pressure drop suction pipe to filter | kPa | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0872 | 0.049 | 0.0292 | 0.0411 | 0.0514 | 0.0865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1686 | 0.1747 | 0.1749 | 0.4556 | 0.4408 | 0.4838 | 3.3904 | 3.3879 | 3.3606 | 3.3046 | 3.2879 | 3.2334
476 | Pressure drop filter to top cover | kPa | 79.0446 | 72.0045 | 76.7265 | 51.7749 | 48.4661 | 46.4437 | 40.8644 | 42.6302 | 40.5135 | 37.0194 | 31.952 | 32.8637 | 29.9453 | 29.8331 | 29.6606 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1155 | 0 | 0 | 0.1052 | 0.0097 | 0.1678 | 0.3164 | 0.1496 | 0.5355 | 0.6535 | 0.6495 | 1.051 | 4.4663 | 0 | 0 | 1.6812 | 2.7744 | 2.8507 | 3.4682 | 3.168 | 2.8812 | 10.6808 | 11.5317 | 10.1948 | 11.8421 | 10.5654 | 11.39 | 7.8594 | 30.5197 | 29.2345 | 27.2408 | 43.1248 | 46.1397 | 41.9368 | 50.4251 | 49.8651 | 51.2142 | 50.101 | 51.8478 | 47.4352 | 9.3556 | 9.867 | 10.041 | 10.0932 | 11.4324 | 11.209 | 7.7079 | 7.1561 | 7.7607 | 6.2366 | 6.9865 | 5.6254 | 6.3103 | 7.8986 | 5.5828 | 0 | 0.082 | 0 | 0 | 0 | 0 | 3.1969 | 3.6495 | 3.4924 | 6.0112 | 5.3141 | 4.7325 | 0.4242 | 0.9007 | 1.3462 | 13.4567 | 12.8145 | 14.0343 | 9.0137 | 13.7328 | 9.5501 | 16.6797 | 24.3422 | 23.6794 | 24.947 | 25.9055 | 24.5853 | 25.553 | 24.3844 | 25.3375 | 37.7201 | 35.1299 | 38.186 | 42.5456 | 40.7081 | 41.3902 | 39.0902 | 38.8113 | 42.5121 | 49.3133 | 47.9484 | 46.151 | 15.7946 | 14.892 | 15.6729 | 12.3263 | 11.5221 | 12.2814 | 1.977 | 2.7919 | 2.9386 | 0.7061 | 0.4924 | 0.4827 | 0.1013 | 0.5646 | 12.5629 | 13.1617 | 12.7395 | 5.4923 | 5.9711 | 5.7888 | 6.5692 | 6.6983 | 6.3541 | 6.6146 | 7.618 | 7.4618 | 7.4094 | 1.8845 | 2.2384 | 2.1011 | 2.4074 | 23.6284 | 22.8935 | 21.9697 | 24.6406 | 45.0461 | 47.7008 | 47.0909 | 41.9282 | 41.3169 | 41.4869 | 30.5252 | 28.3615 | 28.7126 | 27.3807 | 27.1931 | 26.487 | 27.7559 | 26.8388 | 38.7864 | 40.3277 | 38.1956 | 30.5368 | 28.1018 | 39.0821 | 42.9934 | 29.0481 | 31.7378 | 25.4593 | 24.7524 | 24.9427 | 10.7971 | 10.809 | 10.7223 | 25.9915 | 35.2869 | 32.7173 | 37.6353 | 39.385 | 39.3113 | 35.3511 | 28.4517 | 29.4388 | 40.4273 | 59.5074 | 36.6139 | 7.4257 | 7.803 | 8.1209 | 5.1692 | 5.2651 | 4.3763 | 7.4811 | 7.4955 | 7.1221 | 0 | 0 | 0 | 0 | 0 | 0 | 11.7822 | 12.4837 | 13.0659 | 5.7835 | 6.8343 | 8.8266 | 27.6218 | 33.1093 | 30.4785 | 48.6195 | 46.3676 | 47.8737 | 39.7814 | 36.0791 | 39.341 | 26.5329 | 29.6682 | 26.6451 | 11.0688 | 10.6688 | 11.0033 | 43.112 | 41.1941 | 41.1255 | 41.8367 | 41.4384 | 39.4345
477 | suction pressure | kPaG | 489.0794 | 489.0071 | 487.3584 | 414.9638 | 414.9734 | 414.7482 | 348.3462 | 350.2065 | 349.8603 | 292.5394 | 292.8087 | 292.4928 | 243.6081 | 243.2348 | 242.9353 | 385.2207 | 384.9044 | 384.485 | 385.4396 | 385.8826 | 385.4339 | 384.1488 | 384.2758 | 385.2251 | 384.7832 | 385.238 | 385.1058 | 379.4038 | 379.283 | 379.9146 | 380.7407 | 380.6997 | 380.4332 | 378.6251 | 379.8465 | 380.0903 | 379.3399 | 380.1967 | 380.371 | 380.8419 | 379.4637 | 380.4485 | 359.7683 | 359.7683 | 359.1307 | 359.9292 | 359.5198 | 360.6241 | 360.2301 | 337.708 | 337.172 | 338.1207 | 310.8277 | 310.9096 | 311.1418 | 338.083 | 337.6283 | 337.7987 | 336.7942 | 337.2529 | 337.6979 | 359.6849 | 358.7273 | 358.8434 | 360.1719 | 359.4261 | 358.9124 | 378.8857 | 379.9471 | 379.4009 | 378.6241 | 380.7248 | 380.7038 | 381.1009 | 379.9561 | 379.8721 | 385.7473 | 385.4673 | 384.1117 | 385.0573 | 385.6745 | 384.9444 | 379.8975 | 380.7896 | 380.2887 | 378.9643 | 379.1564 | 380.083 | 379.983 | 379.6258 | 380.6361 | 360.1724 | 359.3636 | 358.6933 | 358.973 | 359.4407 | 358.6972 | 359.4025 | 337.889 | 338.1478 | 337.7066 | 337.9142 | 338.1843 | 338.3507 | 338.6777 | 338.8808 | 312.0256 | 311.367 | 310.8297 | 337.8763 | 338.1821 | 337.9432 | 337.9959 | 337.7999 | 338.0941 | 311.4359 | 311.5452 | 311.2819 | 359.7353 | 359.2282 | 358.8301 | 359.7274 | 359.3458 | 359.0642 | 380.2666 | 380.4178 | 380.3512 | 384.0429 | 384.1782 | 385.7722 | 386.1108 | 384.6773 | 359.1791 | 359.1847 | 359.7407 | 379.645 | 380.1229 | 379.9231 | 380.788 | 379.9297 | 380.2826 | 380.1696 | 360.0161 | 359.1019 | 360.3694 | 382.6551 | 385.7011 | 385.427 | 385.5362 | 335.7212 | 336.7107 | 337.4706 | 336.4968 | 336.7241 | 338.2995 | 338.8673 | 337.3198 | 337.3585 | 339.165 | 338.4688 | 339.2078 | 337.8717 | 337.8089 | 338.579 | 338.9777 | 338.2865 | 338.7249 | 311.4866 | 311.8845 | 311.2193 | 338.4002 | 337.3218 | 337.8163 | 337.359 | 336.9022 | 337.4341 | 338.3397 | 337.0876 | 337.7584 | 380.3008 | 380.4337 | 378.7995 | 311.4728 | 311.5957 | 311.9075 | 338.6946 | 337.7758 | 337.3257 | 336.9997 | 337.9719 | 338.2524 | 337.774 | 337.2975 | 336.9111 | 379.0038 | 380.1573 | 378.9663 | 380.159 | 380.0419 | 379.6545 | 380.4125 | 379.8428 | 379.7868 | 385.2003 | 385.2262 | 386.6148 | 384.8247 | 384.7193 | 384.3981 | 358.6461 | 359.3946 | 358.9721 | 360.0346 | 359.931 | 359.8542 | 311.6193 | 310.866 | 310.5832 | 338.1907 | 337.7512 | 336.8657 | 337.6472 | 337.4635 | 337.0198 | 338.887 | 337.7717 | 338.1028 | 379.2034 | 379.2797 | 379.9354 | 337.7973 | 337.3051 | 336.7395 | 337.3976 | 338.0853 | 337.5939
478
479
480 | Refrigerant Mass Flow (@ Suction) | Kg/s | 7.9489 | 7.9571 | 7.9399 | 6.7195 | 6.7394 | 6.7741 | 5.6098 | 5.6844 | 5.697 | 4.7338 | 4.7317 | 4.7354 | 3.8907 | 3.8882 | 3.8842 | 0.84497 | 0.84666 | 0.85519 | 0.9195 | 0.91899 | 0.9021 | 0.86095 | 0.88922 | 0.86704 | 0.92182 | 0.94585 | 0.93789 | 2.0144 | 2.0139 | 2.0161 | 2.0198 | 2.0199 | 2.0153 | 2.1651 | 2.1694 | 2.1862 | 2.2051 | 2.2031 | 2.1964 | 2.3118 | 2.2994 | 2.2945 | 3.4147 | 3.409 | 3.4077 | 3.4827 | 3.6936 | 3.6974 | 3.6988 | 5.0717 | 5.0738 | 5.0904 | 5.0286 | 5.0508 | 5.0205 | 5.5041 | 5.4903 | 5.4845 | 5.4731 | 5.4607 | 5.4454 | 3.4113 | 3.3961 | 3.3989 | 3.6032 | 3.6028 | 3.5954 | 2.245 | 2.2506 | 2.2466 | 1.9719 | 1.9843 | 1.9989 | 2.0022 | 1.9923 | 1.9941 | 0.90279 | 0.90239 | 0.90339 | 0.95738 | 0.96313 | 0.97594 | 1.9955 | 2.0039 | 2.0079 | 2.1523 | 2.1567 | 2.1625 | 2.1544 | 2.1618 | 2.1624 | 3.4232 | 3.4153 | 3.4132 | 3.6009 | 3.6014 | 3.5939 | 3.5601 | 4.9802 | 4.9928 | 4.989 | 4.9863 | 4.9803 | 4.9786 | 4.9947 | 4.986 | 4.9395 | 4.9277 | 4.9444 | 5.3674 | 5.3761 | 5.3614 | 5.3669 | 5.3656 | 5.3682 | 4.872 | 4.8748 | 4.8678 | 3.2563 | 3.2448 | 3.2439 | 3.3194 | 3.3287 | 3.3173 | 1.9283 | 1.927 | 1.9185 | 0.81133 | 0.82824 | 0.77394 | 0.89741 | 0.9016 | 3.5591 | 3.5572 | 3.5789 | 2.0998 | 2.0996 | 2.1068 | 2.1139 | 2.2208 | 2.2316 | 2.2242 | 2.0907 | 2.0913 | 2.0981 | 0.87332 | 0.89993 | 0.87827 | 0.90689 | 4.8635 | 4.8719 | 4.8808 | 4.8639 | 5.295 | 5.2907 | 5.2826 | 5.1749 | 5.1771 | 5.2175 | 5.2843 | 5.3043 | 5.293 | 5.2932 | 5.3034 | 5.3113 | 5.3045 | 5.3194 | 5.076 | 5.0697 | 5.0724 | 5.5437 | 5.5157 | 5.5064 | 5.491 | 5.4786 | 5.4826 | 5.1164 | 5.0837 | 5.1154 | 2.2677 | 2.2716 | 2.2653 | 5.0749 | 5.0757 | 5.089 | 5.5529 | 5.5225 | 5.5315 | 5.5029 | 5.513 | 5.5463 | 5.1119 | 5.0984 | 5.0966 | 2.2775 | 2.2874 | 2.2923 | 2.136 | 2.1344 | 2.1239 | 1.9791 | 1.9755 | 1.9819 | 0.82416 | 0.8299 | 0.87659 | 0.93914 | 0.9198 | 0.92729 | 3.4629 | 3.4756 | 3.474 | 3.6779 | 3.6857 | 3.6916 | 5.0125 | 5.0357 | 5.0512 | 5.4851 | 5.4954 | 5.4851 | 5.4924 | 5.4956 | 5.4857 | 5.0671 | 5.0496 | 5.0464 | 2.2403 | 2.2349 | 2.2491 | 5.4632 | 5.4592 | 5.4415 | 5.4556 | 5.4714 | 5.4878
481 | Oil Density (User input) | Kg/m^3 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000
482 | Time @ condition (user input) | Secs | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600
483 | Oil Returned to Separator (user input) | Ltrs
484 | Convert above to Cubic Metre | m^3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
485 | Density*M^3 = Mass | Kg/m^3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
486 | Divide by time @ condition | Kg/s | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
487 | % OIL CARRY OVER | % | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0